## Jan
Monthly Operational Returns Kabirwala
2017-01-01
| Date | Site Avg. Ambient Temp.F | Site Avg. Relative Humidty % | Site Ambient Temp |  | Base load hours |  |  |  | Standby hours |  |  |  | Plant ambient corrected Max Load |  | Corrected Plant Capacity | Ambient Corrected Daclared Avail'y (MWH) | Plant WAPDA Dispatch (MWH) | Net Plant Export (MWH) | Gross Generation | CT1 Average Cap (MW) | CT1 Unavail minutes | CT2 Average Cap (MW) | CT2 Unavail minutes | ST Average Cap (MW) | ST Unavail minutes | Plant Aux Load including Colony Load MWH | Differenece (+/-) MW | Maximum Daily Generation | Daily Load Factor | Avg. Corrected Plant Capacity | Plant Capacity Factor | Plant Availability Factor | Equivalent Plant Availability | LBtu gas flow (mmscf/day) | 1 LBtu gas (Average Btu/scf) | LBTU MMBTU | 1 HBtu gas flow (mmscf/day) | 1 HBtu gas (Average Btu/scf) | HBTU MMBTU | HHV Net Heat Rate (Btu/Kwh) | Avg. declared availability |  | CT1 Derated MW | CT1 derated mintutes | CT-2 derated MW | CT-2 derated mintutes | ST derated MW | ST derated mintutes | WAPDA Backfeed (MWH) |  | CT-1 Gross Generation (MWH) | CT-2 Gross Generation (MWH) | STG Gross Generation (MWH) | CT-1 & CT-2 MWH difference | Base load Heat Rate | STG load | DB1 | DB2 | CT1 | CT1 Gas flow | CT2 Gas flow |  | Pamb | Freq. Hz | LBTU Gas Specific gravity | CT-1 compressor efficiency(%) | CT-2 compressor efficiency(%) |  | CT-1 Heat Rate (Btu/Kwh) | CT-2 Heat Rate (Btu/Kwh) |  | DB(1+2) | DB-1 Ops Hours | DB-2 Ops Hours |  | CT-1 Wetcomprssion Ops Hours | RO Operation Hours
[6 empty] | CT1 |  | CT2 |  | CT1 |  | CT2 | [45 empty] | mmscf/d | mmscf/d | WetC flow | HBTU KPPH | HBTU KPPH | LBTU KPPH | mbar | Hz | [7 empty] | mmscf/d
|  |  |  | Max | Min | hrs | min | hrs | min | hrs | min | hrs | min | hrs | min | [44 empty] | gpm
Week 1 | 2017-01-01 | 57 | 81% | 68 | 51 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 3459 | 3459 | 3411 | 3515 | 46 | 0 | 45 | 0 | 63 | 0 | 104 | -48 | 150 | 97.64% | 155 | 91.69% | 100% | 95.45% | 11.675 | 185.52 | 2165.946 | 29.501 | 929 | 27406.429 | 8669.7083 | 144.125 |  | 0 | 0 | 0 | 0 | 7 | 1440 | 0 |  | 1106 | 1070 | 1339 | -36 | 8669.7083 | 55.7917 | 1.425 | 1.398 | 23.3 | 29.47 | 23.33 | 32.5 | 999.08 | 49.94 | 0.9128 | 91.1 | 84 | -7.1 | 12525 | 12805 | 280 | 2.823 | 24 | 24 |  | 17.0833 | 6.7833
| 2017-01-02 | 55.4 | 90.8% | 59 | 51 | 21 | 14 | 22 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 3485 | 3485 | 3098 | 3203 | 46 | 148 | 45 | 73 | 63 | 104 | 105 | -387 | 148 | 90.17% | 155 | 83.28% | 92.49% | 84.66% | 10.78 | 183.83 | 1981.6874 | 26.844 | 929 | 24938.076 | 8689.4007 | 145.2083 |  | 0 | 0 | 0 | 0 | 13 | 1336 | 0 |  | 906 | 1021 | 1276 | 115 | 8689.4007 | 53.1667 | 1.747 | 1.758 | 0 | 24.6 | 22.2 | 32 | 1001.17 | 49.95 | 0.9136 | 83 | 84.1 | 1.1 | 12737 | 12748 | 11 | 3.505 | 21.28 | 22.01 |  | 0.15 | 5.25
| 2017-01-03 | 59 | 85.4% | 62 | 56 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 3444 | 3444 | 3392 | 3501 | 44 | 0 | 45 | 0 | 63 | 0 | 109 | -52 | 148 | 98.56% | 155 | 91.18% | 100% | 96.05% | 11.53 | 181.21 | 2089.3513 | 29.455 | 929 | 27363.695 | 8683.0915 | 143.5 |  | 0 | 0 | 0 | 0 | 6 | 1440 | 0 |  | 1055 | 1071 | 1375 | 16 | 8683.0915 | 57.2917 | 1.661 | 1.661 | 16.71 | 28.3 | 23.2 | 32.3 | 999.3 | 49.96 | 0.9146 | 88.6 | 84.3 | -4.3 | 12632 | 12769 | 137 | 3.322 | 24 | 24 |  | 12.2333 | 1.8333
| 2017-01-04 | 60.2 | 79.7% | 62 | 58 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 3474 | 3474 | 3417 | 3526 | 47 | 0 | 44 | 0 | 63 | 0 | 109 | -57 | 148 | 99.27% | 155 | 91.85% | 100% | 94.81% | 11.3 | 179.9 | 2032.87 | 29.74 | 929 | 27628.46 | 8680.518 | 144.75 |  | 0 | 0 | 0 | 0 | 8 | 1440 | 0 |  | 1134 | 1066 | 1326 | -68 | 8680.518 | 55.25 | 1.328 | 1.328 | 32.6 | 30 | 23.1 | 32.2 | 996.9 | 49.99 | 0.9151 | 94.1 | 84.3 | -9.8 | 12437 | 12772 | 335 | 2.656 | 24 | 24 |  | 24 | 6.8333
| 2017-01-05 | 59.3 | 82.5% | 62 | 57 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 3484 | 3476 | 3411 | 3522 | 47 | 0 | 44 | 0 | 63 | 0 | 111 | -65 | 149 | 98.49% | 155 | 91.69% | 100% | 94.81% | 11.189 | 180.09 | 2015.027 | 29.601 | 930 | 27528.93 | 8661.377 | 145.1667 |  | 0 | 0 | 0 | 0 | 8 | 1440 | 0 |  | 1133 | 1066 | 1323 | -67 | 8661.377 | 55.125 | 1.324 | 1.32 | 32.43 | 29.97 | 23.13 | 32.2 | 995.3 | 50 | 0.915 | 94.08 | 84.36 | -9.72 | 12452 | 12780 | 328 | 2.644 | 24 | 24 |  | 23.9167 | 7.3333
| 2017-01-06 | 60 | 83.7% | 66 | 57 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 3471 | 3471 | 3411 | 3520 | 47 | 0 | 44 | 0 | 63 | 0 | 109 | -60 | 148 | 99.1% | 155 | 91.69% | 100% | 94.81% | 11.297 | 179.57 | 2028.6023 | 29.512 | 931 | 27475.672 | 8649.7433 | 144.625 |  | 0 | 0 | 0 | 0 | 8 | 1440 | 0 |  | 1130 | 1060 | 1330 | -70 | 8649.7433 | 55.4167 | 1.364 | 1.364 | 32.67 | 29.85 | 23.02 | 32.19 | 992.63 | 50.02 | 0.915 | 94.23 | 84.16 | -10.07 | 12427 | 12798 | 371 | 2.728 | 24 | 24 |  | 24 | 5.9167
| 2017-01-07 | 57.4 | 74.4% | 65 | 52 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 3493 | 3493 | 3434 | 3545 | 45 | 0 | 45 | 0 | 63 | 0 | 111 | -59 | 149 | 99.13% | 155 | 92.31% | 100% | 96.08% | 11.379 | 180.37 | 2052.4302 | 29.694 | 931 | 27645.114 | 8648.0909 | 145.5417 |  | 0 | 0 | 0 | 0 | 6 | 1440 | 0 |  | 1085 | 1077 | 1383 | -8 | 8648.0909 | 57.625 | 1.672 | 1.675 | 16.52 | 28.87 | 23.39 | 32.13 | 993.46 | 49.97 | 0.9147 | 88.33 | 84.11 | -4.22 | 12538 | 12748 | 210 | 3.347 | 24 | 24 |  | 12.0167 | 6.5833
Week 2 | 2017-01-08 | 51.2 | 86% | 56 | 46 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 3355 | 3355 | 3310 | 3413 | 45 | 0 | 45 | 0 | 63 | 0 | 103 | -45 | 149 | 95.44% | 155 | 88.98% | 100% | 93.46% | 11.228 | 182.62 | 2050.4574 | 28.535 | 932 | 26594.62 | 8654.1019 | 139.7917 |  | 0 | 0 | 0 | 0 | 10 | 1440 | 0 |  | 1044 | 1104 | 1265 | 60 | 8654.1019 | 52.7083 | 0.962 | 0.971 | 0 | 27.93 | 23.93 | 32.05 | 997.71 | 50.02 | 0.9138 | 82.76 | 84.08 | 1.32 | 12588 | 12640 | 52 | 1.933 | 14.18 | 14.18 |  | 0 | 0
| 2017-01-09 | 53.59 | 72.06% | 64 | 46 | 9 | 12 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 2422 | 2422 | 2394 | 2478 | 46 | 805 | 46 | 0 | 63 | 0 | 84 | -28 | 144 | 71.7% | 155 | 64.35% | 83.41% | 66.96% | 11.35 | 180.8 | 2052.08 | 20.62 | 931 | 19197.22 | 8876.0652 | 100.9167 |  | 24 | 90 | 0 | 0 | 24 | 1440 | 0 |  | 440 | 1101 | 937 | 661 | 8876.0652 | 39.0417 | 0.301 | 1.956 | 0 | 12.16 | 23.58 | 32.16 | 998.88 | 49.88 | 0.9149 | 83.73 | 84.13 | 0.4 | 12373 | 12549 | 176 | 2.257 | 8 | 22.566 |  | 0 | 6.3333
| 2017-01-10 | 55.08 | 66.53% | 65 | 45 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 3190 | 3190 | 3140 | 3229 | 45 | 0 | 45 | 0 | 63 | 0 | 89 | -50 | 142 | 94.75% | 155 | 84.41% | 100% | 88.24% | 11.599 | 181.91 | 2109.9741 | 26.41 | 930 | 24561.3 | 8494.0363 | 132.9167 |  | 0 | 0 | 0 | 0 | 18 | 1440 | 0 |  | 1071 | 1086 | 1072 | 15 | 8494.0363 | 44.6667 | 0.025 | 0.025 | 0 | 28.35 | 23.31 | 32.31 | 998.96 | 49.93 | 0.9147 | 83.77 | 84.26 | 0.49 | 12456 | 12627 | 171 | 0.05 | 1.8333 | 1.8333 |  | 0 | 0
| 2017-01-11 | 56.9 | 61.2% | 69 | 49 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3718 | 3176 | 3176 | 3134 | 3226 | 44 | 0 | 46 | 0 | 63 | 0 | 92 | -42 | 137 | 98.11% | 154.9167 | 84.29% | 100% | 88.24% | 11.634 | 182.85 | 2127.2769 | 26.224 | 930 | 24388.32 | 8460.6244 | 132.3333 |  | 0 | 0 | 0 | 0 | 18 | 1440 | 0 |  | 1054 | 1095 | 1077 | 41 | 8460.6244 | 44.875 | 0 | 0 | 0 | 28.02 | 23.47 | 32.4 | 998.38 | 49.94 | 0.9149 | 83.7 | 84.27 | 0.57 | 12515 | 12590 | 75 | 0 | 0 | 0 |  | 0 | 0
| 2017-01-12 | 54.7 | 58.5% | 68 | 43 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 3158 | 3158 | 3110 | 3203 | 44 | 0 | 45 | 0 | 63 | 0 | 93 | -48 | 136 | 98.13% | 155 | 83.6% | 100% | 87.5% | 11.597 | 178.81 | 2073.6596 | 26.347 | 930 | 24502.71 | 8545.4565 | 131.5833 |  | 0 | 0 | 0 | 0 | 19 | 1440 | 0 |  | 1061 | 1079 | 1063 | 18 | 8545.4565 | 44.2917 | 0 | 0 | 0 | 28.2 | 23.2 | 32.3 | 998.3 | 49.98 | 0.9153 | 83.1 | 84.27 | 1.17 | 12530 | 12665 | 135 | 0 | 0 | 0 |  | 0 | 2.7333
| 2017-01-13 | 54.7 | 56.5% | 67 | 44 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 3172 | 3172 | 3121 | 3209 | 44 | 0 | 45 | 0 | 63 | 0 | 88 | -51 | 135 | 99.04% | 155 | 83.9% | 100% | 87.5% | 11.629 | 178.11 | 2071.2412 | 26.397 | 928 | 24496.416 | 8512.5464 | 132.1667 |  | 0 | 0 | 0 | 0 | 19 | 1440 | 0 |  | 1057 | 1084 | 1068 | 27 | 8512.5464 | 44.5 | 0 | 0 | 0 | 28.2 | 23.4 | 32.1 | 999.3 | 50.07 | 0.9155 | 83.02 | 84.34 | 1.32 | 12572 | 12679 | 107 | 0 | 0 | 0 |  | 0 | 0
| 2017-01-14 | 55.4 | 64.1% | 58 | 52 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 3169 | 3169 | 3118 | 3209 | 43 | 0 | 45 | 0 | 63 | 0 | 91 | -51 | 135 | 99.04% | 155 | 83.82% | 100% | 88.08% | 11.5 | 177.76 | 2044.24 | 26.328 | 929 | 24458.712 | 8499.9846 | 132.0417 |  | 0 | 0 | 0 | 0 | 18 | 1440 | 0 |  | 1043 | 1089 | 1077 | 46 | 8499.9846 | 44.875 | 0 | 0 | 0 | 28 | 23.5 | 32 | 1002.13 | 50.01 | 0..9157 | 83.4 | 84.6 | 1.2 | 12629 | 12665 | 36 | 0 | 0 | 0 |  | 0 | 3.8333
Week 3 | 2017-01-15 | 51.4 | 79.5% | 54 | 49 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 3147 | 3147 | 3103 | 3193 | 44 | 0 | 45 | 0 | 63 | 0 | 90 | -44 | 135 | 98.55% | 155 | 83.41% | 100% | 87.5% | 11.525 | 178.83 | 2061.0158 | 26.257 | 928 | 24366.496 | 8516.7618 | 131.125 |  | 0 | 0 | 0 | 0 | 19 | 1440 | 0 |  | 1054 | 1075 | 1064 | 21 | 8516.7618 | 44.3333 | 0 | 0 | 0 | 28.2 | 23.3 | 31.9 | 1001.71 | 50.03 | 0.9153 | 83.2 | 84.6 | 1.4 | 12603.2 | 12703.1 | 99.9 | 0 | 0 | 0 |  | 0 | 0
| 2017-01-16 | 52.5 | 78% | 59 | 48 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 3126 | 3126 | 3084 | 3173 | 44 | 0 | 45 | 0 | 63 | 0 | 89 | -42 | 135 | 97.93% | 155 | 82.9% | 100% | 87.5% | 11.56 | 177.14 | 2047.7384 | 26.096 | 928 | 24217.088 | 8516.4807 | 130.25 |  | 0 | 0 | 0 | 0 | 19 | 1440 | 0 |  | 1051 | 1066 | 1056 | 15 | 8516.4807 | 44 | 0 | 0 | 0 | 28.1 | 23 | 32.1 | 1000.63 | 49.98 | 0.9159 | 83.2 | 84.6 | 1.4 | 12596 | 12699 | 103 | 0 | 0 | 0 |  | 0 | 3.75
| 2017-01-17 | 54 | 73% | 67 | 44 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 3146 | 3146 | 3088 | 3179 | 44 | 0 | 45 | 0 | 63 | 0 | 91 | -58 | 136 | 97.4% | 155 | 83.01% | 100% | 87.5% | 11.575 | 180.39 | 2088.0142 | 26.267 | 929 | 24402.043 | 8578.3864 | 131.0833 |  | 0 | 0 | 0 | 0 | 19 | 1440 | 0 |  | 1050 | 1071 | 1058 | 21 | 8578.3864 | 44.0833 | 0 | 0 | 0 | 28.18 | 23.13 | 32.03 | 1000.17 | 50.03 | 0.9147 | 83 | 84.42 | 1.42 | 12624 | 12704 | 80 | 0 | 0 | 0 |  | 0 | 0
| 2017-01-18 | 54.3 | 72.5% | 64 | 46 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 3166 | 3166 | 3111 | 3201 | 43 | 0 | 45 | 0 | 63 | 0 | 90 | -55 | 136 | 98.07% | 155 | 83.63% | 100% | 88.08% | 11.6 | 177.58 | 2059.928 | 26.497 | 928 | 24589.216 | 8566.1022 | 131.9167 |  | 0 | 0 | 0 | 0 | 18 | 1440 | 0 |  | 1044 | 1085 | 1072 | 41 | 8566.1022 | 44.6667 | 0 | 0 | 0 | 28.13 | 23.53 | 31.88 | 1003.54 | 50.02 | 0.9159 | 82.83 | 84.41 | 1.58 | 12678 | 12709 | 31 | 0 | 0 | 0 |  | 0 | 3
| 2017-01-19 | 54 | 71.3% | 67 | 45 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 3196 | 3196 | 3145 | 3236 | 44 | 0 | 46 | 0 | 63 | 0 | 91 | -51 | 138 | 97.71% | 155 | 84.54% | 100% | 88.24% | 11.605 | 176.57 | 2049.0948 | 26.83 | 927 | 24871.41 | 8559.779 | 133.1667 |  | 0 | 0 | 0 | 0 | 18 | 1440 | 0 |  | 1045 | 1107 | 1084 | 62 | 8559.779 | 45.1667 | 0 | 0 | 0 | 28.27 | 24.04 | 31.82 | 1007.67 | 50.02 | 0.9161 | 82.94 | 84.33 | 1.39 | 12727 | 12690 | -37 | 0 | 0 | 0 |  | 0 | 0
| 2017-01-20 | 56.07 | 61.18% | 69 | 45 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3719 | 3194 | 3194 | 3151 | 3242 | 44 | 0 | 46 | 0 | 63 | 0 | 91 | -43 | 139 | 97.18% | 154.9583 | 84.73% | 100% | 88.24% | 11.62 | 178.75 | 2077.075 | 26.684 | 929 | 24789.436 | 8526.3443 | 133.0833 |  | 0 | 0 | 0 | 0 | 18 | 1440 | 0 |  | 1047 | 1110 | 1085 | 63 | 8526.3443 | 45.2083 | 0 | 0 | 0 | 28.14 | 24.07 | 31.43 | 1005.21 | 50.04 | 0.9156 | 82.97 | 84.3 | 1.33 | 12670 | 12618 | -52 | 0 | 0 | 0 |  | 0 | 4.83
| 2017-01-21 | 58.18 | 58.92% | 66 | 49 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 3189 | 3189 | 3130 | 3221 | 43 | 0 | 46 | 0 | 63 | 0 | 91 | -59 | 137 | 97.96% | 155 | 84.14% | 100% | 88.16% | 11.635 | 178.94 | 2081.9669 | 26.511 | 929 | 24628.719 | 8533.7655 | 132.875 |  | 0 | 0 | 0 | 0 | 18 | 1440 | 0 |  | 1039 | 1101 | 1081 | 62 | 8533.7655 | 45.0417 | 0 | 0 | 0 | 28.06 | 23.88 | 31.56 | 1002.38 | 50.07 | 0.9156 | 83.1 | 84.4 | 1.3 | 12705 | 12681 | -24 | 0 | 0 | 0 |  | 0 | 0
Week 4 | 2017-01-22 | 57.87 | 63.86% | 68 | 47 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 3175 | 3175 | 3125 | 3217 | 43 | 0 | 46 | 0 | 63 | 0 | 92 | -50 | 138 | 97.13% | 155 | 84.01% | 100% | 88.16% | 11.675 | 179.27 | 2092.9773 | 26.474 | 925 | 24488.45 | 8506.0567 | 132.2917 |  | 0 | 0 | 0 | 0 | 18 | 1440 | 0 |  | 1038 | 1096 | 1083 | 58 | 8506.0567 | 45.125 | 0 | 0 | 0 | 28.08 | 23.92 | 31.55 | 1003.63 | 50.02 | 0.9158 | 82.84 | 84.39 | 1.55 | 12740 | 12725 | -15 | 0 | 0 | 0 |  | 0 | 3.38
| 2017-01-23 | 59 | 62.4% | 69 | 49 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 3158 | 3158 | 3108 | 3199 | 43 | 0 | 45 | 0 | 63 | 0 | 91 | -50 | 137 | 97.29% | 155 | 83.55% | 100% | 88.08% | 11.69 | 180.02 | 2104.4338 | 26.624 | 916.2 | 24392.9088 | 8525.5285 | 131.5833 |  | 0 | 0 | 0 | 0 | 18 | 1440 | 0 |  | 1029 | 1092 | 1078 | 63 | 8525.5285 | 44.9167 | 0 | 0 | 0 | 28.3 | 24.2 | 31.3 | 1002.8 | 50.05 | 0.9161 | 82.77 | 84.25 | 1.48 | 12924 | 12875 | -49 | 0 | 0 | 0 |  | 0 | 0
| 2017-01-24 | 57 | 76% | 61 | 55 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 3132 | 3132 | 3080 | 3173 | 42 | 0 | 45 | 0 | 65 | 0 | 93 | -52 | 133 | 99.4% | 155 | 82.8% | 100% | 86.84% | 11.71 | 177.72 | 2081.1012 | 26.08 | 925.228 | 24129.9462 | 8510.0803 | 130.5 |  | 0 | 0 | 0 | 0 | 20 | 1440 | 0 |  | 1020 | 1079 | 1074 | 59 | 8510.0803 | 44.75 | 0 | 0 | 0 | 27.8 | 23.7 | 31.2 | 1001.9 | 49.98 | 0.9162 | 82.95 | 84.52 | 1.57 | 12811 | 12809 | -2 | 0 | 0 | 0 |  | 0 | 3.02
| 2017-01-25 | 58.4 | 81% | 65 | 54 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 3107 | 3107 | 3053 | 3147 | 42 | 0 | 44 | 0 | 65 | 0 | 94 | -54 | 133 | 98.59% | 155 | 82.07% | 100% | 86.75% | 11.65 | 175.67 | 2046.5555 | 25.762 | 931 | 23984.422 | 8526.3601 | 129.4583 |  | 0 | 0 | 0 | 0 | 20 | 1440 | 0 |  | 1010 | 1067 | 1070 | 57 | 8526.3601 | 44.5833 | 0 | 0 | 0 | 27.3 | 23.2 | 31.1 | 1000.1 | 49.9 | 0.917 | 83.08 | 84.63 | 1.55 | 12728 | 12740 | 12 | 0 | 0 | 0 |  | 0 | 0
| 2017-01-26 | 56.4 | 89.9% | 59 | 55 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 3127 | 3127 | 3066 | 3159 | 42 | 0 | 45 | 0 | 63 | 0 | 93 | -61 | 133 | 98.97% | 155 | 82.42% | 100% | 88% | 11.36 | 176.44 | 2004.3584 | 26.01 | 928 | 24137.28 | 8526.3008 | 130.2917 |  | 0 | 0 | 0 | 0 | 18 | 1440 | 0 |  | 1018 | 1071 | 1070 | 53 | 8526.3008 | 44.5833 | 0 | 0 | 0 | 27.7 | 23.6 | 30.6 | 999.25 | 49.96 | 0.9165 | 82.9 | 84.5 | 1.6 | 12819 | 12824 | 5 | 0 | 0 | 0 |  | 0 | 3.75
| 2017-01-27 | 56.2 | 84% | 62 | 50 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 3116 | 3116 | 3066 | 3159 | 42 | 0 | 45 | 0 | 63 | 0 | 93 | -50 | 134 | 98.23% | 155 | 82.42% | 100% | 88% | 11.41 | 176.25 | 2011.0125 | 25.986 | 929 | 24140.994 | 8529.6825 | 129.8333 |  | 0 | 0 | 0 | 0 | 18 | 1440 | 0 |  | 1021 | 1070 | 1068 | 49 | 8529.6825 | 44.5 | 0 | 0 | 0 | 27.7 | 23.5 | 31.1 | 1000.5 | 49.97 | 0.9172 | 82.8 | 84.5 | 1.7 | 12777 | 12809 | 32 | 0 | 0 | 0 |  | 0 | 0
| 2017-01-28 | 56.8 | 79% | 68 | 45 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 3093 | 3093 | 3047 | 3136 | 43 | 0 | 44 | 0 | 63 | 0 | 89 | -46 | 133 | 98.25% | 155 | 81.91% | 100% | 87.33% | 11.39 | 174.02 | 1982.0878 | 25.954 | 929 | 24111.266 | 8563.6212 | 128.875 |  | 0 | 0 | 0 | 0 | 19 | 1440 | 0 |  | 1023 | 1057 | 1056 | 34 | 8563.6212 | 44 | 0 | 0 | 0 | 27.8 | 23.3 | 31 | 1002.2 | 49.97 | 0.9176 | 82.6 | 84.4 | 1.8 | 12796 | 12874 | 78 | 0 | 0 | 0 |  | 0 | 3.73
Week 5 | 2017-01-29 | 62.5 | 73.5% | 71 | 54 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3715 | 3104 | 3104 | 3051 | 3146 | 41 | 0 | 44 | 0 | 63 | 0 | 95 | -53 | 133 | 98.56% | 154.7917 | 82.13% | 100% | 87.84% | 11.29 | 172.79 | 1950.7991 | 25.854 | 935 | 24173.49 | 8562.5333 | 129.3333 | 0 | 0 | 0 | 0 | 18 | 1440 | 0 |  | 995 | 1064 | 1087 | 69 | 8562.5333 | 8562.5333 | 0.221 | 0 | 0 | 27.06 | 23.2 | 31.06 | 999.21 | 49.99 | 0.918 | 82.86 | 84.39 |  | 12794 | 12779 | -15 | 0.221 | 10.17 | 0 | 0 | 0
| 2017-01-30 | 63.2 | 72.1% | 73 | 56 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3710 | 3345.5 | 3345.5 | 3289 | 3390 | 44 | 0 | 44 | 0 | 63 | 0 | 101 | -56.5 | 151 | 93.54% | 154.5833 | 88.65% | 100% | 94.04% | 11.3 | 173.28 | 1958.064 | 28.291 | 937 | 26508.667 | 8655.1326 | 139.3958 | 0 | 0 | 0 | 0 | 9 | 1440 | 0 |  | 1061 | 1051 | 1278 | -10 | 8655.1326 | 8655.1326 | 1.269 | 1.095 | 16.81 | 28.3 | 23.01 | 30.73 | 997.21 | 50.01 | 0.9178 | 88.47 | 84.22 |  | 12562 | 12826 | 264 | 2.364 | 24 | 12.48 | 12.7 | 5.42
| 2017-01-31 | 61 | 76.6% | 71 | 51 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3714 | 3578 | 3578 | 3522 | 3628 | 46 | 0 | 44 | 0 | 63 | 0 | 106 | -56 | 153 | 98.8% | 154.75 | 94.83% | 100% | 98.04% | 11.45 | 172.7 | 1977.415 | 30.459 | 939 | 28601.001 | 8682.117 | 149.0833 | 0 | 0 | 0 | 0 | 3 | 1440 | 0 |  | 1124 | 1055 | 1449 | -69 | 8682.117 | 8682.117 | 2.044 | 2.044 | 27.87 | 29.35 | 23.04 | 30.72 | 997.29 | 50.03 | 0.9183 | 92.78 | 84.17 |  | 12306 | 12775 | 469 | 4.088 | 24 | 24 | 20.6667 | 7.3
| 2017-02-01 | 60.76 | 69.64% | 74 | 47 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3707 | 3587 | 3587 | 3531 | 3642 | 46 | 0 | 44 | 0 | 63 | 0 | 111 | -56 | 156 | 97.28% | 154.4583 | 95.25% | 100% | 99.35% | 11.475 | 175.2 | 2010.42 | 30.609 | 939 | 28741.851 | 8709.2243 | 149.4583 | 0 | 0 | 0 | 0 | 1 | 1440 | 0 |  | 1100 | 1062 | 1480 | -38 | 8709.2243 | 8709.2243 | 2.183 | 2.183 | 31.8 | 28.91 | 23.22 | 30.69 | 997.88 | 49.99 | 0.918 | 89.61 | 83.92 | -5.69 | 12365 | 12765 | 400 | 4.366 | 24 | 24 | 15.26 | 7.1
| 2017-02-02 | 61.88 | 67.54% | 69 | 55 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3716 | 3582 | 3582 | 3528 | 3639 | 46 | 0 | 44 | 0 | 64 | 0 | 111 | -54 | 154 | 98.46% | 154.8333 | 94.94% | 100% | 98.05% | 11.5 | 177.19 | 2037.685 | 30.506 | 940 | 28675.64 | 8705.591 | 149.25 | 0 | 0 | 0 | 0 | 3 | 1440 | 0 |  | 1115 | 1059 | 1465 | -56 | 8705.591 | 8705.591 | 2.116 | 2.116 | 31.98 | 29.19 | 23.14 | 30.69 | 1000 | 50.02 | 0.9169 | 91.52 | 84.06 | -7.46 | 12391 | 12656 | 265 | 4.232 | 24 | 24 | 18.77 | 6.83
| 2017-02-03 | 60.92 | 72.25% | 68 | 54 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 3578 | 3578 | 3517 | 3626 | 47 | 0 | 44 | 0 | 64 | 0 | 109 | -61 | 153 | 98.75% | 155 | 94.54% | 100% | 97.42% | 11.35 | 174.49 | 1980.4615 | 30.475 | 940 | 28646.5 | 8708.2632 | 149.0833 | 0 | 0 | 0 | 0 | 4 | 1440 | 0 |  | 1136 | 1054 | 1436 | -82 | 8708.2632 | 8708.2632 | 1.954 | 1.954 | 32.19 | 29.59 | 23.16 | 30.55 | 998.46 | 50.03 | 0.9178 | 93.58 | 83.98 | -9.6 | 12405 | 12576 | 171 | 3.908 | 24 | 24 | 22.45 | 7.65
| 2017-02-04 | 59.8 | 81.2% | 67 | 55 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 3571 | 3531 | 3476 | 3582 | 47 | 0 | 44 | 0 | 64 | 0 | 106 | -55 | 153 | 97.55% | 155 | 93.44% | 100% | 96.13% | 11.375 | 176.27 | 2005.0713 | 30.221 | 941 | 28437.961 | 8758.0645 | 148.7917 | 0 | 0 | 0 | 0 | 6 | 1440 | 0 |  | 1134 | 1046 | 1402 | -88 | 8758.0645 | 8758.0645 | 1.782 | 1.762 | 32 | 29.5 | 22.9 | 30.26 | 989.9 | 50 | 0.9168 | 94.98 | 84.09 | -10.89 | 12366 | 12545 | 179 | 3.544 | 24 | 24 | 24 | 7.12
Week 6 | 2017-02-05 | 57 | 62% | 66 | 49 | 24 | 0 | 12 | 31 | 0 | 0 | 0 | 0 | 6 | 31 | 3720 | 2835 | 2745 | 2663 | 2752 | 44 | 0 | 44 | 624 | 64 | 0 | 89 | -82 | 157 | 73.04% | 155 | 71.59% | 87.46% | 77.73% | 5.853 | 183.36 | 1073.2061 | 23.966 | 939 | 22504.074 | 8853.6538 | 118.125 | 0 | 0 | 21 | 65 | 19 | 1049 | 0 |  | 1063 | 614 | 1075 | -449 | 8853.6538 | 8853.6538 | 2.173 | 0.743 | 33.2 | 28.11 | 13.45 | 16.74 | 994.46 | 50 | 0.9143 | 84.9 | 86.17 | 1.27 | 12579 | 12033 | -546 | 2.916 | 24 | 9.43 | 4.03 | 6.28
| 2017-02-06 | 57 | 63% | 69 | 45 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 3585 | 3474 | 3445 | 3546 | 45 | 0 | 48 | 0 | 64 | 0 | 101 | -29 | 153 | 96.57% | 155 | 92.61% | 100% | 94.27% | 10.23 | 175.06 | 1790.8638 | 29.699 | 939 | 27887.361 | 8614.8693 | 149.375 | 0 | 0 | 0 | 0 | 9 | 1440 | 0 |  | 1080 | 1157 | 1309 | 77 | 8614.8693 | 8614.8693 | 1.326 | 1.282 | 31.9 | 28.49 | 24.56 | 30.69 | 999.08 | 50.02 | 0.9174 | 86.11 | 86.13 | 0.02 | 12550 | 12033 | -517 | 2.608 | 24 | 24 | 7.78 | 0
| 2017-02-07 | 59.3 | 62.6% | 70 | 47 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3717 | 3599 | 3599 | 3554 | 3665 | 46 | 0 | 48 | 0 | 64 | 0 | 111 | -45 | 155 | 98.52% | 154.875 | 95.61% | 100% | 96.84% | 10.8 | 170.09 | 1836.972 | 30.965 | 938 | 29045.17 | 8689.4041 | 149.9583 | 0 | 0 | 0 | 0 | 5 | 1440 | 0 |  | 1099 | 1143 | 1423 | 44 | 8689.4041 | 8689.4041 | 1.829 | 1.779 | 32 | 28.9 | 24.4 | 30.5 | 998.71 | 49.95 | 0.9193 | 88.7 | 86.1 | -2.6 | 12521 | 12124 | -397 | 3.608 | 24 | 24 | 13.88 | 6.16
| 2017-02-08 | 62.7 | 59.5% | 74 | 52 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3703 | 3588 | 3588 | 3537 | 3645 | 45 | 0 | 47 | 0 | 64 | 0 | 108 | -51 | 154 | 98.62% | 154.2917 | 95.52% | 100% | 97.44% | 11 | 172.3 | 1895.3 | 30.779 | 936 | 28809.144 | 8680.9285 | 149.5 | 0 | 0 | 0 | 0 | 4 | 1440 | 0 |  | 1088 | 1126 | 1431 | 38 | 8680.9285 | 8680.9285 | 1.878 | 1.878 | 31.7 | 28.7 | 24.1 | 30.5 | 996 | 50 | 0.9186 | 89 | 86.1 | -2.9 | 12547 | 12171 | -376 | 3.756 | 24 | 24 | 14.7 | 7.2
| 2017-02-09 | 62.2 | 59.9% | 74 | 55 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3707 | 3586 | 3586 | 3540 | 3649 | 46 | 0 | 47 | 0 | 64 | 0 | 109 | -46 | 154 | 98.73% | 154.4583 | 95.5% | 100% | 97.45% | 10.97 | 171.9 | 1885.743 | 30.755 | 938 | 28848.19 | 8681.902 | 149.4167 | 0 | 0 | 0 | 0 | 4 | 1440 | 0 |  | 1091 | 1121 | 1437 | 30 | 8681.902 | 8681.902 | 1.897 | 1.897 | 31.9 | 28.8 | 24.1 | 30.3 | 998.3 | 50.05 | 0.9194 | 89.3 | 85.9 | -3.4 | 12550 | 12222 | -328 | 3.794 | 24 | 24 | 15.4 | 6.9
| 2017-02-10 | 62.8 | 53.8% | 78 | 50 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3705 | 3603 | 3603 | 3544 | 3654 | 45 | 0 | 47 | 0 | 64 | 0 | 110 | -59 | 155 | 98.23% | 154.375 | 95.65% | 100% | 97.44% | 11.005 | 171.4 | 1886.257 | 30.748 | 938 | 28841.624 | 8670.3953 | 150.125 | 0 | 0 | 0 | 0 | 4 | 1440 | 0 |  | 1084 | 1126 | 1444 | 42 | 8670.3953 | 8670.3953 | 1.962 | 1.956 | 31.57 | 28.59 | 24.22 | 30.22 | 997.71 | 50.04 | 0.9201 | 88.15 | 85.75 | -2.4 | 12543 | 12206 | -337 | 3.918 | 24 | 24 | 12.83 | 5.92
| 2017-02-11 | 61.2 | 58% | 80 | 49 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3705 | 3607 | 3607 | 3551 | 3659 | 45 | 0 | 47 | 0 | 64 | 0 | 108 | -56 | 155 | 98.36% | 154.375 | 95.84% | 100% | 98.08% | 10.763 | 172.29 | 1854.3573 | 30.881 | 937 | 28935.497 | 8670.7559 | 150.2917 | 0 | 0 | 0 | 0 | 3 | 1440 | 0 |  | 1079 | 1124 | 1456 | 45 | 8670.7559 | 8670.7559 | 2.021 | 2.021 | 31.58 | 28.55 | 24.21 | 30.24 | 960.71 | 50 | 0.9207 | 87.47 | 85.74 | -1.73 | 12586 | 12236 | -350 | 4.042 | 24 | 24 | 11.73 | 0
Week 7 | 2017-02-12 | 62.4 | 60.3% | 79 | 50 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3705 | 3593 | 3482 | 3444 | 3550 | 45 | 0 | 46 | 0 | 64 | 0 | 106 | -38 | 153 | 96.68% | 154.375 | 92.96% | 100% | 94.84% | 10.79 | 172.21 | 1858.1459 | 29.902 | 936 | 27988.272 | 8666.2073 | 149.7083 | 0 | 0 | 0 | 0 | 8 | 1440 | 0 |  | 1088 | 1177 | 1345 | 89 | 8666.2073 | 8666.2073 | 1.366 | 1.356 | 31.69 | 28.79 | 24.09 | 30.11 | 1001.9 | 50.05 | 0.919 | 88.79 | 85.72 | -3.07 | 12588 | 12250 | -338 | 2.722 | 24 | 24 | 14.28 | 6.75
| 2017-02-13 | 65.79 | 56.36% | 79 | 55 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3692 | 3586 | 3535 | 3497 | 3599 | 45 | 0 | 46 | 0 | 64 | 0 | 102 | -38 | 154 | 97.38% | 153.8333 | 94.72% | 100% | 96.77% | 10.8 | 172.85 | 1866.78 | 30.464 | 939 | 28605.696 | 8713.8908 | 149.4167 | 0 | 0 | 0 | 0 | 5 | 1440 | 0 |  | 1075 | 1106 | 1418 | 31 | 8713.8908 | 8713.8908 | 1.91 | 1.91 | 31.41 | 28.46 | 23.8 | 29.89 | 1004.04 | 50.04 | 0.9188 | 89.09 | 85.62 | -3.47 | 12597 | 12252 | -345 | 3.82 | 24 | 24 | 15.266 | 7.166
| 2017-02-14 | 66.43 | 59.2% | 78 | 54 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3693 | 3583 | 3583 | 3519 | 3628 | 45 | 0 | 46 | 0 | 64 | 0 | 109 | -64 | 154 | 98.16% | 153.875 | 95.29% | 100% | 97.42% | 10.82 | 172.26 | 1863.8532 | 30.588 | 941 | 28783.308 | 8709.054 | 149.2917 | 0 | 0 | 0 | 0 | 4 | 1440 | 0 |  | 1081 | 1099 | 1448 | 18 | 8709.054 | 8709.054 | 2.07 | 2.07 | 31.34 | 28.54 | 23.53 | 30.01 | 1003.08 | 50.03 | 0.9195 | 90.08 | 85.67 | -4.41 | 12561 | 12236 | -325 | 4.14 | 24 | 24 | 15.5 | 6.08
| 2017-02-15 | 70.16 | 60.4% | 82 | 59 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3670 | 3580 | 3521 | 3475 | 3583 | 46 | 0 | 45 | 0 | 64 | 0 | 108 | -46 | 153 | 97.58% | 152.9167 | 94.69% | 100% | 96.77% | 10.786 | 168.81 | 1820.7847 | 30.301 | 940 | 28482.94 | 8720.4963 | 149.1667 | 0 | 0 | 0 | 0 | 5 | 1440 | 0 |  | 1103 | 1077 | 1403 | -26 | 8720.4963 | 8720.4963 | 1.773 | 1.76 | 31.45 | 29 | 23.15 | 29.8 | 1001.1 | 50.07 | 0.9206 | 93.32 | 85.69 | -7.63 | 12500 | 12309 | -191 | 3.533 | 24 | 24 | 24 | 6.55
| 2017-02-16 | 68 | 66% | 75 | 61 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3696 | 3573 | 3573 | 3505 | 3612 | 46 | 0 | 45 | 0 | 64 | 0 | 107 | -68 | 153 | 98.37% | 154 | 94.83% | 100% | 97.42% | 10.79 | 169.61 | 1830.0919 | 30.602 | 939 | 28735.278 | 8720.505 | 148.875 | 0 | 0 | 0 | 0 | 4 | 1440 | 0 |  | 1106 | 1074 | 1432 | -32 | 8720.505 | 8720.505 | 1.971 | 1.971 | 31.6 | 29.11 | 23.18 | 29.65 | 1000.33 | 50.02 | 0.9196 | 93.88 | 85.77 | -8.11 | 12523 | 12337 | -186 | 3.942 | 24 | 24 | 24 | 7.67
| 2017-02-17 | 70.1 | 59% | 81 | 62 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3677 | 3559 | 3559 | 3509 | 3617 | 46 | 0 | 45 | 0 | 63 | 0 | 108 | -50 | 154 | 97.86% | 153.2083 | 95.43% | 100% | 98.05% | 10.81 | 171.08 | 1849.3748 | 30.595 | 940 | 28759.3 | 8722.9053 | 148.2917 | 0 | 0 | 0 | 0 | 3 | 1440 | 0 |  | 1098 | 1075 | 1444 | -23 | 8722.9053 | 8722.9053 | 2.038 | 2.038 | 31.43 | 28.97 | 23.2 | 29.66 | 999.4 | 50.05 | 0.9195 | 93.14 | 85.76 | -7.38 | 12538 | 12338 | -200 | 4.076 | 24 | 24 | 24 | 7.4
| 2017-02-18 | 72.1 | 62.1% | 82 | 63 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3667 | 3551 | 3551 | 3492 | 3600 | 45 | 0 | 44 | 0 | 63 | 0 | 108 | -59 | 153 | 98.04% | 152.7917 | 95.23% | 100% | 98.03% | 10.76 | 169.28 | 1821.4528 | 30.579 | 939 | 28713.681 | 8744.3109 | 147.9583 | 0 | 0 | 0 | 0 | 3 | 1440 | 0 |  | 1088 | 1064 | 1448 | -24 | 8744.3109 | 8744.3109 | 2.124 | 2.124 | 31.2 | 28.85 | 23.14 | 29.47 | 998.4 | 50.04 | 0.9205 | 93.38 | 85.84 | -7.54 | 12615 | 12420 | -195 | 4.248 | 24 | 24 | 24 | 7.3
Week 8 | 2017-02-19 | 73 | 67.2% | 83 | 65 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3662 | 3522 | 3522 | 3463 | 3572 | 45 | 0 | 44 | 0 | 63 | 0 | 109 | -59 | 152 | 97.92% | 152.5833 | 94.57% | 100% | 98.03% | 10.7 | 166.25 | 1778.875 | 30.446 | 937 | 28527.902 | 8751.596 | 146.75 | 0 | 0 | 0 | 0 | 3 | 1440 | 0 |  | 1078 | 1051 | 1443 | -27 | 8751.596 | 8751.596 | 2.154 | 2.133 | 31.1 | 28.6 | 22.9 | 29.1 | 993.1 | 50.07 | 0.9213 | 93.8 | 85.8 | -8 | 12635 | 12462 | -173 | 4.287 | 24 | 24 | 24 | 8.05
| 2017-02-20 | 69 | 45.7% | 77 | 61 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3692 | 3556 | 3556 | 3512 | 3619 | 45 | 0 | 45 | 0 | 63 | 0 | 107 | -44 | 154 | 97.92% | 153.8333 | 95.12% | 100% | 98.04% | 10.66 | 167.62 | 1786.8292 | 30.813 | 938 | 28902.594 | 8738.4462 | 148.1667 | 0 | 0 | 0 | 0 | 3 | 1440 | 0 |  | 1082 | 1085 | 1452 | 3 | 8738.4462 | 8738.4462 | 2.053 | 2.053 | 31.3 | 28.7 | 23.5 | 28.9 | 988.5 | 50.04 | 0.9211 | 90.8 | 85.5 | -5.3 | 12610 | 12231 | -379 | 4.106 | 24 | 24 | 20.77 | 6.95
| 2017-02-21 | 65.1 | 52.5% | 80 | 53 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3689 | 3567 | 3567 | 3507 | 3614 | 45 | 0 | 46 | 0 | 63 | 0 | 107 | -60 | 153 | 98.42% | 153.7083 | 95.07% | 100% | 98.05% | 10.56 | 164.02 | 1732.0512 | 30.904 | 936 | 28926.144 | 8742.0003 | 148.625 | 0 | 0 | 0 | 0 | 3 | 1440 | 0 |  | 1070 | 1100 | 1444 | 30 | 8742.0003 | 8742.0003 | 1.994 | 1.973 | 31.3 | 28.5 | 23.9 | 28.8 | 989.5 | 50.03 | 0.922 | 88 | 85.5 | -2.5 | 12644 | 12313 | -331 | 3.967 | 24 | 24 | 14.68 | 7.03
| 2017-02-22 | 65.5 | 48.2% | 81 | 52 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3690 | 3559 | 3559 | 3500 | 3607 | 44 | 0 | 46 | 0 | 63 | 0 | 107 | -59 | 152 | 98.88% | 153.75 | 94.85% | 100% | 98.04% | 10.54 | 162.91 | 1717.0714 | 31.001 | 935 | 28985.935 | 8772.2875 | 148.2917 | 0 | 0 | 0 | 0 | 3 | 1440 | 0 |  | 1064 | 1104 | 1439 | 40 | 8772.2875 | 8772.2875 | 1.956 | 1.956 | 31.14 | 28.52 | 24.23 | 28.92 | 994.79 | 49.99 | 0.9224 | 87.21 | 85.49 | -1.72 | 12750 | 12401 | -349 | 3.912 | 24 | 24 | 13.73 | 6.8
| 2017-02-23 | 66.7 | 49.3% | 82 | 54 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3689 | 3575 | 3575 | 3526 | 3635 | 44 | 0 | 46 | 0 | 63 | 0 | 109 | -49 | 154 | 98.35% | 153.7083 | 95.58% | 100% | 98.69% | 10.56 | 163.96 | 1731.4176 | 31.135 | 936 | 29142.36 | 8756.0345 | 148.9583 | 0 | 0 | 0 | 0 | 2 | 1440 | 0 |  | 1072 | 1102 | 1461 | 30 | 8756.0345 | 8756.0345 | 2.088 | 2.078 | 31.27 | 28.43 | 24.14 | 28.8 | 997.58 | 50.02 | 0.9227 | 88.36 | 85.53 | -2.83 | 12623 | 12371 | -252 | 4.166 | 24 | 24 | 14.8 | 2.67
| 2017-02-24 | 67 | 54.3% | 82 | 55 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3687 | 3562 | 3562 | 3509 | 3616 | 44 | 0 | 45 | 0 | 63 | 0 | 107 | -53 | 155 | 97.2% | 153.625 | 95.17% | 100% | 98.68% | 10.58 | 161.41 | 1707.7178 | 30.925 | 936 | 28945.8 | 8735.6848 | 148.4167 | 0 | 0 | 0 | 0 | 2 | 1440 | 0 |  | 1072 | 1093 | 1451 | 21 | 8735.6848 | 8735.6848 | 2.046 | 2.048 | 31.24 | 28.49 | 23.59 | 28.78 | 999.13 | 50 | 0.9232 | 88.92 | 85.59 | -3.33 | 12641 | 12401 | -240 | 4.094 | 24 | 24 | 15.75 | 5.5
| 2017-02-25 | 68.2 | 54.2% | 81 | 56 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3683 | 3584 | 3584 | 3526 | 3635 | 45 | 0 | 45 | 0 | 63 | 0 | 109 | -58 | 155 | 97.72% | 153.4583 | 95.74% | 100% | 98.8% | 10.55 | 160.98 | 1698.339 | 31.188 | 936 | 29191.968 | 8760.7223 | 149.3333 | 0 | 0 | 0 | 0 | 2 | 1320 | 0 |  | 1075 | 1086 | 1474 | 11 | 8760.7223 | 8760.7223 | 2.187 | 2.192 | 31.7 | 28.57 | 23.08 | 28.55 | 996.9 | 50.01 | 0.9237 | 89.87 | 85.59 | -4.28 | 12635 | 12451 | -184 | 4.379 | 24 | 24 | 18.4 | 5.18
Week 9 | 2017-02-26 | 68.9 | 57.3% | 83 | 56 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3676 | 3577 | 3577 | 3513 | 3621 | 45 | 0 | 45 | 0 | 63 | 0 | 108 | -64 | 154 | 97.97% | 153.1667 | 95.57% | 100% | 99.37% | 10.515 | 159.82 | 1680.5073 | 31.089 | 936 | 29099.304 | 8761.6884 | 149.0417 | 0 | 0 | 0 | 0 | 1 | 1380 | 0 |  | 1074 | 1080 | 1467 | 6 | 8761.6884 | 8761.6884 | 2.187 | 2.187 | 31.7 | 28.55 | 23 | 28.5 | 994.2 | 50.04 | 0.9264 | 90.51 | 85.63 | -4.88 | 12636 | 12489 | -147 | 4.374 | 24 | 24 | 19.48 | 6.65
| 2017-02-27 | 69.98 | 53.76% | 81 | 55 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3665 | 3552 | 3552 | 3497 | 3606 | 45 | 0 | 45 | 0 | 63 | 0 | 109 | -55 | 153 | 98.2% | 152.7083 | 95.42% | 100% | 98.04% | 10.53 | 159.11 | 1675.4283 | 30.931 | 937 | 28982.347 | 8766.8788 | 148 | 0 | 0 | 0 | 0 | 3 | 1440 | 0 |  | 1083 | 1077 | 1446 | -6 | 8766.8788 | 8766.8788 | 2.074 | 2.057 | 31.65 | 28.69 | 23.02 | 28.26 | 994.92 | 50.02 | 0.9242 | 91.14 | 85.59 | -5.55 | 12599 | 12520 | -79 | 4.131 | 24 | 24 | 21.38 | 10.13
| 2017-02-28 | 71.7 | 56% | 82 | 64 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 3677 | 3549 | 3549 | 3496 | 3606 | 45 | 0 | 44 | 0 | 63 | 0 | 110 | -53 | 152 | 98.85% | 153.2083 | 95.08% | 100% | 98.11% | 10.49 | 157.18 | 1648.8182 | 30.915 | 937 | 28967.355 | 8757.4866 | 147.875 | 0 | 0 | 0 | 0 | 3 | 1380 | 0 |  | 1091 | 1067 | 1448 | -24 | 8757.4866 | 8757.4866 | 2.088 | 2.093 | 31.2 | 28.8 | 22.9 | 28.1 | 995.4 | 50.06 | 0.9249 | 92.61 | 85.68 | -6.93 | 12562 | 12552 | -10 | 4.181 | 24 | 24 | 24 | 6.92
| 2017-03-01 | 68.5 | 61.9% | 81 | 60 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3687 | 3534 | 3534 | 3475 | 3582 | 46 | 0 | 45 | 0 | 63 | 0 | 107 | -59 | 153 | 97.55% | 153.625 | 94.25% | 100% | 97.4% | 10.47 | 158.12 | 1655.5164 | 30.466 | 938 | 28577.108 | 8700.0358 | 147.25 | 0 | 0 | 0 | 0 | 4 | 1440 | 0 |  | 1100 | 1073 | 1409 | -27 | 8700.0358 | 8700.0358 | 1.834 | 1.829 | 31.6 | 29 | 23.1 | 28.17 | 995.4 | 50 | 0.9249 | 93.08 | 85.68 | -7.4 | 12532 | 12563 | 31 | 3.663 | 24 | 24 | 24 | 7.1
| 2017-03-02 | 69.3 | 55.4% | 83 | 58 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3678 | 3564 | 3564 | 3510 | 3621 | 46 | 0 | 45 | 0 | 63 | 0 | 111 | -54 | 154 | 97.97% | 153.25 | 95.43% | 100% | 98.05% | 10.41 | 155.94 | 1623.3354 | 30.868 | 938 | 28954.184 | 8711.544 | 148.5 | 0 | 0 | 0 | 0 | 3 | 1440 | 0 |  | 1102 | 1079 | 1440 | -23 | 8711.544 | 8711.544 | 1.989 | 1.989 | 31.6 | 29 | 23.1 | 28.3 | 995.04 | 50 | 0.9262 | 92.5 | 85.6 | -6.9 | 12522 | 12540 | 18 | 3.978 | 24 | 24 | 24 | 7.6
| 2017-03-03 | 68.5 | 58.9% | 81 | 58 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3680 | 3558 | 3558 | 3499 | 3606 | 46 | 0 | 45 | 0 | 63 | 0 | 107 | -59 | 153 | 98.2% | 153.3333 | 95.08% | 100% | 97.4% | 10.45 | 155.3 | 1622.885 | 30.772 | 938 | 28864.136 | 8713.0669 | 148.25 | 0 | 0 | 0 | 0 | 4 | 1440 | 0 |  | 1104 | 1079 | 1423 | -25 | 8713.0669 | 8713.0669 | 1.907 | 1.907 | 31.6 | 29 | 23.2 | 28 | 992.79 | 50.02 | 0.9262 | 92.9 | 85.6 | -7.3 | 12514 | 12554 | 40 | 3.814 | 24 | 24 | 24 | 7.48
| 2017-03-04 | 67.74 | 60.88% | 80 | 56 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3683 | 3547 | 3547 | 3493 | 3602 | 46 | 0 | 45 | 0 | 63 | 0 | 109 | -54 | 152 | 98.74% | 153.4583 | 94.84% | 100% | 97.4% | 10.455 | 155.55 | 1626.2753 | 30.768 | 938 | 28860.384 | 8727.9299 | 147.7917 | 0 | 0 | 0 | 0 | 4 | 1440 | 0 |  | 1104 | 1075 | 1423 | -29 | 8727.9299 | 8727.9299 | 1.902 | 1.92 | 31.74 | 29.05 | 23.15 | 28.17 | 992 | 50.03 | 0.926 | 92.89 | 85.53 | -7.36 | 12519 | 12582 | 63 | 3.822 | 24 | 24 | 24 | 7.16
Week 10 | 2017-03-05 | 69.58 | 56.7% | 81 | 59 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3675 | 3253 | 3253 | 3206 | 3302 | 46 | 0 | 45 | 0 | 63 | 0 | 96 | -47 | 141 | 97.58% | 153.125 | 87.24% | 100% | 89.61% | 10.425 | 152.87 | 1593.6698 | 27.393 | 939 | 25722.027 | 8520.1799 | 135.5417 | 0 | 0 | 0 | 0 | 16 | 1440 | 0 |  | 1097 | 1075 | 1130 | -22 | 8520.1799 | 8520.1799 | 0.345 | 0.236 | 31.51 | 28.96 | 23.08 | 28.15 | 992.83 | 50.08 | 0.9271 | 92.44 | 85.53 | -6.91 | 12550 | 12545 | -5 | 0.581 | 24 | 24 | 24 | 7.3
| 2017-03-06 | 69 | 58.6% | 79 | 60 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3686 | 3430 | 3430 | 3372 | 3475 | 46 | 0 | 45 | 0 | 63 | 0 | 103 | -58 | 151 | 95.89% | 153.5833 | 91.48% | 100% | 94.81% | 10.44 | 153.91 | 1606.8204 | 29.466 | 939 | 27668.574 | 8681.9082 | 142.9167 | 0 | 0 | 0 | 0 | 8 | 1440 | 0 |  | 1095 | 1072 | 1308 | -23 | 8681.9082 | 8681.9082 | 1.402 | 1.36 | 31.58 | 28.89 | 22.91 | 28.16 | 991.4 | 50.04 | 0.9267 | 92.67 | 85.59 | -7.08 | 12545 | 12529 | -16 | 2.762 | 24 | 24 | 24 | 7.42
| 2017-03-07 | 67.5 | 67.9% | 79 | 62 | 24 | 0 | 7 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 3701 | 2348.5 | 2348.5 | 2328 | 2412 | 46 | 0 | 45 | 943 | 63 | 0 | 84 | -20.5 | 152 | 66.12% | 154.2083 | 62.9% | 80.86% | 65.97% | 3.25 | 167.44 | 544.18 | 20.922 | 939 | 19645.758 | 8672.6538 | 97.8542 | 0 | 0 | 20 | 68 | 22 | 1440 | 0 |  | 1095 | 352 | 965 | -743 | 8672.6538 | 8672.6538 | 2.564 | 0.678 | 31.75 | 28.92 | 22.97 | 29.53 | 990.83 | 50.01 | 0.9213 | 93.51 | 86.81 | -6.7 | 12555 | 12376 | -179 | 3.242 | 24 | 7.4 | 24 | 5.42
| 2017-03-08 | 67.6 | 66.9% | 83 | 59 | 6 | 9 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3688 | 2286.5 | 2286.5 | 2273 | 2357 | 47 | 1006 | 46 | 0 | 63 | 0 | 84 | -13.5 | 154 | 63.77% | 153.6667 | 61.63% | 78.95% | 63.57% | 10.3 | 152.45 | 1570.235 | 19.31 | 939 | 18132.09 | 8667.9828 | 95.2708 | 22 | 65 | 0 | 0 | 23 | 1440 | 0 |  | 310 | 1101 | 946 | 791 | 8667.9828 | 8667.9828 | 0.586 | 2.581 | 31.86 | 28.97 | 22.99 | 28.19 | 990.29 | 50 | 0.9269 | 94.76 | 86.42 | -8.34 | 12346 | 12256 | -90 | 3.167 | 6.47 | 24 | 5.25 | 1.6
| 2017-03-09 | 62.39 | 70.78% | 70 | 56 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3718 | 3580 | 3580 | 3531 | 3640 | 48 | 0 | 46 | 0 | 63 | 0 | 109 | -49 | 154 | 98.48% | 154.9167 | 94.97% | 100% | 96.18% | 10.215 | 152.38 | 1556.5617 | 31.018 | 939 | 29125.902 | 8689.4545 | 149.1667 | 0 | 0 | 0 | 0 | 6 | 1440 | 0 |  | 1156 | 1112 | 1372 | -44 | 8689.4545 | 8689.4545 | 1.655 | 1.655 | 32.39 | 29.73 | 23.55 | 27.86 | 988.9 | 50.02 | 0.9268 | 96.61 | 86.35 | -10.26 | 12230 | 12308 | 78 | 3.31 | 24 | 24 | 24 | 5.45
| 2017-03-10 | 62.61 | 67.18% | 76 | 54 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3706 | 3595 | 3595 | 3532 | 3641 | 48 | 0 | 47 | 0 | 63 | 0 | 109 | -63 | 154 | 98.51% | 154.4167 | 95.3% | 100% | 96.84% | 10.2 | 152.16 | 1552.032 | 31.022 | 939 | 29129.658 | 8686.7752 | 149.7917 | 0 | 0 | 0 | 0 | 5 | 1440 | 0 |  | 1144 | 1115 | 1382 | -29 | 8686.7752 | 8686.7752 | 1.665 | 1.64 | 32.58 | 29.56 | 23.68 | 27.89 | 988.6 | 50.02 | 0.9269 | 95.18 | 86.13 | -9.05 | 12286 | 12339 | 53 | 3.305 | 24 | 24 | 21.7 | 8.6
| 2017-03-11 | 62.05 | 61.07% | 72 | 51 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3708 | 3604 | 3518 | 3477 | 3582 | 46 | 0 | 47 | 0 | 63 | 0 | 105 | -41 | 154 | 96.92% | 154.5 | 93.77% | 100% | 97.49% | 10.22 | 152.3 | 1556.506 | 30.367 | 939 | 28514.613 | 8648.5818 | 150.1667 | 0 | 0 | 0 | 0 | 5 | 1126 | 0 |  | 1115 | 1123 | 1344 | 8 | 8648.5818 | 8648.5818 | 1.404 | 1.385 | 31.78 | 28.97 | 23.86 | 27.79 | 991.67 | 50.05 | 0.9269 | 91.39 | 85.97 | -5.42 | 12351 | 12314 | -37 | 2.789 | 24 | 24 | 14.3 | 3.81
Week 11 | 2017-03-12 | 63.3 | 58.4% | 76 | 53 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 3702 | 3584 | 3584 | 3535 | 3644 | 46 | 0 | 46 | 0 | 63 | 0 | 109 | -49 | 153 | 99.24% | 154.25 | 95.49% | 100% | 97.53% | 10.25 | 152.74 | 1565.585 | 31.039 | 939 | 29145.621 | 8687.7528 | 149.3333 | 0 | 0 | 0 | 0 | 4 | 1380 | 0 |  | 1112 | 1117 | 1415 | 5 | 8687.7528 | 8687.7528 | 1.808 | 1.808 | 19.3 | 28.9 | 23.8 | 27.6 | 996.1 | 50 | 0.9271 | 91.4 | 85.8 | -5.6 | 12359 | 12363 | 4 | 3.616 | 24 | 24 | 14.6 | 5.1
| 2017-03-13 | 64.8 | 55.2% | 76 | 54 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3697 | 3582 | 3582 | 3530 | 3637 | 46 | 0 | 46 | 0 | 63 | 0 | 107 | -52 | 154 | 98.4% | 154.0417 | 95.48% | 100% | 97.42% | 10.012 | 153.24 | 1534.2389 | 31.001 | 939 | 29109.939 | 8681.0702 | 149.25 | 0 | 0 | 0 | 0 | 4 | 1440 | 0 |  | 1111 | 1106 | 1420 | -5 | 8681.0702 | 8681.0702 | 1.846 | 1.844 | 31.4 | 28.9 | 23.7 | 27.7 | 996.4 | 50.05 | 0.9271 | 91.7 | 85.6 | -6.1 | 12385 | 12427 | 42 | 3.69 | 24 | 24 | 15.4 | 5.6
| 2017-03-14 | 65.6 | 53.5% | 76 | 54 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3697 | 3580 | 3580 | 3528 | 3640 | 46 | 0 | 46 | 0 | 63 | 0 | 112 | -52 | 154 | 98.48% | 154.0417 | 95.43% | 100% | 97.42% | 10.002 | 151.91 | 1519.4038 | 30.98 | 939 | 29090.22 | 8676.1972 | 149.1667 | 0 | 0 | 0 | 0 | 4 | 1440 | 0 |  | 1115 | 1103 | 1422 | -12 | 8676.1972 | 8676.1972 | 1.893 | 1.931 | 31.4 | 29.1 | 23.6 | 27.7 | 998.1 | 50.06 | 0.9274 | 92.3 | 85.6 | -6.7 | 12393 | 12464 | 71 | 3.824 | 24 | 24 | 17.3 | 2.3
| 2017-03-15 | 66.3 | 59.2% | 73 | 60 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3690 | 3584 | 3584 | 3526 | 3631 | 47 | 0 | 45 | 0 | 63 | 0 | 105 | -58 | 154 | 98.24% | 153.75 | 95.56% | 100% | 96.77% | 10 | 152.33 | 1523.3 | 31.173 | 939 | 29271.447 | 8733.6208 | 149.3333 | 0 | 0 | 0 | 0 | 5 | 1440 | 0 |  | 1139 | 1091 | 1401 | -48 | 8733.6208 | 8733.6208 | 1.752 | 1.752 | 31.9 | 29.5 | 23.4 | 27.6 | 997.08 | 50.01 | 0.9281 | 95.6 | 85.7 | -9.9 | 12336 | 12484 | 148 | 3.504 | 24 | 24 | 24 | 7.12
| 2017-03-16 | 70.4 | 57.2% | 81 | 61 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 15 | 47 | 3675 | 3606 | 3606 | 3545 | 3654 | 47 | 0 | 45 | 0 | 63 | 0 | 109 | -61 | 155 | 98.23% | 153.125 | 96.46% | 100% | 98.9% | 10.178 | 151.97 | 1546.7507 | 31.18 | 939 | 29278.02 | 8695.2809 | 150.25 | 0 | 0 | 0 | 0 | 5 | 493 | 0 |  | 1120 | 1082 | 1452 | -38 | 8695.2809 | 8695.2809 | 2.078 | 2.078 | 31.4 | 29.2 | 23.3 | 27.5 | 994.58 | 50.03 | 0.9276 | 95.3 | 85.7 | -9.6 | 12388 | 12526 | 138 | 4.156 | 24 | 24 | 24 | 9.75
| 2017-03-17 | 72.4 | 57.5% | 84 | 61 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3657 | 3603 | 3603 | 3539 | 3648 | 46 | 0 | 44 | 0 | 61 | 0 | 109 | -64 | 154 | 98.7% | 152.375 | 96.77% | 100% | 100% | 10.378 | 154.36 | 1601.9481 | 31.02 | 940 | 29158.8 | 8691.9322 | 150.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1107 | 1067 | 1474 | -40 | 8691.9322 | 8691.9322 | 2.263 | 2.261 | 31.2 | 28.9 | 23 | 27.5 | 992.22 | 50 | 0.9272 | 95.2 | 85.7 | -9.5 | 12414 | 12564 | 150 | 4.524 | 24 | 24 | 24 | 7.16
| 2017-03-18 | 73.4 | 55.5% | 85 | 63 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3653 | 3597 | 3597 | 3538 | 3646 | 46 | 0 | 44 | 0 | 62 | 0 | 108 | -59 | 155 | 98.01% | 152.2083 | 96.85% | 100% | 100% | 10.449 | 150.57 | 1573.3059 | 31.083 | 940 | 29218.02 | 8703.0316 | 149.875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1101 | 1064 | 1481 | -37 | 8703.0316 | 8703.0316 | 2.328 | 2.328 | 31.1 | 28.8 | 22.9 | 27.6 | 990.67 | 50.03 | 0.928 | 94.9 | 85.6 | -9.3 | 12420 | 12569 | 149 | 4.656 | 24 | 24 | 24 | 7.58
Week 12 | 2017-03-19 | 75.7 | 53.1% | 91 | 65 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3634 | 3282 | 3282 | 3237 | 3333 | 45 | 0 | 44 | 0 | 62 | 0 | 96 | -45 | 143 | 97.12% | 151.4167 | 89.08% | 100% | 91.39% | 10.832 | 150.54 | 1630.6493 | 28.12 | 940 | 26432.8 | 8669.5858 | 136.75 | 0 | 0 | 0 | 0 | 13 | 1440 | 0 |  | 1091 | 1057 | 1185 | -34 | 8669.5858 | 8669.5858 | 0.668 | 0.661 | 30.8 | 28.62 | 22.69 | 27.52 | 992.96 | 49.97 | 0.9281 | 94.66 | 85.64 | -9.02 | 12470 | 12547 | 77 | 1.329 | 24 | 24 | 24 | 7.63
| 2017-03-20 | 77 | 57.1% | 90 | 64 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3621 | 3401 | 3401 | 3350 | 3453 | 45 | 0 | 43 | 0 | 62 | 0 | 103 | -51 | 150 | 95.92% | 150.875 | 92.52% | 100% | 95.33% | 10.677 | 150.88 | 1610.9458 | 29.353 | 941 | 27621.173 | 8726.0056 | 141.7083 | 0 | 0 | 0 | 0 | 7 | 1440 | 0 |  | 1078 | 1047 | 1328 | -31 | 8726.0056 | 8726.0056 | 1.556 | 1.556 | 30.6 | 28.36 | 22.51 | 27.52 | 993.63 | 49.98 | 0.9283 | 94.84 | 85.63 | -9.21 | 12500 | 12595 | 95 | 3.112 | 24 | 24 | 24
| 2017-03-21 | 79.16 | 56.69% | 93 | 68 | 20 | 2 | 20 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 3606 | 3293 | 3293 | 2999 | 3099 | 45 | 101 | 43 | 81 | 62 | 222 | 102 | -294 | 151 | 85.51% | 150.25 | 83.17% | 89.91% | 86.96% | 10.677 | 155.83 | 1663.7969 | 27.74 | 942 | 26131.08 | 9268.0483 | 137.2083 | 15 | 137 | 12 | 157 | 2 | 1218 | 2 |  | 942 | 941 | 1216 | -1 | 9268.0483 | 9268.0483 | 1.952 | 1.952 | 30.51 | 25.24 | 20.85 | 25.56 | 992 | 49.92 | 0.9267 | 93.67 | 85.58 | -8.09 | 12622 | 12782 | 160 | 3.904 | 20 | 19.92 | 19.1667 | 9.3167
| 2017-03-22 | 75.54 | 62.3% | 86 | 65 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3637 | 3516 | 3516 | 3455 | 3567 | 45 | 0 | 43 | 0 | 63 | 0 | 112 | -61 | 153 | 97.14% | 151.5417 | 95% | 100% | 98.01% | 10.448 | 150.28 | 1570.1254 | 30.31 | 946 | 28673.26 | 8753.5124 | 146.5 | 0 | 0 | 0 | 0 | 3 | 1440 | 0 |  | 1070 | 1039 | 1458 | -31 | 8753.5124 | 8753.5124 | 2.286 | 2.286 | 30.83 | 28.02 | 22.29 | 27.48 | 992 | 49.99 | 0.9281 | 94.88 | 85.77 | -9.11 | 12470 | 12591 | 121 | 4.572 | 24 | 24 | 24 | 6.75
| 2017-03-23 | 75.29 | 60.35% | 87 | 64 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3638 | 3522 | 3522 | 3459 | 3569 | 45 | 0 | 44 | 0 | 64 | 0 | 110 | -63 | 152 | 97.83% | 151.5833 | 95.08% | 100% | 98.04% | 10.525 | 148.9 | 1567.1725 | 30.325 | 946 | 28687.45 | 8746.6385 | 146.75 | 0 | 0 | 0 | 0 | 3 | 1440 | 0 |  | 1071 | 1045 | 1453 | -26 | 8746.6385 | 8746.6385 | 2.215 | 2.215 | 30.86 | 28.12 | 22.47 | 27.3 | 992.38 | 50.05 | 0.9279 | 94.65 | 85.78 | -8.87 | 12486 | 12580 | 94 | 4.43 | 24 | 24 | 24 | 7.78
| 2017-03-24 | 78.9 | 53.7% | 94 | 66 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3615 | 3522 | 3522 | 3453 | 3563 | 44 | 0 | 43 | 0 | 64 | 0 | 110 | -69 | 152 | 97.67% | 150.625 | 95.52% | 100% | 98.01% | 10.523 | 151.64 | 1595.7077 | 30.184 | 945 | 28523.88 | 8722.7303 | 146.75 | 0 | 0 | 0 | 0 | 3 | 1440 | 0 |  | 1060 | 1043 | 1460 | -17 | 8722.7303 | 8722.7303 | 2.274 | 2.274 | 30.43 | 27.91 | 22.3 | 27.3 | 999.33 | 50 | 0.9281 | 93.9 | 85.73 | -8.17 | 12514 | 12557 | 43 | 4.548 | 24 | 24 | 24 | 7.5
| 2017-03-25 | 79.4 | 57.3% | 92 | 71 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3598 | 3341 | 3341 | 3294 | 3396 | 44 | 0 | 43 | 0 | 64 | 0 | 102 | -47 | 147 | 96.26% | 149.9167 | 91.55% | 100% | 94.04% | 10.545 | 154.11 | 1625.09 | 28.79 | 944.5442 | 27193.4275 | 8748.791 | 139.2083 | 0 | 0 | 0 | 0 | 9 | 1440 | 0 |  | 1055 | 1034 | 1307 | -21 | 8748.791 | 8748.791 | 1.469 | 1.457 | 30.37 | 27.81 | 22.14 | 27.23 | 992.67 | 50 | 0.8493 | 94.33 | 85.79 | -8.54 | 12547 | 12566 | 19 | 2.926 | 23.16 | 23.52 | 24 | 8.08
Week 13 | 2017-03-26 | 82.4 | 53.7% | 97 | 70 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3573 | 3073 | 3073 | 3013 | 3109 | 43 | 0 | 43 | 0 | 64 | 0 | 96 | -60 | 135 | 95.96% | 148.875 | 84.33% | 100% | 86% | 10.555 | 151.35 | 1597.4992 | 25.974 | 945 | 24545.43 | 8676.7107 | 128.0417 | 0 | 0 | 0 | 0 | 21 | 1440 | 0 |  | 1042 | 1029 | 1038 | -13 | 8676.7107 | 43.25 | 0 | 0 | 30.04 | 27.6 | 21.93 | 27.22 | 993.38 | 49.97 | 0.9275 | 93.89 | 85.67 | -8.22 | 12595 | 12556 | -39 | 0 | 0 | 0 |  | 24 | 7.72
| 2017-03-27 | 83.5 | 55.8% | 96 | 71 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3565 | 3209 | 3209 | 3153 | 3256 | 43 | 0 | 42 | 0 | 64 | 0 | 103 | -56 | 142 | 95.54% | 148.5417 | 88.44% | 100% | 90.6% | 10.53 | 150.79 | 1587.8187 | 27.423 | 944 | 25887.312 | 8713.9647 | 133.7083 | 0 | 0 | 0 | 0 | 14 | 1440 | 0 |  | 1033 | 1016 | 1207 | -17 | 8713.9647 | 50.2917 | 0.996 | 1 | 29.9 | 27.4 | 21.8 | 26.9 | 991.5 | 49.95 | 0.9287 | 94.1 | 85.7 | -8.4 | 12631 | 12653 | 22 | 1.996 | 13 | 13 |  | 24 | 6.92
| 2017-03-28 | 83.8 | 58.5% | 94 | 73 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3558 | 3212 | 3212 | 3160 | 3263 | 43 | 0 | 42 | 0 | 64 | 0 | 103 | -52 | 142 | 95.75% | 148.25 | 88.81% | 100% | 91.28% | 10.33 | 153.03 | 1580.7999 | 27.59 | 944 | 26044.96 | 8742.3291 | 133.8333 | 0 | 0 | 0 | 0 | 13 | 1440 | 0 |  | 1027 | 1009 | 1227 | -18 | 8742.3291 | 51.125 | 1.131 | 1.131 | 29.9 | 27.3 | 21.7 | 26.7 | 990.3 | 49.97 | 0.9284 | 94.4 | 85.7 | -8.7 | 12638 | 12662 | 24 | 2.262 | 24 | 24 |  | 24 | 7.5
| 2017-03-29 | 85.8 | 53.8% | 98 | 74 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 3543 | 3312 | 3312 | 3253 | 3359 | 43 | 0 | 42 | 0 | 64 | 0 | 106 | -59 | 147 | 95.21% | 147.625 | 91.81% | 100% | 94.46% | 10.105 | 156.33 | 1579.7147 | 28.734 | 944 | 27124.896 | 8824.0426 | 138 | 0 | 0 | 0 | 0 | 9 | 1320 | 0 |  | 1021 | 1011 | 1327 | -10 | 8824.0426 | 55.2917 | 1.733 | 1.707 | 29.7 | 27.17 | 21.84 | 26.68 | 989.4 | 50.03 | 0.9275 | 93.17 | 85.59 | -7.58 | 12649 | 12689 | 40 | 3.44 | 24 | 24 |  | 24 | 7.3
| 2017-03-30 | 85.6 | 52.3% | 98 | 74 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3546 | 3269 | 3269 | 3208 | 3313 | 42 | 0 | 42 | 0 | 64 | 0 | 105 | -61 | 150 | 92.03% | 147.75 | 90.47% | 100% | 92.57% | 10 | 153.77 | 1537.7 | 28.153 | 944 | 26576.432 | 8763.7569 | 136.2083 | 0 | 0 | 0 | 0 | 11 | 1440 | 0 |  | 1022 | 1013 | 1278 | -9 | 8763.7569 | 53.25 | 1.404 | 1.402 | 29.7 | 27.17 | 21.74 | 26.92 | 988.71 | 49.99 | 0.9279 | 93.65 | 85.59 | -8.06 | 12644 | 12654 | 10 | 2.806 | 24 | 24 |  | 24 | 7.58
| 2017-03-31 | 86.8 | 52.8% | 99 | 74 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3525 | 3159 | 3159 | 3103 | 3205 | 42 | 0 | 42 | 0 | 64 | 0 | 102 | -56 | 142 | 94.04% | 146.875 | 88.03% | 100% | 89.86% | 9.786 | 149.1 | 1459.0926 | 27.168 | 944 | 25646.592 | 8735.3157 | 131.625 | 0 | 0 | 0 | 0 | 15 | 1440 | 0 |  | 1016 | 1008 | 1181 | -8 | 8735.3157 | 49.2083 | 0.937 | 0.891 | 29.54 | 27.08 | 21.69 | 26.77 | 989.13 | 50.02 | 0.9293 | 93.69 | 85.64 | -8.05 | 12674 | 12672 | -2 | 1.828 | 24 | 24 |  | 24 | 8.42
| 2017-04-01 | 86.1 | 53.6% | 98 | 76 | 24 | 0 | 11 | 34 | 0 | 0 | 0 | 0 | 10 | 0 | 3537 | 2529 | 2529 | 2511 | 2607 | 42 | 0 | 42 | 668 | 62 | 0 | 96 | -18 | 148 | 73.4% | 147.375 | 70.99% | 86.66% | 74.44% | 4.96 | 163.61 | 811.5056 | 23.698 | 943 | 22347.214 | 9222.907 | 105.375 | 0 | 0 | 17 | 78 | 29 | 840 | 0 |  | 1014 | 526 | 1067 | -488 | 9222.907 | 44.4583 | 2.434 | 1.112 | 29.6 | 27.09 | 22 | 23.83 | 988.08 | 49.98 | 0.9248 | 93.76 | 86.49 | -7.27 | 12683 | 12330 | -353 | 3.546 | 23.18 | 11.32 |  | 24 | 8.46
Week 14 | 2017-04-02 | 87.2 | 50.14% | 102 | 71 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3522 | 3038 | 3038 | 2983 | 3082 | 42 | 0 | 43 | 0 | 62 | 0 | 99 | -55 | 133 | 96.55% | 146.75 | 84.7% | 100% | 85.71% | 9 | 157.79 | 1420.11 | 26.012 | 944 | 24555.328 | 8707.8237 | 126.5833 | 0 | 0 | 0 | 0 | 21 | 1440 | 0 |  | 1017 | 1037 | 1028 | 20 | 8707.8237 | 42.8333 | 0 | 0 | 29.51 | 27.09 | 22.16 | 24 | 986.1 | 50.05 | 0.9267 | 93.1 | 86.41 | -6.69 | 12679 | 12261 | -418 | 0 | 0 | 0 |  | 24 | 6.95
| 2017-04-03 | 86.41 | 45.79% | 100 | 74 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 12 | 49 | 3536 | 3252 | 3252 | 3192 | 3297 | 42 | 0 | 43 | 0 | 62 | 0 | 105 | -60 | 146 | 94.09% | 147.3333 | 90.27% | 100% | 93.98% | 9.025 | 156.54 | 1412.7735 | 28.045 | 943 | 26446.435 | 8727.8222 | 135.5 | 0 | 0 | 0 | 0 | 19 | 671 | 0 |  | 1018 | 1042 | 1237 | 24 | 8727.8222 | 51.5417 | 1.171 | 1.171 | 29.59 | 27.12 | 22.31 | 24.37 | 985.9 | 49.99 | 0.927 | 92.89 | 86.37 | -6.52 | 12665 | 12319 | -346 | 2.342 | 12.98 | 12.95 |  | 24 | 7.66
| 2017-04-04 | 85 | 54% | 96 | 74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3549 | 3463 | 3463 | 30 | 31 | 42 | 1418 | 43 | 1418 | 62 | 1418 | 24 | -3433 | 31 | 4.167% | 147.875 | 0.8453% | 1.528% | 0.3222% | 0 | 156.54 | 0 | 0.714 | 943 | 673.302 | 22443.4 | 144.2917 | 33 | 22 | 34 | 22 | 49 | 22 | 23 |  | 9 | 9 | 13 | 0 | 22443.4 | 0.54167 | 0 | 0 | 0 | 0.536 | 0.631 | 0.169 | 984.21 | 50.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16667 | 0.17 |  | 0 | 0
| 2017-04-05 | 81.8 | 59% | 94 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3574 | 3473 | 3473 | 0 | 0 | 42 | 1440 | 43 | 1440 | 63 | 1440 | 19 | -3473 | 0 | no data | 148.9167 | no data | 0% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 144.7083 | 0 | 0 | 0 | 0 | 0 | 0 | 19 |  | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 981.6 | 50.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 6
| 2017-04-06 | 76 | 56% | 85 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3636 | 3480 | 3480 | 0 | 0 | 43 | 1440 | 44 | 1440 | 63 | 1440 | 13 | -3480 | 0 | no data | 151.5 | no data | 0% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 13 |  | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 982.7 | 50.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
| 2017-04-07 | 73 | 48% | 85 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3648 | 3487 | 3487 | 0 | 0 | 43 | 1440 | 44 | 1440 | 63 | 1440 | 12 | -3487 | 0 | no data | 152 | no data | 0% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 145.2917 | 0 | 0 | 0 | 0 | 0 | 0 | 12 |  | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 988.5 | 50.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
| 2017-04-08 | 75.2 | 47.4% | 88 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3635 | 3491 | 3491 | 0 | 0 | 43 | 1440 | 44 | 1440 | 63 | 1440 | 13 | -3491 | 0 | no data | 151.4583 | no data | 0% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 145.4583 | 0 | 0 | 0 | 0 | 0 | 0 | 13 |  | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 993.92 | 50.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Week 15 | 2017-04-09 | 77.6 | 41.4% | 92 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3612 | 3492 | 3492 | 0 | 0 | 43 | 1440 | 44 | 1440 | 63 | 1440 | 13 | -3492 | 0 | no data | 150.5 | no data | 0% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 145.5 | 0 | 0 | 0 | 0 | 0 | 0 | 13 |  | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 994.1 | 50.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
| 2017-04-10 | 81.4 | 37.5% | 97 | 67 | 11 | 4 | 11 | 10 | 0 | 0 | 0 | 0 | 10 | 30 | 3581 | 3462 | 3462 | 1593 | 1650 | 43 | 741 | 44 | 635 | 60 | 762 | 63 | -1869 | 149 | 46.14% | 149.2083 | 44.48% | 50.15% | 47.71% | 4.3 | 162.46 | 698.578 | 14.452 | 957.573 | 13838.845 | 9125.8148 | 144.25 | 27 | 35 | 21 | 135 | 29 | 48 | 6 |  | 486 | 546 | 618 | 60 | 9125.8148 | 25.75 | 1.084 | 0.467 | 29.5 | 25.5 | 21.2 | 25.2 | 991.3 | 50.06 | 0.9265 | 91.5 | 85.9 | -5.6 | 12220 | 12132 | -88 | 1.551 | 11 | 10.83 |  | 9.97 | 0
| 2017-04-11 | 85.7 | 34.8% | 101 | 70 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3536 | 3460 | 3460 | 3397 | 3507 | 43 | 0 | 44 | 0 | 58 | 0 | 110 | -63 | 151 | 96.77% | 147.3333 | 96.07% | 100% | 100% | 8.889 | 154.45 | 1372.906 | 29.401 | 959 | 28195.559 | 8704.2876 | 144.1667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1041 | 1064 | 1402 | 23 | 8704.2876 | 58.4167 | 2.173 | 1.638 | 29.7 | 26.73 | 22.07 | 24.7 | 989.33 | 50.04 | 0.9287 | 91.95 | 86.01 | -5.94 | 12338 | 12155 | -183 | 3.811 | 24 | 23.05 |  | 24 | 2.75
| 2017-04-12 | 88.9 | 34.5% | 105 | 72 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 3506 | 3423 | 3423 | 3384 | 3497 | 43 | 0 | 44 | 0 | 59 | 0 | 113 | -39 | 153 | 95.23% | 146.0833 | 96.52% | 100% | 99.6% | 8.849 | 155.35 | 1374.6922 | 29.402 | 960 | 28225.92 | 8747.2258 | 142.625 | 0 | 0 | 0 | 0 | 14 | 60 | 0 |  | 1025 | 1053 | 1419 | 28 | 8747.2258 | 59.125 | 2.059 | 2.067 | 29.33 | 26.98 | 22.37 | 24.25 | 987.9 | 49.98 | 0.9293 | 91.71 | 85.98 | -5.73 | 12744 | 12551 | -193 | 4.126 | 24 | 24 |  | 24 | 6.95
| 2017-04-13 | 90.2 | 33.6% | 108 | 76 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3495 | 3158 | 3158 | 3105 | 3203 | 42 | 0 | 43 | 0 | 60 | 0 | 98 | -53 | 137 | 97.41% | 145.625 | 88.84% | 100% | 91.03% | 8.913 | 153.86 | 1371.3542 | 27.021 | 956 | 25832.076 | 8761.1691 | 131.5833 | 0 | 0 | 0 | 0 | 13 | 1440 | 0 |  | 1017 | 1044 | 1142 | 27 | 8761.1691 | 47.5833 | 0.632 | 0.531 | 29.18 | 26.89 | 22.17 | 24.38 | 987.1 | 49.95 | 0.9289 | 91.65 | 85.97 | -5.68 | 12795 | 12580 | -215 | 1.163 | 24 | 24 |  | 24 | 6.73
| 2017-04-14 | 90.66 | 35.13% | 106 | 76 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3488 | 3150 | 3150 | 3087 | 3187 | 42 | 0 | 43 | 0 | 60 | 0 | 100 | -63 | 137 | 96.93% | 145.3333 | 88.5% | 100% | 91.03% | 8.84 | 154.66 | 1367.1944 | 26.789 | 954 | 25556.706 | 8721.704 | 131.25 | 0 | 0 | 0 | 0 | 13 | 1440 | 0 |  | 1014 | 1036 | 1137 | 22 | 8721.704 | 47.375 | 0.629 | 0.522 | 29.13 | 26.74 | 21.9 | 24.22 | 984.79 | 49.95 | 0.928 | 91.93 | 85.91 | -6.02 | 12771 | 12563 | -208 | 1.151 | 24 | 24 |  | 24 | 8.1
| 2017-04-15 | 92.9 | 34.4% | 108 | 78 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3472 | 3132 | 3132 | 3066 | 3165 | 42 | 0 | 43 | 0 | 60 | 0 | 99 | -66 | 135 | 97.69% | 144.6667 | 88.31% | 100% | 91.03% | 8.85 | 154.57 | 1367.9445 | 26.94 | 940 | 25323.6 | 8705.657 | 130.5 | 0 | 0 | 0 | 0 | 13 | 1440 | 0 |  | 1004 | 1028 | 1133 | 24 | 8705.657 | 47.2083 | 0.602 | 0.543 | 28.9 | 27.09 | 22.33 | 24.1 | 983.6 | 49.95 | 0.9288 | 91.85 | 85.85 | -6 | 13060 | 12837 | -223 | 1.145 | 23 | 23 |  | 24 | 7.37
Week 16 | 2017-04-16 | 94.55 | 34.08% | 110 | 79 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3455 | 3007 | 3007 | 2944 | 3042 | 41 | 0 | 43 | 0 | 60 | 0 | 98 | -63 | 132 | 96.02% | 143.9583 | 85.21% | 100% | 88.19% | 8.896 | 157.51 | 1401.209 | 25.684 | 940 | 24142.96 | 8676.6878 | 125.2917 | 0 | 0 | 0 | 0 | 17 | 1440 | 0 |  | 995 | 1023 | 1024 | 28 | 8676.6878 | 42.6667 | 0 | 0 | 28.68 | 26.94 | 22.23 | 24.17 | 982.75 | 49.9 | 0.9283 | 91.33 | 85.6 | -5.73 | 13091 | 12869 | -222 | 0 | 0 | 0 |  | 24 | 7
| 2017-04-17 | 94.9 | 37% | 107 | 79 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3446 | 3074 | 3074 | 3020 | 3122 | 41 | 0 | 42 | 0 | 60 | 0 | 102 | -54 | 134 | 97.08% | 143.5833 | 87.64% | 100% | 90.21% | 8.901 | 155.6 | 1384.9956 | 26.308 | 945 | 24861.06 | 8690.7469 | 128.0833 | 0 | 0 | 0 | 0 | 14 | 1440 | 0 |  | 988 | 1021 | 1113 | 33 | 8690.7469 | 46.375 | 0.518 | 0.524 | 28.3 | 26.7 | 22.1 | 24.3 | 983.8 | 49.97 | 0.9289 | 90.9 | 85.4 | -5.5 | 13075 | 12827 | -248 | 1.042 | 13 | 13 |  | 23.7 | 7.6
| 2017-04-18 | 95.4 | 34.3% | 108 | 83 | 20 | 9 | 20 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 3437 | 3060 | 3060 | 2602 | 2692 | 41 | 187 | 42 | 133 | 60 | 206 | 92 | -458 | 134 | 83.71% | 143.2083 | 75.71% | 87.56% | 75.28% | 8.901 | 158.8 | 1413.4788 | 22.667 | 944 | 21397.648 | 8766.7666 | 127.5 | 17 | 44 | 14 | 78 | 19 | 1234 | 2 |  | 852 | 913 | 927 | 61 | 8766.7666 | 38.625 | 0.356 | 0.318 | 28.2 | 23.2 | 21.4 | 23.8 | 981.9 | 49.8 | 0.927 | 88.3 | 84.9 | -3.4 | 13280 | 12975 | -305 | 0.674 | 14.8 | 14.7 |  | 18.2 | 7.6
| 2017-04-19 | 96.4 | 34% | 108 | 85 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3430 | 2968 | 2968 | 2910 | 3010 | 41 | 0 | 42 | 0 | 60 | 0 | 100 | -58 | 130 | 96.47% | 142.9167 | 84.84% | 100% | 87.41% | 8.875 | 150.25 | 1333.4688 | 25.225 | 944 | 23812.4 | 8641.192 | 123.6667 | 0 | 0 | 0 | 0 | 18 | 1440 | 0 |  | 979 | 1018 | 1013 | 39 | 8641.192 | 42.2083 | 0 | 0 | 28.5 | 26.5 | 22.1 | 24.1 | 978.3 | 50 | 0.9288 | 90.6 | 85.7 | -4.9 | 12888 | 12663 | -225 | 0 | 0 | 0 |  | 24 | 7.5
| 2017-04-20 | 95.8 | 35.3% | 110 | 81 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3433 | 2962 | 2962 | 2903 | 3005 | 41 | 0 | 42 | 0 | 60 | 0 | 102 | -59 | 131 | 95.58% | 143.0417 | 84.56% | 100% | 87.41% | 8.891 | 145.45 | 1293.1959 | 25.147 | 944 | 23738.768 | 8622.7916 | 123.4167 | 0 | 0 | 0 | 0 | 18 | 1440 | 0 |  | 986 | 1010 | 1009 | 24 | 8622.7916 | 42.0417 | 0 | 0 | 28.5 | 26.5 | 22 | 24 | 977.63 | 50 | 0.9304 | 91.7 | 85.9 | -5.8 | 12676 | 12535 | -141 | 0 | 0 | 0 |  | 24 | 7.6
| 2017-04-21 | 95.2 | 36.5% | 107 | 82 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3446 | 2952 | 2952 | 2903 | 3000 | 41 | 0 | 42 | 0 | 60 | 0 | 97 | -49 | 129 | 96.9% | 143.5833 | 84.24% | 100% | 87.41% | 8.77 | 146.23 | 1282.4371 | 25.243 | 945 | 23854.635 | 8658.9983 | 123 | 0 | 0 | 0 | 0 | 18 | 1440 | 0 |  | 983 | 1009 | 1008 | 26 | 8658.9983 | 42 | 0 | 0 | 28.5 | 26.5 | 22 | 24.1 | 980.1 | 50.06 | 0.9301 | 91.9 | 85.9 | -6 | 12683 | 12537 | -146 | 0 | 0 | 0 |  | 23.9 | 6.9
| 2017-04-22 | 87.7 | 43.8% | 98 | 75 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3525 | 3032 | 3032 | 2970 | 3072 | 41 | 0 | 42 | 0 | 60 | 0 | 102 | -62 | 133 | 96.24% | 146.875 | 84.26% | 100% | 88.11% | 8.8 | 146 | 1284.8 | 25.741 | 945 | 24325.245 | 8622.9108 | 126.3333 | 0 | 0 | 0 | 0 | 17 | 1440 | 0 |  | 1021 | 1030 | 1021 | 9 | 8622.9108 | 42.5417 | 0 | 0 | 29.4 | 27.2 | 22.3 | 24.4 | 982 | 50.09 | 0.9297 | 93.2 | 86.2 | -7 | 12553 | 12466 | -87 | 0 | 0 | 0 |  | 24 | 7.83
Week 17 | 2017-04-23 | 82.7 | 56.9% | 93 | 74 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3572 | 3068 | 3068 | 3006 | 3104 | 43 | 0 | 43 | 0 | 60 | 0 | 98 | -62 | 133 | 97.24% | 148.8333 | 84.15% | 100% | 88.36% | 8.835 | 148.08 | 1308.2868 | 26.019 | 945 | 24587.955 | 8614.8509 | 127.8333 | 0 | 0 | 0 | 0 | 17 | 1440 | 0 |  | 1044 | 1032 | 1028 | -12 | 8614.8509 | 42.8333 | 0 | 0 | 30 | 27.69 | 22.39 | 24.51 | 984.1 | 50.07 | 0.9296 | 95.05 | 86.62 | -8.43 | 12489 | 12448 | -41 | 0 | 0 | 0 |  | 24 | 7.47
| 2017-04-24 | 81.9 | 54.5% | 93 | 70 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3575 | 3082 | 3082 | 3022 | 3120 | 44 | 0 | 43 | 0 | 60 | 0 | 98 | -60 | 134 | 97.01% | 148.9583 | 84.53% | 100% | 88.44% | 8.792 | 146.6 | 1288.9072 | 26.25 | 944 | 24780 | 8626.3756 | 128.4167 | 0 | 0 | 0 | 0 | 17 | 1440 | 0 |  | 1048 | 1039 | 1033 | -9 | 8626.3756 | 43.0417 | 0 | 0 | 30.1 | 27.8 | 22.59 | 24.42 | 988.3 | 50.04 | 0.9297 | 94.48 | 86.41 | -8.07 | 12476 | 12455 | -21 | 0 | 0 | 0 |  | 24 | 7.92
| 2017-04-25 | 86.1 | 45.6% | 98 | 74 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3534 | 3058 | 3058 | 3000 | 3098 | 43 | 0 | 43 | 0 | 60 | 0 | 98 | -58 | 133 | 97.06% | 147.25 | 84.89% | 100% | 88.36% | 8.82 | 144.65 | 1275.813 | 26.091 | 945 | 24655.995 | 8643.936 | 127.4167 | 0 | 0 | 0 | 0 | 17 | 1440 | 0 |  | 1032 | 1036 | 1030 | 4 | 8643.936 | 42.9167 | 0 | 0 | 29.64 | 27.49 | 22.58 | 24.35 | 989.5 | 50.05 | 0.9301 | 93.51 | 86.27 | -7.24 | 12530 | 12477 | -53 | 0 | 0 | 0 |  | 24
| 2017-04-26 | 89.69 | 41.13% | 102 | 78 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 3500 | 3206 | 3206 | 3149 | 3254 | 42 | 0 | 43 | 0 | 60 | 0 | 105 | -57 | 144 | 94.16% | 145.8333 | 89.97% | 100% | 94.14% | 8.83 | 145.85 | 1287.8555 | 27.578 | 944 | 26033.632 | 8676.2425 | 133.5833 | 0 | 0 | 0 | 0 | 17 | 720 | 0 |  | 1017 | 1029 | 1208 | 12 | 8676.2425 | 50.3333 | 1.05 | 1.02 | 29.24 | 27.23 | 22.45 | 24.22 | 988.17 | 50.09 | 0.93 | 92.86 | 86.03 | -6.83 | 12590 | 12504 | -86 | 2.07 | 13.06 | 12.983 |  | 24 | 4.75
| 2017-04-27 | 88.48 | 40.1% | 101 | 76 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 3510 | 3258 | 3258 | 3192 | 3301 | 43 | 0 | 43 | 0 | 60 | 0 | 109 | -66 | 144 | 95.52% | 146.25 | 90.94% | 100% | 94.86% | 8.825 | 147.75 | 1303.8937 | 27.915 | 944 | 26351.76 | 8664.0519 | 135.75 | 0 | 0 | 0 | 0 | 15 | 720 | 0 |  | 1026 | 1032 | 1243 | 6 | 8664.0519 | 51.7917 | 1.3 | 1.22 | 29.37 | 27.4 | 22.53 | 24.2 | 989.96 | 50.08 | 0.9296 | 92.92 | 86.02 | -6.9 | 12582 | 12508 | -74 | 2.52 | 24 | 24 |  | 24 | 7.1
| 2017-04-28 | 91.54 | 41.45% | 102 | 80 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 3485 | 3230 | 3230 | 3164 | 3270 | 42 | 0 | 43 | 0 | 60 | 0 | 106 | -66 | 145 | 93.97% | 145.2083 | 90.79% | 100% | 94.83% | 8.72 | 148.43 | 1294.3096 | 27.728 | 944 | 26175.232 | 8681.9032 | 134.5833 | 0 | 0 | 0 | 0 | 15 | 720 | 0 |  | 1008 | 1024 | 1238 | 16 | 8681.9032 | 51.5833 | 1.26 | 1.18 | 29.03 | 27.08 | 22.34 | 24.12 | 988.38 | 50.09 | 0.9293 | 92.6 | 85.81 | -6.79 | 12626 | 12519 | -107 | 2.44 | 23.766 | 23.266 |  | 24 | 7.82
| 2017-04-29 | 88 | 41% | 97 | 76 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 3517 | 3221 | 3221 | 3160 | 3268 | 42 | 0 | 43 | 0 | 60 | 0 | 108 | -61 | 145 | 93.91% | 146.5417 | 89.85% | 100% | 94.48% | 8.735 | 148.59 | 1297.9336 | 27.654 | 945 | 26133.03 | 8680.6847 | 134.2083 | 0 | 0 | 0 | 0 | 16 | 720 | 0 |  | 1024 | 1028 | 1216 | 4 | 8680.6847 | 50.6667 | 1.109 | 1.069 | 29.37 | 27.29 | 22.36 | 24.32 | 988.54 | 50.12 | 0.9293 | 92.9 | 86.03 | -6.87 | 12538 | 12476 | -62 | 2.178 | 12 | 12 |  | 24 | 6.95

## Feb
Monthly Operational Returns Kabirwala
2017-02-01
| Date | Site Avg. Ambient Temp.F | Site Avg. Relative Humidty % | Site Ambient Temp |  | Base load hours |  |  |  | Standby hours |  |  |  | Plant ambient corrected Max Load |  | Corrected Plant Capacity | Ambient Corrected Daclared Avail'y (MWH) | Plant WAPDA Dispatch (MWH) | Net Plant Export (MWH) | Gross Generation | CT1 Average Cap (MW) | CT1 Unavail minutes | CT2 Average Cap (MW) | CT2 Unavail minutes | ST Average Cap (MW) | ST Unavail minutes | Plant Aux Load including Colony Load MWH | Differenece (+/-) MW | Maximum Daily Generation | Daily Load Factor | Avg. Corrected Plant Capacity | Plant Capacity Factor | Plant Availability Factor | Equivalent Plant Availability | LBtu gas flow (mmscf/day) | 1 LBtu gas (Average Btu/scf) | LBTU MMBTU | 1 HBtu gas flow (mmscf/day) | 1 HBtu gas (Average Btu/scf) | HBTU MMBTU | HHV Net Heat Rate (Btu/Kwh) | Avg. declared availability | CT1 Derated MW | CT1 derated mintutes | CT-2 derated MW | CT-2 derated mintutes | ST derated MW | ST derated mintutes | WAPDA Backfeed (MWH) | CT-1 Gross Generation (MWH) | CT-2 Gross Generation (MWH) | STG Gross Generation (MWH) | CT-1 & CT-2 MWH difference | Base load Heat Rate | Part load Heat Rate | DB1 | DB2 | CT1 | CT1 Gas flow | CT2 Gas flow |  | Pamb | Freq. Hz | LBTU Gas Specific gravity | CT-1 compressor efficiency(%) | CT-2 compressor efficiency(%) |  | CT-1 Heat Rate (Btu/Kwh) | CT-2 Heat Rate (Btu/Kwh) |  | DB(1+2) | DB-1 Ops Hours | DB-2 Ops Hours | CT-1 Wetcomprssion Ops Hours | RO Operation Hours
[6 empty] | CT1 |  | CT2 |  | CT1 |  | CT2 | [43 empty] | mmscf/d | mmscf/d | WetC flow | HBTU KPPH | HBTU KPPH | LBTU KPPH | mbar | Hz | [7 empty] | mmscf/d
|  |  |  | Max | Min | hrs | min | hrs | min | hrs | min | hrs | min | hrs | min | [42 empty] | gpm
Week 5 | 2017-01-29 | 62.5 | 73.5% | 71 | 54 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3715 | 3104 | 3104 | 3051 | 3146 | 41 | 0 | 44 | 0 | 63 | 0 | 95 | -53 | 133 | 98.56% | 154.7917 | 82.13% | 100% | 87.84% | 11.29 | 172.79 | 1950.7991 | 25.854 | 935 | 24173.49 | 8562.5333 | 129.3333 | 0 | 0 | 0 | 0 | 18 | 1440 | 0 | 995 | 1064 | 1087 | 69 | 8562.5333 | 8562.5333 | 0.221 | 0 | 0 | 27.06 | 23.2 | 31.06 | 999.21 | 49.99 | 0.918 | 82.86 | 84.39 |  | 12794 | 12779 | -15 | 0.221 | 10.17 | 0 | 0 | 0
| 2017-01-30 | 63.2 | 72.1% | 73 | 56 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3710 | 3345.5 | 3345.5 | 3289 | 3390 | 44 | 0 | 44 | 0 | 63 | 0 | 101 | -56.5 | 151 | 93.54% | 154.5833 | 88.65% | 100% | 94.04% | 11.3 | 173.28 | 1958.064 | 28.291 | 937 | 26508.667 | 8655.1326 | 139.3958 | 0 | 0 | 0 | 0 | 9 | 1440 | 0 | 1061 | 1051 | 1278 | -10 | 8655.1326 | 8655.1326 | 1.269 | 1.095 | 16.81 | 28.3 | 23.01 | 30.73 | 997.21 | 50.01 | 0.9178 | 88.47 | 84.22 |  | 12562 | 12826 | 264 | 2.364 | 24 | 12.48 | 12.7 | 5.42
| 2017-01-31 | 61 | 76.6% | 71 | 51 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3714 | 3578 | 3578 | 3522 | 3628 | 46 | 0 | 44 | 0 | 63 | 0 | 106 | -56 | 153 | 98.8% | 154.75 | 94.83% | 100% | 98.04% | 11.45 | 172.7 | 1977.415 | 30.459 | 939 | 28601.001 | 8682.117 | 149.0833 | 0 | 0 | 0 | 0 | 3 | 1440 | 0 | 1124 | 1055 | 1449 | -69 | 8682.117 | 8682.117 | 2.044 | 2.044 | 27.87 | 29.35 | 23.04 | 30.72 | 997.29 | 50.03 | 0.9183 | 92.78 | 84.17 |  | 12306 | 12775 | 469 | 4.088 | 24 | 24 | 20.6667 | 7.3
| 2017-02-01 | 60.76 | 69.64% | 74 | 47 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3707 | 3587 | 3587 | 3531 | 3642 | 46 | 0 | 44 | 0 | 63 | 0 | 111 | -56 | 156 | 97.28% | 154.4583 | 95.25% | 100% | 99.35% | 11.475 | 175.2 | 2010.42 | 30.609 | 939 | 28741.851 | 8709.2243 | 149.4583 | 0 | 0 | 0 | 0 | 1 | 1440 | 0 | 1100 | 1062 | 1480 | -38 | 8709.2243 | 8709.2243 | 2.183 | 2.183 | 31.8 | 28.91 | 23.22 | 30.69 | 997.88 | 49.99 | 0.918 | 89.61 | 83.92 | -5.69 | 12365 | 12765 | 400 | 4.366 | 24 | 24 | 15.26 | 7.1
| 2017-02-02 | 61.88 | 67.54% | 69 | 55 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3716 | 3582 | 3582 | 3528 | 3639 | 46 | 0 | 44 | 0 | 64 | 0 | 111 | -54 | 154 | 98.46% | 154.8333 | 94.94% | 100% | 98.05% | 11.5 | 177.19 | 2037.685 | 30.506 | 940 | 28675.64 | 8705.591 | 149.25 | 0 | 0 | 0 | 0 | 3 | 1440 | 0 | 1115 | 1059 | 1465 | -56 | 8705.591 | 8705.591 | 2.116 | 2.116 | 31.98 | 29.19 | 23.14 | 30.69 | 1000 | 50.02 | 0.9169 | 91.52 | 84.06 | -7.46 | 12391 | 12656 | 265 | 4.232 | 24 | 24 | 18.77 | 6.83
| 2017-02-03 | 60.92 | 72.25% | 68 | 54 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 3578 | 3578 | 3517 | 3626 | 47 | 0 | 44 | 0 | 64 | 0 | 109 | -61 | 153 | 98.75% | 155 | 94.54% | 100% | 97.42% | 11.35 | 174.49 | 1980.4615 | 30.475 | 940 | 28646.5 | 8708.2632 | 149.0833 | 0 | 0 | 0 | 0 | 4 | 1440 | 0 | 1136 | 1054 | 1436 | -82 | 8708.2632 | 8708.2632 | 1.954 | 1.954 | 32.19 | 29.59 | 23.16 | 30.55 | 998.46 | 50.03 | 0.9178 | 93.58 | 83.98 | -9.6 | 12405 | 12576 | 171 | 3.908 | 24 | 24 | 22.45 | 7.65
| 2017-02-04 | 59.8 | 81.2% | 67 | 55 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 3571 | 3531 | 3476 | 3582 | 47 | 0 | 44 | 0 | 64 | 0 | 106 | -55 | 153 | 97.55% | 155 | 93.44% | 100% | 96.13% | 11.375 | 176.27 | 2005.0713 | 30.221 | 941 | 28437.961 | 8758.0645 | 148.7917 | 0 | 0 | 0 | 0 | 6 | 1440 | 0 | 1134 | 1046 | 1402 | -88 | 8758.0645 | 8758.0645 | 1.782 | 1.762 | 32 | 29.5 | 22.9 | 30.26 | 989.9 | 50 | 0.9168 | 94.98 | 84.09 | -10.89 | 12366 | 12545 | 179 | 3.544 | 24 | 24 | 24 | 7.12
Week 6 | 2017-02-05 | 57 | 62% | 66 | 49 | 24 | 0 | 12 | 31 | 0 | 0 | 0 | 0 | 6 | 31 | 3720 | 2835 | 2745 | 2663 | 2752 | 44 | 0 | 44 | 624 | 64 | 0 | 89 | -82 | 157 | 73.04% | 155 | 71.59% | 87.46% | 77.73% | 5.853 | 183.36 | 1073.2061 | 23.966 | 939 | 22504.074 | 8853.6538 | 118.125 | 0 | 0 | 21 | 65 | 19 | 1049 | 0 | 1063 | 614 | 1075 | -449 | 8853.6538 | 8853.6538 | 2.173 | 0.743 | 33.2 | 28.11 | 13.45 | 16.74 | 994.46 | 50 | 0.9143 | 84.9 | 86.17 | 1.27 | 12579 | 12033 | -546 | 2.916 | 24 | 9.43 | 4.03 | 6.28
| 2017-02-06 | 57 | 63% | 69 | 45 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 3585 | 3474 | 3445 | 3546 | 45 | 0 | 48 | 0 | 64 | 0 | 101 | -29 | 153 | 96.57% | 155 | 92.61% | 100% | 94.27% | 10.23 | 175.06 | 1790.8638 | 29.699 | 939 | 27887.361 | 8614.8693 | 149.375 | 0 | 0 | 0 | 0 | 9 | 1440 | 0 | 1080 | 1157 | 1309 | 77 | 8614.8693 | 8614.8693 | 1.326 | 1.282 | 31.9 | 28.49 | 24.56 | 30.69 | 999.08 | 50.02 | 0.9174 | 86.11 | 86.13 | 0.02 | 12550 | 12033 | -517 | 2.608 | 24 | 24 | 7.78 | 0
| 2017-02-07 | 59.3 | 62.6% | 70 | 47 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3717 | 3599 | 3599 | 3554 | 3665 | 46 | 0 | 48 | 0 | 64 | 0 | 111 | -45 | 155 | 98.52% | 154.875 | 95.61% | 100% | 96.84% | 10.8 | 170.09 | 1836.972 | 30.965 | 938 | 29045.17 | 8689.4041 | 149.9583 | 0 | 0 | 0 | 0 | 5 | 1440 | 0 | 1099 | 1143 | 1423 | 44 | 8689.4041 | 8689.4041 | 1.829 | 1.779 | 32 | 28.9 | 24.4 | 30.5 | 998.71 | 49.95 | 0.9193 | 88.7 | 86.1 | -2.6 | 12521 | 12124 | -397 | 3.608 | 24 | 24 | 13.88 | 6.16
| 2017-02-08 | 62.7 | 59.5% | 74 | 52 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3703 | 3588 | 3588 | 3537 | 3645 | 45 | 0 | 47 | 0 | 64 | 0 | 108 | -51 | 154 | 98.62% | 154.2917 | 95.52% | 100% | 97.44% | 11 | 172.3 | 1895.3 | 30.779 | 936 | 28809.144 | 8680.9285 | 149.5 | 0 | 0 | 0 | 0 | 4 | 1440 | 0 | 1088 | 1126 | 1431 | 38 | 8680.9285 | 8680.9285 | 1.878 | 1.878 | 31.7 | 28.7 | 24.1 | 30.5 | 996 | 50 | 0.9186 | 89 | 86.1 | -2.9 | 12547 | 12171 | -376 | 3.756 | 24 | 24 | 14.7 | 7.2
| 2017-02-09 | 62.2 | 59.9% | 74 | 55 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3707 | 3586 | 3586 | 3540 | 3649 | 46 | 0 | 47 | 0 | 64 | 0 | 109 | -46 | 154 | 98.73% | 154.4583 | 95.5% | 100% | 97.45% | 10.97 | 171.9 | 1885.743 | 30.755 | 938 | 28848.19 | 8681.902 | 149.4167 | 0 | 0 | 0 | 0 | 4 | 1440 | 0 | 1091 | 1121 | 1437 | 30 | 8681.902 | 8681.902 | 1.897 | 1.897 | 31.9 | 28.8 | 24.1 | 30.3 | 998.3 | 50.05 | 0.9194 | 89.3 | 85.9 | -3.4 | 12550 | 12222 | -328 | 3.794 | 24 | 24 | 15.4 | 6.9
| 2017-02-10 | 62.8 | 53.8% | 78 | 50 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3705 | 3603 | 3603 | 3544 | 3654 | 45 | 0 | 47 | 0 | 64 | 0 | 110 | -59 | 155 | 98.23% | 154.375 | 95.65% | 100% | 97.44% | 11.005 | 171.4 | 1886.257 | 30.748 | 938 | 28841.624 | 8670.3953 | 150.125 | 0 | 0 | 0 | 0 | 4 | 1440 | 0 | 1084 | 1126 | 1444 | 42 | 8670.3953 | 8670.3953 | 1.962 | 1.956 | 31.57 | 28.59 | 24.22 | 30.22 | 997.71 | 50.04 | 0.9201 | 88.15 | 85.75 | -2.4 | 12543 | 12206 | -337 | 3.918 | 24 | 24 | 12.83 | 5.92
| 2017-02-11 | 61.2 | 58% | 80 | 49 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3705 | 3607 | 3607 | 3551 | 3659 | 45 | 0 | 47 | 0 | 64 | 0 | 108 | -56 | 155 | 98.36% | 154.375 | 95.84% | 100% | 98.08% | 10.763 | 172.29 | 1854.3573 | 30.881 | 937 | 28935.497 | 8670.7559 | 150.2917 | 0 | 0 | 0 | 0 | 3 | 1440 | 0 | 1079 | 1124 | 1456 | 45 | 8670.7559 | 8670.7559 | 2.021 | 2.021 | 31.58 | 28.55 | 24.21 | 30.24 | 960.71 | 50 | 0.9207 | 87.47 | 85.74 | -1.73 | 12586 | 12236 | -350 | 4.042 | 24 | 24 | 11.73 | 0
Week 7 | 2017-02-12 | 62.4 | 60.3% | 79 | 50 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3705 | 3593 | 3482 | 3444 | 3550 | 45 | 0 | 46 | 0 | 64 | 0 | 106 | -38 | 153 | 96.68% | 154.375 | 92.96% | 100% | 94.84% | 10.79 | 172.21 | 1858.1459 | 29.902 | 936 | 27988.272 | 8666.2073 | 149.7083 | 0 | 0 | 0 | 0 | 8 | 1440 | 0 | 1088 | 1177 | 1345 | 89 | 8666.2073 | 8666.2073 | 1.366 | 1.356 | 31.69 | 28.79 | 24.09 | 30.11 | 1001.9 | 50.05 | 0.919 | 88.79 | 85.72 | -3.07 | 12588 | 12250 | -338 | 2.722 | 24 | 24 | 14.28 | 6.75
| 2017-02-13 | 65.79 | 56.36% | 79 | 55 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3692 | 3586 | 3535 | 3497 | 3599 | 45 | 0 | 46 | 0 | 64 | 0 | 102 | -38 | 154 | 97.38% | 153.8333 | 94.72% | 100% | 96.77% | 10.8 | 172.85 | 1866.78 | 30.464 | 939 | 28605.696 | 8713.8908 | 149.4167 | 0 | 0 | 0 | 0 | 5 | 1440 | 0 | 1075 | 1106 | 1418 | 31 | 8713.8908 | 8713.8908 | 1.91 | 1.91 | 31.41 | 28.46 | 23.8 | 29.89 | 1004.04 | 50.04 | 0.9188 | 89.09 | 85.62 | -3.47 | 12597 | 12252 | -345 | 3.82 | 24 | 24 | 15.266 | 7.166
| 2017-02-14 | 66.43 | 59.2% | 78 | 54 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3693 | 3583 | 3583 | 3519 | 3628 | 45 | 0 | 46 | 0 | 64 | 0 | 109 | -64 | 154 | 98.16% | 153.875 | 95.29% | 100% | 97.42% | 10.82 | 172.26 | 1863.8532 | 30.588 | 941 | 28783.308 | 8709.054 | 149.2917 | 0 | 0 | 0 | 0 | 4 | 1440 | 0 | 1081 | 1099 | 1448 | 18 | 8709.054 | 8709.054 | 2.07 | 2.07 | 31.34 | 28.54 | 23.53 | 30.01 | 1003.08 | 50.03 | 0.9195 | 90.08 | 85.67 | -4.41 | 12561 | 12236 | -325 | 4.14 | 24 | 24 | 15.5 | 6.08
| 2017-02-15 | 70.16 | 60.4% | 82 | 59 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3670 | 3580 | 3521 | 3475 | 3583 | 46 | 0 | 45 | 0 | 64 | 0 | 108 | -46 | 153 | 97.58% | 152.9167 | 94.69% | 100% | 96.77% | 10.786 | 168.81 | 1820.7847 | 30.301 | 940 | 28482.94 | 8720.4963 | 149.1667 | 0 | 0 | 0 | 0 | 5 | 1440 | 0 | 1103 | 1077 | 1403 | -26 | 8720.4963 | 8720.4963 | 1.773 | 1.76 | 31.45 | 29 | 23.15 | 29.8 | 1001.1 | 50.07 | 0.9206 | 93.32 | 85.69 | -7.63 | 12500 | 12309 | -191 | 3.533 | 24 | 24 | 24 | 6.55
| 2017-02-16 | 68 | 66% | 75 | 61 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3696 | 3573 | 3573 | 3505 | 3612 | 46 | 0 | 45 | 0 | 64 | 0 | 107 | -68 | 153 | 98.37% | 154 | 94.83% | 100% | 97.42% | 10.79 | 169.61 | 1830.0919 | 30.602 | 939 | 28735.278 | 8720.505 | 148.875 | 0 | 0 | 0 | 0 | 4 | 1440 | 0 | 1106 | 1074 | 1432 | -32 | 8720.505 | 8720.505 | 1.971 | 1.971 | 31.6 | 29.11 | 23.18 | 29.65 | 1000.33 | 50.02 | 0.9196 | 93.88 | 85.77 | -8.11 | 12523 | 12337 | -186 | 3.942 | 24 | 24 | 24 | 7.67
| 2017-02-17 | 70.1 | 59% | 81 | 62 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3677 | 3559 | 3559 | 3509 | 3617 | 46 | 0 | 45 | 0 | 63 | 0 | 108 | -50 | 154 | 97.86% | 153.2083 | 95.43% | 100% | 98.05% | 10.81 | 171.08 | 1849.3748 | 30.595 | 940 | 28759.3 | 8722.9053 | 148.2917 | 0 | 0 | 0 | 0 | 3 | 1440 | 0 | 1098 | 1075 | 1444 | -23 | 8722.9053 | 8722.9053 | 2.038 | 2.038 | 31.43 | 28.97 | 23.2 | 29.66 | 999.4 | 50.05 | 0.9195 | 93.14 | 85.76 | -7.38 | 12538 | 12338 | -200 | 4.076 | 24 | 24 | 24 | 7.4
| 2017-02-18 | 72.1 | 62.1% | 82 | 63 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3667 | 3551 | 3551 | 3492 | 3600 | 45 | 0 | 44 | 0 | 63 | 0 | 108 | -59 | 153 | 98.04% | 152.7917 | 95.23% | 100% | 98.03% | 10.76 | 169.28 | 1821.4528 | 30.579 | 939 | 28713.681 | 8744.3109 | 147.9583 | 0 | 0 | 0 | 0 | 3 | 1440 | 0 | 1088 | 1064 | 1448 | -24 | 8744.3109 | 8744.3109 | 2.124 | 2.124 | 31.2 | 28.85 | 23.14 | 29.47 | 998.4 | 50.04 | 0.9205 | 93.38 | 85.84 | -7.54 | 12615 | 12420 | -195 | 4.248 | 24 | 24 | 24 | 7.3
Week 8 | 2017-02-19 | 73 | 67.2% | 83 | 65 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3662 | 3522 | 3522 | 3463 | 3572 | 45 | 0 | 44 | 0 | 63 | 0 | 109 | -59 | 152 | 97.92% | 152.5833 | 94.57% | 100% | 98.03% | 10.7 | 166.25 | 1778.875 | 30.446 | 937 | 28527.902 | 8751.596 | 146.75 | 0 | 0 | 0 | 0 | 3 | 1440 | 0 | 1078 | 1051 | 1443 | -27 | 8751.596 | 8751.596 | 2.154 | 2.133 | 31.1 | 28.6 | 22.9 | 29.1 | 993.1 | 50.07 | 0.9213 | 93.8 | 85.8 | -8 | 12635 | 12462 | -173 | 4.287 | 24 | 24 | 24 | 8.05
| 2017-02-20 | 69 | 45.7% | 77 | 61 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3692 | 3556 | 3556 | 3512 | 3619 | 45 | 0 | 45 | 0 | 63 | 0 | 107 | -44 | 154 | 97.92% | 153.8333 | 95.12% | 100% | 98.04% | 10.66 | 167.62 | 1786.8292 | 30.813 | 938 | 28902.594 | 8738.4462 | 148.1667 | 0 | 0 | 0 | 0 | 3 | 1440 | 0 | 1082 | 1085 | 1452 | 3 | 8738.4462 | 8738.4462 | 2.053 | 2.053 | 31.3 | 28.7 | 23.5 | 28.9 | 988.5 | 50.04 | 0.9211 | 90.8 | 85.5 | -5.3 | 12610 | 12231 | -379 | 4.106 | 24 | 24 | 20.77 | 6.95
| 2017-02-21 | 65.1 | 52.5% | 80 | 53 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3689 | 3567 | 3567 | 3507 | 3614 | 45 | 0 | 46 | 0 | 63 | 0 | 107 | -60 | 153 | 98.42% | 153.7083 | 95.07% | 100% | 98.05% | 10.56 | 164.02 | 1732.0512 | 30.904 | 936 | 28926.144 | 8742.0003 | 148.625 | 0 | 0 | 0 | 0 | 3 | 1440 | 0 | 1070 | 1100 | 1444 | 30 | 8742.0003 | 8742.0003 | 1.994 | 1.973 | 31.3 | 28.5 | 23.9 | 28.8 | 989.5 | 50.03 | 0.922 | 88 | 85.5 | -2.5 | 12644 | 12313 | -331 | 3.967 | 24 | 24 | 14.68 | 7.03
| 2017-02-22 | 65.5 | 48.2% | 81 | 52 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3690 | 3559 | 3559 | 3500 | 3607 | 44 | 0 | 46 | 0 | 63 | 0 | 107 | -59 | 152 | 98.88% | 153.75 | 94.85% | 100% | 98.04% | 10.54 | 162.91 | 1717.0714 | 31.001 | 935 | 28985.935 | 8772.2875 | 148.2917 | 0 | 0 | 0 | 0 | 3 | 1440 | 0 | 1064 | 1104 | 1439 | 40 | 8772.2875 | 8772.2875 | 1.956 | 1.956 | 31.14 | 28.52 | 24.23 | 28.92 | 994.79 | 49.99 | 0.9224 | 87.21 | 85.49 | -1.72 | 12750 | 12401 | -349 | 3.912 | 24 | 24 | 13.73 | 6.8
| 2017-02-23 | 66.7 | 49.3% | 82 | 54 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3689 | 3575 | 3575 | 3526 | 3635 | 44 | 0 | 46 | 0 | 63 | 0 | 109 | -49 | 154 | 98.35% | 153.7083 | 95.58% | 100% | 98.69% | 10.56 | 163.96 | 1731.4176 | 31.135 | 936 | 29142.36 | 8756.0345 | 148.9583 | 0 | 0 | 0 | 0 | 2 | 1440 | 0 | 1072 | 1102 | 1461 | 30 | 8756.0345 | 8756.0345 | 2.088 | 2.078 | 31.27 | 28.43 | 24.14 | 28.8 | 997.58 | 50.02 | 0.9227 | 88.36 | 85.53 | -2.83 | 12623 | 12371 | -252 | 4.166 | 24 | 24 | 14.8 | 2.67
| 2017-02-24 | 67 | 54.3% | 82 | 55 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3687 | 3562 | 3562 | 3509 | 3616 | 44 | 0 | 45 | 0 | 63 | 0 | 107 | -53 | 155 | 97.2% | 153.625 | 95.17% | 100% | 98.68% | 10.58 | 161.41 | 1707.7178 | 30.925 | 936 | 28945.8 | 8735.6848 | 148.4167 | 0 | 0 | 0 | 0 | 2 | 1440 | 0 | 1072 | 1093 | 1451 | 21 | 8735.6848 | 8735.6848 | 2.046 | 2.048 | 31.24 | 28.49 | 23.59 | 28.78 | 999.13 | 50 | 0.9232 | 88.92 | 85.59 | -3.33 | 12641 | 12401 | -240 | 4.094 | 24 | 24 | 15.75 | 5.5
| 2017-02-25 | 68.2 | 54.2% | 81 | 56 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3683 | 3584 | 3584 | 3526 | 3635 | 45 | 0 | 45 | 0 | 63 | 0 | 109 | -58 | 155 | 97.72% | 153.4583 | 95.74% | 100% | 98.8% | 10.55 | 160.98 | 1698.339 | 31.188 | 936 | 29191.968 | 8760.7223 | 149.3333 | 0 | 0 | 0 | 0 | 2 | 1320 | 0 | 1075 | 1086 | 1474 | 11 | 8760.7223 | 8760.7223 | 2.187 | 2.192 | 31.7 | 28.57 | 23.08 | 28.55 | 996.9 | 50.01 | 0.9237 | 89.87 | 85.59 | -4.28 | 12635 | 12451 | -184 | 4.379 | 24 | 24 | 18.4 | 5.18
Week 9 | 2017-02-26 | 68.9 | 57.3% | 83 | 56 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3676 | 3577 | 3577 | 3513 | 3621 | 45 | 0 | 45 | 0 | 63 | 0 | 108 | -64 | 154 | 97.97% | 153.1667 | 95.57% | 100% | 99.37% | 10.515 | 159.82 | 1680.5073 | 31.079 | 936 | 29089.944 | 8759.024 | 149.0417 | 0 | 0 | 0 | 0 | 1 | 1380 | 0 | 1074 | 1080 | 1467 | 6 | 8759.024 | 8759.024 | 2.187 | 2.187 | 31.7 | 28.55 | 23 | 28.5 | 994.2 | 50.04 | 0.9264 | 90.51 | 85.63 | -4.88 | 12636 | 12489 | -147 | 4.374 | 24 | 24 | 19.48 | 6.65
| 2017-02-27 | 69.98 | 53.76% | 81 | 55 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3665 | 3552 | 3552 | 3497 | 3606 | 45 | 0 | 45 | 0 | 63 | 0 | 109 | -55 | 153 | 98.2% | 152.7083 | 95.42% | 100% | 98.04% | 10.53 | 159.11 | 1675.4283 | 30.912 | 937 | 28964.544 | 8761.7879 | 148 | 0 | 0 | 0 | 0 | 3 | 1440 | 0 | 1083 | 1077 | 1446 | -6 | 8761.7879 | 8761.7879 | 2.074 | 2.057 | 31.65 | 28.69 | 23.02 | 28.26 | 994.92 | 50.02 | 0.9242 | 91.14 | 85.59 | -5.55 | 12599 | 12520 | -79 | 4.131 | 24 | 24 | 21.38 | 10.13
| 2017-02-28 | 71.7 | 56% | 82 | 64 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 3677 | 3549 | 3549 | 3496 | 3606 | 45 | 0 | 44 | 0 | 63 | 0 | 110 | -53 | 152 | 98.85% | 153.2083 | 95.08% | 100% | 98.11% | 10.49 | 157.18 | 1648.8182 | 30.905 | 937.7564 | 28981.3615 | 8761.4931 | 147.875 | 0 | 0 | 0 | 0 | 3 | 1380 | 0 | 1091 | 1067 | 1448 | -24 | 8761.4931 | 8761.4931 | 2.088 | 2.093 | 31.2 | 28.8 | 22.9 | 28.1 | 995.4 | 50.06 | 0.9249 | 92.61 | 85.68 | -6.93 | 12562 | 12552 | -10 | 4.181 | 24 | 24 | 24 | 6.92
| 2017-03-01 | [25 empty] | 0 | 0 |  | no data | no data | no data | #DIV/0! | no data |  |  | 0 |  |  | 0 | no data | 0 | [10 empty] | 0 | no data | [12 empty] | 0 |  |  | 0 | 0
| 2017-03-02 | [25 empty] | 0 | 0 |  | no data | no data | no data | #DIV/0! | no data |  |  | 0 |  |  | 0 | no data | 0 | [10 empty] | 0 | no data | [12 empty] | 0 |  |  | 0 | 0
| 2017-03-03 | [25 empty] | 0 | 0 |  | no data | no data | no data | #DIV/0! | no data |  |  | 0 |  |  | 0 | no data | 0 | [10 empty] | 0 | no data | [12 empty] | 0 |  |  | 0 | 0
| 2017-03-04 | [25 empty] | 0 | 0 |  | no data | no data | no data | #DIV/0! | no data |  |  | 0 |  |  | 0 | no data | 0 | [10 empty] | 0 | no data | [12 empty] | 0 |  |  | 0 | 0
| Monthly | 65.2007 | 59.69% | 77.0357 | 54.75 | 672 | 11 | 660 | 31 | 0 | 0 | 0 | 0 | 7 | 1755 | 103450 | 99349 | 98887 | 97577.24 | 100379 | 45.25 | 0 | 45.4286 | 624 | 63.5357 | 0 | 2801.76 | -1511 | 153.8214 | 97.13% | 153.9435 | 94.32% | #DIV/0! | 96.9% | 297.562 | 169.2468 | 50323.8752 | 851.943 | 937.9913 | 799100.0395 | 8705.6832 |  | 0 | 0 | 21 | 65 | 119 | 39689 | 0 |  |  |  | 0 | 8705.6832 |  | 55.2 | 53.57 | 885.54 | 804.9 | 649.81 | 816.68 | 995.8386 | 50.0243 | 0.92031 | 90.2221 | 85.4968 |  | 12559.2857 | 12353.5714 |  | 108.77 | 672 | 657.43 | 488.866 | 175.956
| Totals | Avg.F | % Avg. | M Avg | m Avg | hrs | min | hrs | min | hrs | min | hrs | min | Avg Int Avi | Avg Ext Avi | MWhr Total | MWhr Total | MWhr Total | MWhr Total | MWhr Total | MW Avg | Total min | Avg MW | Total min | Avg MW | Total min | MWhr | Total MW | Av Max D/Gen | Av. DailyLF | Avg. | Avg. |  | Avg. | Total | Avg. |  | Total | Avg. |  | Avg. | [7 empty] | Total | 30469 | 30149 | 39821 | -320 | Avg. | [18 empty] | 664.715
24.8
| Weeks data | Site Avg. Amb. Temp F | Site Avg. Relative humidity % | Max: Site Maximum/Minumum Temperature; CT1 hrs: CT-1 Base Load Hours; CT2 hrs: CT-2 Base Load Hours; CT1 hrs: CT-1 stand by hours / min; CT2 hrs: CT-2 standby hours / min; CT2 hrs: Plant ambient Corrected maximum Load hours/min | Average Corrected Plant Capacity | Ambient Corrected Declared Avail'y (MWH) | Av Plant WAPDA Dispatch | Net Plant Export (MWH) | Gross Generation | CT1 Av Cap (MW) | CT1 Unavail minutes | CT2 Av Cap (MW) | CT2 Unavail minutes | ST Unavail minutes | ST Average Cap (MW) | Plant Aux Load including Colony Load MWH | Differenece (+/-) MW | Maximum Daily Generation | Daily Load Factor | Avg. Corrected Plant |  |  | Equivalent Plant Availability | LBtu gas flow mmscf | 1 LBtu gas (Average Btu/scf) |  | PL gas flow (mscf/week) | 1 PL gas (Average Btu/scf) |  | Plant Net Heat Rate (Btu/Kwh) | [11 empty] | 25.75
| Week 5 | 61.4371 | 73.26% | 70.4286 | 53.1429 | 168 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3714.5714 | 3477.9286 | 3472.2143 | 3416.2857 | 3521.8571 | 45.2857 | #REF! | 44 | #REF! | 444 | no data | no data | -391.5 | 150.4286 | 97.56% | 154.7738 | 91.97% | 100% | 95.84% | 79.74 | 174.56 |  | 206.415 | 938.7143 |  | 8682.9894
| Week 6 | 60.3143 | 59.83% | 73 | 49.5714 | 168 | -2 | 156 | 31 | 0 | 0 | 0 | 0 | 6 | 31 | 3711 | 3486.1429 | 3457.4286 | 23834 | 24570 | 45.1429 | No outage | 328 | 89.1429 | 448 | no data | 736 | -368 | 154.7143 | 94.58% | 154.625 | 91.76% | 98.21% | 94.18% | 70.621 | 173.7714 |  | 207.793 | 937.8571 |  | 8694.5584
| Week 7 | 67.8543 | 60.48% | 79.4286 | 57.7143 | 168 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3685.7143 | 3575 | 3543.4286 | 24441 | 25189 | 45.4286 | No outage | 317 | no data | 446 | no data | 748 | -363 | 153.4286 | 97.72% | 153.5714 | 94.73% | 100% | 97.04% | 75.556 | 170.8714 |  | 213.031 | 939.1429 |  | 8713.9099
| Week 8 | 67.7857 | 53.06% | 80.8571 | 56.5714 | 168 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3684.5714 | 3560.7143 | 3560.7143 | 24543 | 25298 | 44.5714 | No outage | 317 | no data | 441 | no data | 755 | -382 | 153.5714 | 98.06% | 153.5238 | 95.16% | 100% | 98.33% | 74.15 | 163.8786 |  | 216.412 | 936.2857 |  | 8750.9674
| Week 9 | 70.1933 | 0.55687 | 82 | 58.3333 | 72 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 3686.5714 | 3559.3333 | 3559.3333 | 10506 | 10833 | 45 | No outage | 179 | no data | 189 | no data | 327 | -172 | 153 | 98.34% | 153.0278 | 95.35% | #DIV/0! | 98.51% | 31.535 | 158.7033 |  | 92.896 | 936.9188 |  | 8760.7683
| Date | Plant Status Whether Normal Operation or Tripping (State full detail for trippings/return to normal).
| 2016-02-01 | Plant load remained 144~152 MW to remain within HBTU gas quota by M/S SNGPL.
| 2016-02-02 | Plant load remained 145~149 MW to remain within allocated HBTU gas quota by M/S SNGPL.
| 2016-02-03 | Plant load remained 145~149 MW to remain within allocated HBTU gas quota by M/S SNGPL.
| 2016-02-04 | Plant load remained 144~148 MW to remain within allocated HBTU gas quota by M/S SNGPL. WAPDA Load despatch of 135MW received from 0152~0415hrs
| 2016-02-05 | CT-2 desynch @0418 hrs & synch @1442 hrs after compressor offline washing. WAPDA Load despatch of 135MW received from 0020~1638hrs & 2308~0000hrs.
| 2016-02-06 | Plant load remained 146~149 MW to remain within allocated HBTU gas quota by M/S SNGPL. WAPDA Load despatch of 150 MW received at 0830 hrs.
| 2016-02-07 | Plant load remained 145~150 MW to remain within HBTU gas quota by M/S SNGPL.
| 2016-02-08 | Plant load remained 145~149 MW to remain within HBTU gas quota by M/S SNGPL.
| 2016-02-09 | Plant load remained 145~149 MW to remain within HBTU gas quota by M/S SNGPL.
| 2016-02-10 | Plant load remained 145~150 MW to remain within HBTU gas quota by M/S SNGPL.
| 2016-02-11 | Plant load remained 146~151 MW to remain within HBTU gas quota by M/S SNGPL.
| 2016-02-12 | Plant load remained 145~149 MW to remain within HBTU gas quota by M/S SNGPL. Wapda Load Despatch of 135 MW received from 0221~0908 hrs & from 2322~2400 hrs.
| 2016-02-13 | Plant load remained 145~149 MW to remain within HBTU gas quota by M/S SNGPL. Wapda Load Despatch of 135 MW received from 0000~0323 hrs.
| 2016-02-14 | Plant load remained 144~149 MW to remain within HBTU gas quota by M/S SNGPL.
| 2016-02-15 | Plant load remained 144~149 MW to remain within HBTU gas quota by M/S SNGPL. Wapda Load Despatch of 135 MW received from 0055~0426 hrs.
| 2016-02-16 | Plant load remained 144~148 MW to remain within HBTU gas quota by M/S SNGPL.
| 2016-02-17 | Plant load remained 143~149 MW to remain within allocated HBTU gas quota by M/S SNGPL.
| 2016-02-18 | Plant load remained 142~148 MW to remain within allocated HBTU gas quota by M/S SNGPL.
| 2016-02-19 | Plant load remained 141~147 MW to remain within allocated HBTU gas quota by M/S SNGPL.
| 2016-02-20 | Plant load remained 143~150 MW to remain within allocated HBTU gas quota by M/S SNGPL.
| 2016-02-21 | Plant load remained 144~148 MW to remain within HBTU gas quota by M/S SNGPL.
| 2016-02-22 | Plant load remained 144~147 MW to remain within HBTU gas quota by M/S SNGPL.
| 2016-02-23 | Plant load remained 144~149 MW to remain within HBTU gas quota by M/S SNGPL.
| 2016-02-24 | Plant load remained 144~150 MW to remain within HBTU gas quota by M/S SNGPL.
| 2016-02-25 | Plant load remained 144~151 MW to remain within HBTU gas quota by M/S SNGPL.
| 2016-02-26 | Plant load remained 143~150 MW to remain within HBTU gas quota by M/S SNGPL.
| 2016-02-27 | Plant load remained 143~148 MW to remain within HBTU gas quota by M/S SNGPL.
| 2016-02-28 | Plant load remained 144~148 MW to remain within HBTU gas quota by M/S SNGPL.

## Mar
Monthly Operational Returns Kabirwala
2017-03-01
| Date | Site Avg. Ambient Temp.F | Site Avg. Relative Humidty % | Site Ambient Temp |  | Base load hours |  |  |  | Standby hours |  |  |  | Plant ambient corrected Max Load |  | Corrected Plant Capacity | Ambient Corrected Daclared Avail'y (MWH) | Plant WAPDA Dispatch (MWH) | Net Plant Export (MWH) | Gross Generation | CT1 Average Cap (MW) | CT1 Unavail minutes | CT2 Average Cap (MW) | CT2 Unavail minutes | ST Average Cap (MW) | ST Unavail minutes | Plant Aux Load including Colony Load MWH | Differenece (+/-) MW | Maximum Daily Generation | Daily Load Factor | Avg. Corrected Plant Capacity | Plant Capacity Factor | Plant Availability Factor | Equivalent Plant Availability | LBtu gas flow (mmscf/day) | 1 LBtu gas (Average Btu/scf) | LBTU MMBTU | 1 HBtu gas flow (mmscf/day) | 1 HBtu gas (Average Btu/scf) | HBTU MMBTU | HHV Net Heat Rate (Btu/Kwh) | Avg. declared availability | CT1 Derated MW | CT1 derated mintutes | CT-2 derated MW | CT-2 derated mintutes | ST derated MW | ST derated mintutes | WAPDA Backfeed (MWH) | CT-1 Gross Generation (MWH) | CT-2 Gross Generation (MWH) | STG Gross Generation (MWH) | CT-1 & CT-2 MWH difference | Base load Heat Rate | Part load Heat Rate | DB1 | DB2 | CT1 | CT1 Gas flow | CT2 Gas flow |  | Pamb | Freq. Hz | LBTU Gas Specific gravity | CT-1 compressor efficiency(%) | CT-2 compressor efficiency(%) |  | CT-1 Heat Rate (Btu/Kwh) | CT-2 Heat Rate (Btu/Kwh) |  | DB(1+2) | DB-1 Ops Hours | DB-2 Ops Hours | CT-1 Wetcomprssion Ops Hours | RO Operation Hours
[6 empty] | CT1 |  | CT2 |  | CT1 |  | CT2 | [43 empty] | mmscf/d | mmscf/d | WetC flow | HBTU KPPH | HBTU KPPH | LBTU KPPH | mbar | Hz | [7 empty] | mmscf/d
|  |  |  | Max | Min | hrs | min | hrs | min | hrs | min | hrs | min | hrs | min | [42 empty] | gpm
Week 9 | 2017-02-26 | 68.9 | 57.3% | 83 | 56 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3676 | 3577 | 3577 | 3513 | 3621 | 45 | 0 | 45 | 0 | 63 | 0 | 108 | -64 | 154 | 97.97% | 153.1667 | 95.57% | 100% | 99.37% | 10.515 | 159.82 | 1680.5073 | 31.089 | 936 | 29099.304 | 8761.6884 | 149.0417 | 0 | 0 | 0 | 0 | 1 | 1380 | 0 | 1074 | 1080 | 1467 | 6 | 8761.6884 | 8761.6884 | 2.187 | 2.187 | 31.7 | 28.55 | 23 | 28.5 | 994.2 | 50.04 | 0.9264 | 90.51 | 85.63 | -4.88 | 12636 | 12489 | -147 | 4.374 | 24 | 24 | 19.48 | 6.65
| 2017-02-27 | 69.98 | 53.76% | 81 | 55 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3665 | 3552 | 3552 | 3497 | 3606 | 45 | 0 | 45 | 0 | 63 | 0 | 109 | -55 | 153 | 98.2% | 152.7083 | 95.42% | 100% | 98.04% | 10.53 | 159.11 | 1675.4283 | 30.931 | 937 | 28982.347 | 8766.8788 | 148 | 0 | 0 | 0 | 0 | 3 | 1440 | 0 | 1083 | 1077 | 1446 | -6 | 8766.8788 | 8766.8788 | 2.074 | 2.057 | 31.65 | 28.69 | 23.02 | 28.26 | 994.92 | 50.02 | 0.9242 | 91.14 | 85.59 | -5.55 | 12599 | 12520 | -79 | 4.131 | 24 | 24 | 21.38 | 10.13
| 2017-02-28 | 71.7 | 56% | 82 | 64 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 3677 | 3549 | 3549 | 3496 | 3606 | 45 | 0 | 44 | 0 | 63 | 0 | 110 | -53 | 152 | 98.85% | 153.2083 | 95.08% | 100% | 98.11% | 10.49 | 157.18 | 1648.8182 | 30.915 | 937 | 28967.355 | 8757.4866 | 147.875 | 0 | 0 | 0 | 0 | 3 | 1380 | 0 | 1091 | 1067 | 1448 | -24 | 8757.4866 | 8757.4866 | 2.088 | 2.093 | 31.2 | 28.8 | 22.9 | 28.1 | 995.4 | 50.06 | 0.9249 | 92.61 | 85.68 | -6.93 | 12562 | 12552 | -10 | 4.181 | 24 | 24 | 24 | 6.92
| 2017-03-01 | 68.5 | 61.9% | 81 | 60 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3687 | 3534 | 3534 | 3475 | 3582 | 46 | 0 | 45 | 0 | 63 | 0 | 107 | -59 | 153 | 97.55% | 153.625 | 94.25% | 100% | 97.4% | 10.47 | 158.12 | 1655.5164 | 30.466 | 938 | 28577.108 | 8700.0358 | 147.25 | 0 | 0 | 0 | 0 | 4 | 1440 | 0 | 1100 | 1073 | 1409 | -27 | 8700.0358 | 8700.0358 | 1.834 | 1.829 | 31.6 | 29 | 23.1 | 28.17 | 995.4 | 50 | 0.9249 | 93.08 | 85.68 | -7.4 | 12532 | 12563 | 31 | 3.663 | 24 | 24 | 24 | 7.1
| 2017-03-02 | 69.3 | 55.4% | 83 | 58 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3678 | 3564 | 3564 | 3510 | 3621 | 46 | 0 | 45 | 0 | 63 | 0 | 111 | -54 | 154 | 97.97% | 153.25 | 95.43% | 100% | 98.05% | 10.41 | 155.94 | 1623.3354 | 30.868 | 938 | 28954.184 | 8711.544 | 148.5 | 0 | 0 | 0 | 0 | 3 | 1440 | 0 | 1102 | 1079 | 1440 | -23 | 8711.544 | 8711.544 | 1.989 | 1.989 | 31.6 | 29 | 23.1 | 28.3 | 995.04 | 50 | 0.9262 | 92.5 | 85.6 | -6.9 | 12522 | 12540 | 18 | 3.978 | 24 | 24 | 24 | 7.6
| 2017-03-03 | 68.5 | 58.9% | 81 | 58 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3680 | 3558 | 3558 | 3499 | 3606 | 46 | 0 | 45 | 0 | 63 | 0 | 107 | -59 | 153 | 98.2% | 153.3333 | 95.08% | 100% | 97.4% | 10.45 | 155.3 | 1622.885 | 30.772 | 938 | 28864.136 | 8713.0669 | 148.25 | 0 | 0 | 0 | 0 | 4 | 1440 | 0 | 1104 | 1079 | 1423 | -25 | 8713.0669 | 8713.0669 | 1.907 | 1.907 | 31.6 | 29 | 23.2 | 28 | 992.79 | 50.02 | 0.9262 | 92.9 | 85.6 | -7.3 | 12514 | 12554 | 40 | 3.814 | 24 | 24 | 24 | 7.48
| 2017-03-04 | 67.74 | 60.88% | 80 | 56 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3683 | 3547 | 3547 | 3493 | 3602 | 46 | 0 | 45 | 0 | 63 | 0 | 109 | -54 | 152 | 98.74% | 153.4583 | 94.84% | 100% | 97.4% | 10.455 | 155.55 | 1626.2753 | 30.768 | 938 | 28860.384 | 8727.9299 | 147.7917 | 0 | 0 | 0 | 0 | 4 | 1440 | 0 | 1104 | 1075 | 1423 | -29 | 8727.9299 | 8727.9299 | 1.902 | 1.92 | 31.74 | 29.05 | 23.15 | 28.17 | 992 | 50.03 | 0.926 | 92.89 | 85.53 | -7.36 | 12519 | 12582 | 63 | 3.822 | 24 | 24 | 24 | 7.16
Week 10 | 2017-03-05 | 69.58 | 56.7% | 81 | 59 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3675 | 3253 | 3253 | 3206 | 3302 | 46 | 0 | 45 | 0 | 63 | 0 | 96 | -47 | 141 | 97.58% | 153.125 | 87.24% | 100% | 89.61% | 10.425 | 152.87 | 1593.6698 | 27.393 | 939 | 25722.027 | 8520.1799 | 135.5417 | 0 | 0 | 0 | 0 | 16 | 1440 | 0 | 1097 | 1075 | 1130 | -22 | 8520.1799 | 8520.1799 | 0.345 | 0.236 | 31.51 | 28.96 | 23.08 | 28.15 | 992.83 | 50.08 | 0.9271 | 92.44 | 85.53 | -6.91 | 12550 | 12545 | -5 | 0.581 | 24 | 24 | 24 | 7.3
| 2017-03-06 | 69 | 58.6% | 79 | 60 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3686 | 3430 | 3430 | 3372 | 3475 | 46 | 0 | 45 | 0 | 63 | 0 | 103 | -58 | 151 | 95.89% | 153.5833 | 91.48% | 100% | 94.81% | 10.44 | 153.91 | 1606.8204 | 29.466 | 939 | 27668.574 | 8681.9082 | 142.9167 | 0 | 0 | 0 | 0 | 8 | 1440 | 0 | 1095 | 1072 | 1308 | -23 | 8681.9082 | 8681.9082 | 1.402 | 1.36 | 31.58 | 28.89 | 22.91 | 28.16 | 991.4 | 50.04 | 0.9267 | 92.67 | 85.59 | -7.08 | 12545 | 12529 | -16 | 2.762 | 24 | 24 | 24 | 7.42
| 2017-03-07 | 67.5 | 67.9% | 79 | 62 | 24 | 0 | 7 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 3701 | 2348.5 | 2348.5 | 2328 | 2412 | 46 | 0 | 45 | 943 | 63 | 0 | 84 | -20.5 | 152 | 66.12% | 154.2083 | 62.9% | 80.86% | 65.97% | 3.25 | 167.44 | 544.18 | 20.922 | 939 | 19645.758 | 8672.6538 | 97.8542 | 0 | 0 | 20 | 68 | 22 | 1440 | 0 | 1095 | 352 | 965 | -743 | 8672.6538 | 8672.6538 | 2.564 | 0.678 | 31.75 | 28.92 | 22.97 | 29.53 | 990.83 | 50.01 | 0.9213 | 93.51 | 86.81 | -6.7 | 12555 | 12376 | -179 | 3.242 | 24 | 7.4 | 24 | 5.42
| 2017-03-08 | 67.6 | 66.9% | 83 | 59 | 6 | 9 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3688 | 2286.5 | 2286.5 | 2273 | 2357 | 47 | 1006 | 46 | 0 | 63 | 0 | 84 | -13.5 | 154 | 63.77% | 153.6667 | 61.63% | 78.95% | 63.57% | 10.3 | 152.45 | 1570.235 | 19.31 | 939 | 18132.09 | 8667.9828 | 95.2708 | 22 | 65 | 0 | 0 | 23 | 1440 | 0 | 310 | 1101 | 946 | 791 | 8667.9828 | 8667.9828 | 0.586 | 2.581 | 31.86 | 28.97 | 22.99 | 28.19 | 990.29 | 50 | 0.9269 | 94.76 | 86.42 | -8.34 | 12346 | 12256 | -90 | 3.167 | 6.47 | 24 | 5.25 | 1.6
| 2017-03-09 | 62.39 | 70.78% | 70 | 56 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3718 | 3580 | 3580 | 3531 | 3640 | 48 | 0 | 46 | 0 | 63 | 0 | 109 | -49 | 154 | 98.48% | 154.9167 | 94.97% | 100% | 96.18% | 10.215 | 152.38 | 1556.5617 | 31.018 | 939 | 29125.902 | 8689.4545 | 149.1667 | 0 | 0 | 0 | 0 | 6 | 1440 | 0 | 1156 | 1112 | 1372 | -44 | 8689.4545 | 8689.4545 | 1.655 | 1.655 | 32.39 | 29.73 | 23.55 | 27.86 | 988.9 | 50.02 | 0.9268 | 96.61 | 86.35 | -10.26 | 12230 | 12308 | 78 | 3.31 | 24 | 24 | 24 | 5.45
| 2017-03-10 | 62.61 | 67.18% | 76 | 54 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3706 | 3595 | 3595 | 3532 | 3641 | 48 | 0 | 47 | 0 | 63 | 0 | 109 | -63 | 154 | 98.51% | 154.4167 | 95.3% | 100% | 96.84% | 10.2 | 152.16 | 1552.032 | 31.022 | 939 | 29129.658 | 8686.7752 | 149.7917 | 0 | 0 | 0 | 0 | 5 | 1440 | 0 | 1144 | 1115 | 1382 | -29 | 8686.7752 | 8686.7752 | 1.665 | 1.64 | 32.58 | 29.56 | 23.68 | 27.89 | 988.6 | 50.02 | 0.9269 | 95.18 | 86.13 | -9.05 | 12286 | 12339 | 53 | 3.305 | 24 | 24 | 21.7 | 8.6
| 2017-03-11 | 62.05 | 61.07% | 72 | 51 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3708 | 3604 | 3518 | 3477 | 3582 | 46 | 0 | 47 | 0 | 63 | 0 | 105 | -41 | 154 | 96.92% | 154.5 | 93.77% | 100% | 97.49% | 10.22 | 152.3 | 1556.506 | 30.367 | 939 | 28514.613 | 8648.5818 | 150.1667 | 0 | 0 | 0 | 0 | 5 | 1126 | 0 | 1115 | 1123 | 1344 | 8 | 8648.5818 | 8648.5818 | 1.404 | 1.385 | 31.78 | 28.97 | 23.86 | 27.79 | 991.67 | 50.05 | 0.9269 | 91.39 | 85.97 | -5.42 | 12351 | 12314 | -37 | 2.789 | 24 | 24 | 14.3 | 3.81
Week 11 | 2017-03-12 | 63.3 | 58.4% | 76 | 53 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 3702 | 3584 | 3584 | 3535 | 3644 | 46 | 0 | 46 | 0 | 63 | 0 | 109 | -49 | 153 | 99.24% | 154.25 | 95.49% | 100% | 97.53% | 10.25 | 152.74 | 1565.585 | 31.039 | 939 | 29145.621 | 8687.7528 | 149.3333 | 0 | 0 | 0 | 0 | 4 | 1380 | 0 | 1112 | 1117 | 1415 | 5 | 8687.7528 | 8687.7528 | 1.808 | 1.808 | 19.3 | 28.9 | 23.8 | 27.6 | 996.1 | 50 | 0.9271 | 91.4 | 85.8 | -5.6 | 12359 | 12363 | 4 | 3.616 | 24 | 24 | 14.6 | 5.1
| 2017-03-13 | 64.8 | 55.2% | 76 | 54 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3697 | 3582 | 3582 | 3530 | 3637 | 46 | 0 | 46 | 0 | 63 | 0 | 107 | -52 | 154 | 98.4% | 154.0417 | 95.48% | 100% | 97.42% | 10.012 | 153.24 | 1534.2389 | 31.001 | 939 | 29109.939 | 8681.0702 | 149.25 | 0 | 0 | 0 | 0 | 4 | 1440 | 0 | 1111 | 1106 | 1420 | -5 | 8681.0702 | 8681.0702 | 1.846 | 1.844 | 31.4 | 28.9 | 23.7 | 27.7 | 996.4 | 50.05 | 0.9271 | 91.7 | 85.6 | -6.1 | 12385 | 12427 | 42 | 3.69 | 24 | 24 | 15.4 | 5.6
| 2017-03-14 | 65.6 | 53.5% | 76 | 54 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3697 | 3580 | 3580 | 3528 | 3640 | 46 | 0 | 46 | 0 | 63 | 0 | 112 | -52 | 154 | 98.48% | 154.0417 | 95.43% | 100% | 97.42% | 10.002 | 151.91 | 1519.4038 | 30.98 | 939 | 29090.22 | 8676.1972 | 149.1667 | 0 | 0 | 0 | 0 | 4 | 1440 | 0 | 1115 | 1103 | 1422 | -12 | 8676.1972 | 8676.1972 | 1.893 | 1.931 | 31.4 | 29.1 | 23.6 | 27.7 | 998.1 | 50.06 | 0.9274 | 92.3 | 85.6 | -6.7 | 12393 | 12464 | 71 | 3.824 | 24 | 24 | 17.3 | 2.3
| 2017-03-15 | 66.3 | 59.2% | 73 | 60 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3690 | 3584 | 3584 | 3526 | 3631 | 47 | 0 | 45 | 0 | 63 | 0 | 105 | -58 | 154 | 98.24% | 153.75 | 95.56% | 100% | 96.77% | 10 | 152.33 | 1523.3 | 31.173 | 939 | 29271.447 | 8733.6208 | 149.3333 | 0 | 0 | 0 | 0 | 5 | 1440 | 0 | 1139 | 1091 | 1401 | -48 | 8733.6208 | 8733.6208 | 1.752 | 1.752 | 31.9 | 29.5 | 23.4 | 27.6 | 997.08 | 50.01 | 0.9281 | 95.6 | 85.7 | -9.9 | 12336 | 12484 | 148 | 3.504 | 24 | 24 | 24 | 7.12
| 2017-03-16 | 70.4 | 57.2% | 81 | 61 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 15 | 47 | 3675 | 3606 | 3606 | 3545 | 3654 | 47 | 0 | 45 | 0 | 63 | 0 | 109 | -61 | 155 | 98.23% | 153.125 | 96.46% | 100% | 98.9% | 10.178 | 151.97 | 1546.7507 | 31.18 | 939 | 29278.02 | 8695.2809 | 150.25 | 0 | 0 | 0 | 0 | 5 | 493 | 0 | 1120 | 1082 | 1452 | -38 | 8695.2809 | 8695.2809 | 2.078 | 2.078 | 31.4 | 29.2 | 23.3 | 27.5 | 994.58 | 50.03 | 0.9276 | 95.3 | 85.7 | -9.6 | 12388 | 12526 | 138 | 4.156 | 24 | 24 | 24 | 9.75
| 2017-03-17 | 72.4 | 57.5% | 84 | 61 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3657 | 3603 | 3603 | 3539 | 3648 | 46 | 0 | 44 | 0 | 61 | 0 | 109 | -64 | 154 | 98.7% | 152.375 | 96.77% | 100% | 100% | 10.378 | 154.36 | 1601.9481 | 31.02 | 940 | 29158.8 | 8691.9322 | 150.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1107 | 1067 | 1474 | -40 | 8691.9322 | 8691.9322 | 2.263 | 2.261 | 31.2 | 28.9 | 23 | 27.5 | 992.22 | 50 | 0.9272 | 95.2 | 85.7 | -9.5 | 12414 | 12564 | 150 | 4.524 | 24 | 24 | 24 | 7.16
| 2017-03-18 | 73.4 | 55.5% | 85 | 63 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3653 | 3597 | 3597 | 3538 | 3646 | 46 | 0 | 44 | 0 | 62 | 0 | 108 | -59 | 155 | 98.01% | 152.2083 | 96.85% | 100% | 100% | 10.449 | 150.57 | 1573.3059 | 31.083 | 940 | 29218.02 | 8703.0316 | 149.875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1101 | 1064 | 1481 | -37 | 8703.0316 | 8703.0316 | 2.328 | 2.328 | 31.1 | 28.8 | 22.9 | 27.6 | 990.67 | 50.03 | 0.928 | 94.9 | 85.6 | -9.3 | 12420 | 12569 | 149 | 4.656 | 24 | 24 | 24 | 7.58
Week 12 | 2017-03-19 | 75.7 | 53.1% | 91 | 65 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3634 | 3282 | 3282 | 3237 | 3333 | 45 | 0 | 44 | 0 | 62 | 0 | 96 | -45 | 143 | 97.12% | 151.4167 | 89.08% | 100% | 91.39% | 10.832 | 150.54 | 1630.6493 | 28.12 | 940 | 26432.8 | 8669.5858 | 136.75 | 0 | 0 | 0 | 0 | 13 | 1440 | 0 | 1091 | 1057 | 1185 | -34 | 8669.5858 | 8669.5858 | 0.668 | 0.661 | 30.8 | 28.62 | 22.69 | 27.52 | 992.96 | 49.97 | 0.9281 | 94.66 | 85.64 | -9.02 | 12470 | 12547 | 77 | 1.329 | 24 | 24 | 24 | 7.63
| 2017-03-20 | 77 | 57.1% | 90 | 64 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3621 | 3401 | 3401 | 3350 | 3453 | 45 | 0 | 43 | 0 | 62 | 0 | 103 | -51 | 150 | 95.92% | 150.875 | 92.52% | 100% | 95.33% | 10.677 | 150.88 | 1610.9458 | 29.353 | 941 | 27621.173 | 8726.0056 | 141.7083 | 0 | 0 | 0 | 0 | 7 | 1440 | 0 | 1078 | 1047 | 1328 | -31 | 8726.0056 | 8726.0056 | 1.556 | 1.556 | 30.6 | 28.36 | 22.51 | 27.52 | 993.63 | 49.98 | 0.9283 | 94.84 | 85.63 | -9.21 | 12500 | 12595 | 95 | 3.112 | 24 | 24 | 24
| 2017-03-21 | 79.16 | 56.69% | 93 | 68 | 20 | 2 | 20 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 3606 | 3293 | 3293 | 2999 | 3099 | 45 | 101 | 43 | 81 | 62 | 222 | 102 | -294 | 151 | 85.51% | 150.25 | 83.17% | 89.91% | 86.96% | 10.677 | 155.83 | 1663.7969 | 27.74 | 942 | 26131.08 | 9268.0483 | 137.2083 | 15 | 137 | 12 | 157 | 2 | 1218 | 2 | 942 | 941 | 1216 | -1 | 9268.0483 | 9268.0483 | 1.952 | 1.952 | 30.51 | 25.24 | 20.85 | 25.56 | 992 | 49.92 | 0.9267 | 93.67 | 85.58 | -8.09 | 12622 | 12782 | 160 | 3.904 | 20 | 19.92 | 19.1667 | 9.3167
| 2017-03-22 | 75.54 | 62.3% | 86 | 65 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3637 | 3516 | 3516 | 3455 | 3567 | 45 | 0 | 43 | 0 | 63 | 0 | 112 | -61 | 153 | 97.14% | 151.5417 | 95% | 100% | 98.01% | 10.448 | 150.28 | 1570.1254 | 30.31 | 946 | 28673.26 | 8753.5124 | 146.5 | 0 | 0 | 0 | 0 | 3 | 1440 | 0 | 1070 | 1039 | 1458 | -31 | 8753.5124 | 8753.5124 | 2.286 | 2.286 | 30.83 | 28.02 | 22.29 | 27.48 | 992 | 49.99 | 0.9281 | 94.88 | 85.77 | -9.11 | 12470 | 12591 | 121 | 4.572 | 24 | 24 | 24 | 6.75
| 2017-03-23 | 75.29 | 60.35% | 87 | 64 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3638 | 3522 | 3522 | 3459 | 3569 | 45 | 0 | 44 | 0 | 64 | 0 | 110 | -63 | 152 | 97.83% | 151.5833 | 95.08% | 100% | 98.04% | 10.525 | 148.9 | 1567.1725 | 30.325 | 946 | 28687.45 | 8746.6385 | 146.75 | 0 | 0 | 0 | 0 | 3 | 1440 | 0 | 1071 | 1045 | 1453 | -26 | 8746.6385 | 8746.6385 | 2.215 | 2.215 | 30.86 | 28.12 | 22.47 | 27.3 | 992.38 | 50.05 | 0.9279 | 94.65 | 85.78 | -8.87 | 12486 | 12580 | 94 | 4.43 | 24 | 24 | 24 | 7.78
| 2017-03-24 | 78.9 | 53.7% | 94 | 66 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3615 | 3522 | 3522 | 3453 | 3563 | 44 | 0 | 43 | 0 | 64 | 0 | 110 | -69 | 152 | 97.67% | 150.625 | 95.52% | 100% | 98.01% | 10.523 | 151.64 | 1595.7077 | 30.184 | 945 | 28523.88 | 8722.7303 | 146.75 | 0 | 0 | 0 | 0 | 3 | 1440 | 0 | 1060 | 1043 | 1460 | -17 | 8722.7303 | 8722.7303 | 2.274 | 2.274 | 30.43 | 27.91 | 22.3 | 27.3 | 999.33 | 50 | 0.9281 | 93.9 | 85.73 | -8.17 | 12514 | 12557 | 43 | 4.548 | 24 | 24 | 24 | 7.5
| 2017-03-25 | 79.4 | 57.3% | 92 | 71 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3598 | 3341 | 3341 | 3294 | 3396 | 44 | 0 | 43 | 0 | 64 | 0 | 102 | -47 | 147 | 96.26% | 149.9167 | 91.55% | 100% | 94.04% | 10.545 | 154.11 | 1625.09 | 28.79 | 944.5442 | 27193.4275 | 8748.791 | 139.2083 | 0 | 0 | 0 | 0 | 9 | 1440 | 0 | 1055 | 1034 | 1307 | -21 | 8748.791 | 8748.791 | 1.469 | 1.457 | 30.37 | 27.81 | 22.14 | 27.23 | 992.67 | 50 | 0.8493 | 94.33 | 85.79 | -8.54 | 12547 | 12566 | 19 | 2.926 | 23.16 | 23.52 | 24 | 8.08
Week 13 | 2017-03-26 | 82.4 | 53.7% | 97 | 70 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3573 | 3073 | 3073 | 3013 | 3109 | 43 | 0 | 43 | 0 | 64 | 0 | 96 | -60 | 135 | 95.96% | 148.875 | 84.33% | 100% | 86% | 10.555 | 151.35 | 1597.4992 | 25.973 | 945 | 24544.485 | 8676.397 | 128.0417 | 0 | 0 | 0 | 0 | 21 | 1440 | 0 | 1042 | 1029 | 1038 | -13 | 8676.397 | 8676.397 | 0 | 0 | 30.04 | 27.6 | 21.93 | 27.22 | 993.38 | 49.97 | 0.9275 | 93.89 | 85.67 | -8.22 | 12595 | 12556 | -39 | 0 | 0 | 0 | 24 | 7.72
| 2017-03-27 | 83.5 | 55.8% | 96 | 71 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3565 | 3209 | 3209 | 3153 | 3256 | 43 | 0 | 42 | 0 | 64 | 0 | 103 | -56 | 142 | 95.54% | 148.5417 | 88.44% | 100% | 90.6% | 10.53 | 150.79 | 1587.8187 | 27.423 | 944 | 25887.312 | 8713.9647 | 133.7083 | 0 | 0 | 0 | 0 | 14 | 1440 | 0 | 1033 | 1016 | 1207 | -17 | 8713.9647 | 8713.9647 | 0.996 | 1 | 29.9 | 27.4 | 21.8 | 26.9 | 991.5 | 49.95 | 0.9287 | 94.1 | 85.7 | -8.4 | 12631 | 12653 | 22 | 1.996 | 13 | 13 | 24 | 6.92
| 2017-03-28 | 83.8 | 58.5% | 94 | 73 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3558 | 3212 | 3212 | 3160 | 3263 | 43 | 0 | 42 | 0 | 64 | 0 | 103 | -52 | 142 | 95.75% | 148.25 | 88.81% | 100% | 91.28% | 10.33 | 153.03 | 1580.7999 | 27.59 | 944 | 26044.96 | 8742.3291 | 133.8333 | 0 | 0 | 0 | 0 | 13 | 1440 | 0 | 1027 | 1009 | 1227 | -18 | 8742.3291 | 8742.3291 | 1.131 | 1.131 | 29.9 | 27.3 | 21.7 | 26.7 | 990.3 | 49.97 | 0.9284 | 94.4 | 85.7 | -8.7 | 12638 | 12662 | 24 | 2.262 | 24 | 24 | 24 | 7.5
| 2017-03-29 | 85.8 | 53.8% | 98 | 74 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 3543 | 3312 | 3312 | 3253 | 3359 | 43 | 0 | 42 | 0 | 64 | 0 | 106 | -59 | 147 | 95.21% | 147.625 | 91.81% | 100% | 94.46% | 10.105 | 156.33 | 1579.7147 | 28.734 | 943.9358 | 27123.0513 | 8823.4755 | 138 | 0 | 0 | 0 | 0 | 9 | 1320 | 0 | 1021 | 1011 | 1327 | -10 | 8823.4755 | 8823.4755 | 1.733 | 1.707 | 29.7 | 27.17 | 21.84 | 26.68 | 989.4 | 50.03 | 0.9275 | 93.17 | 85.59 | -7.58 | 12649 | 12689 | 40 | 3.44 | 24 | 24 | 24 | 7.3
| 2017-03-30 | 85.6 | 52.3% | 98 | 74 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3546 | 3269 | 3269 | 3208 | 3313 | 42 | 0 | 42 | 0 | 64 | 0 | 105 | -61 | 150 | 92.03% | 147.75 | 90.47% | 100% | 92.57% | 10 | 153.77 | 1537.7 | 28.153 | 944 | 26576.432 | 8763.7569 | 136.2083 | 0 | 0 | 0 | 0 | 11 | 1440 | 0 | 1022 | 1013 | 1278 | -9 | 8763.7569 | 8763.7569 | 1.404 | 1.402 | 29.7 | 27.17 | 21.74 | 26.92 | 988.71 | 49.99 | 0.9279 | 93.65 | 85.59 | -8.06 | 12644 | 12654 | 10 | 2.806 | 24 | 24 | 24 | 7.58
| 2017-03-31 | 86.8 | 52.8% | 99 | 74 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3525 | 3159 | 3159 | 3103 | 3205 | 42 | 0 | 42 | 0 | 64 | 0 | 102 | -56 | 142 | 94.04% | 146.875 | 88.03% | 100% | 89.86% | 9.786 | 149.1 | 1459.0926 | 27.168 | 944 | 25646.592 | 8735.3157 | 131.625 | 0 | 0 | 0 | 0 | 15 | 1440 | 0 | 1016 | 1008 | 1181 | -8 | 8735.3157 | 8735.3157 | 0.937 | 0.891 | 29.54 | 27.08 | 21.69 | 26.77 | 989.13 | 50.02 | 0.9293 | 93.69 | 85.64 | -8.05 | 12674 | 12672 | -2 | 1.828 | 24 | 24 | 24 | 8.42
| 2017-04-01 | [25 empty] | 0 | 0 |  | no data | no data | no data | #DIV/0! | no data |  |  | 0 |  |  | 0 | no data | 0 | [10 empty] | 0 | no data | [12 empty] | 0 |  |  | 0 | 0
| Monthly | 72.8987 | 58.39% | 84.871 | 62.5161 | 722 | 23 | 723 | 11 | 0 | 0 | 0 | 1 | 66 | 1931 | 113040 | 104547 | 104461 | 102785.56 | 105805 | 45.2903 | 1107 | 44.2903 | 1024 | 63.0968 | 222 | 3017.44 | -1887 | 150.2258 | 94.68% | 151.9355 | 90.93% | 98.38% | 93.2% | 313.637 | 153.2932 | 47978.6619 | 899.711 | 940.951 | 846552.4038 | 8704.1639 |  | 37 | 202 | 32 | 225 | 245 | 40097 | 2 |  |  |  | 0 | 8704.1639 |  | 49.842 | 49.714 | 950.87 | 881.15 | 705.24 | 854.51 | 992.6545 | 50.0094 | 0.92465 | 93.8116 | 85.7652 |  | 12486.6129 | 12529.2581 |  | 99.556 | 686.63 | 687.84 | 683.7167 | 206.0467
| Totals | Avg.F | % Avg. | M Avg | m Avg | hrs | min | hrs | min | hrs | min | hrs | min | Avg Int Avi | Avg Ext Avi | MWhr Total | MWhr Total | MWhr Total | MWhr Total | MWhr Total | MW Avg | Total min | Avg MW | Total min | Avg MW | Total min | MWhr | Total MW | Av Max D/Gen | Av. DailyLF | Avg. | Avg. |  | Avg. | Total | Avg. |  | Total | Avg. |  | Avg. | [7 empty] | Total | 32755 | 32178 | 40872 | -577 | Avg. | [18 empty] | 687.235
-21.2
| Weeks data | Site Avg. Amb. Temp F | Site Avg. Relative humidity % | Max: Site Maximum/Minumum Temperature; CT1 hrs: CT-1 Base Load Hours; CT2 hrs: CT-2 Base Load Hours; CT1 hrs: CT-1 stand by hours / min; CT2 hrs: CT-2 standby hours / min; CT2 hrs: Plant ambient Corrected maximum Load hours/min | Average Corrected Plant Capacity | Ambient Corrected Declared Avail'y (MWH) | Av Plant WAPDA Dispatch | Net Plant Export (MWH) | Gross Generation | CT1 Av Cap (MW) | CT1 Unavail minutes | CT2 Av Cap (MW) | CT2 Unavail minutes | ST Unavail minutes | ST Average Cap (MW) | Plant Aux Load including Colony Load MWH | Differenece (+/-) MW | Maximum Daily Generation | Daily Load Factor | Avg. Corrected Plant |  |  | Equivalent Plant Availability | LBtu gas flow mmscf | 1 LBtu gas (Average Btu/scf) |  | PL gas flow (mscf/week) | 1 PL gas (Average Btu/scf) |  | Plant Net Heat Rate (Btu/Kwh) | [11 empty] | -22.25
| Week 9 | 69.2314 | 57.73% | 81.5714 | 58.1429 | 168 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 3678 | 3554.4286 | 3554.4286 | 3497.5714 | 3606.2857 | 45.5714 | #REF! | 44.8571 | #REF! | 441 | no data | no data | -398 | 153 | 98.21% | 153.25 | 95.09% | 100% | 97.97% | 73.32 | 157.2886 |  | 215.809 | 937.4286 |  | 8734.0901
| Week 10 | 65.8186 | 64.16% | 77.1429 | 57.2857 | 150 | 7 | 151 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 3697.4286 | 3156.7143 | 3144.4286 | 21719 | 22409 | 46.7143 | 1006 | 321 | no data | 441 | no data | 690 | -292 | 151.4286 | 88.18% | 154.0595 | 83.9% | 94.26% | 86.35% | 65.05 | 154.7871 |  | 189.498 | 939 |  | 8652.5052
| Week 11 | 68.0286 | 56.64% | 78.7143 | 58 | 168 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 64 | 47 | 3681.5714 | 3590.8571 | 3590.8571 | 24741 | 25500 | 46.2857 | No outage | 316 | no data | 438 | no data | 759 | -395 | 154.1429 | 98.47% | 153.3988 | 96.01% | 100% | 98.29% | 71.269 | 152.4457 |  | 217.476 | 939.2857 |  | 8695.5551
| Week 12 | 77.2843 | 57.22% | 90.4286 | 66.1429 | 164 | 2 | 164 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 3621.2857 | 3411 | 3411 | 23247 | 23980 | 44.7143 | 101 | 303 | no data | 441 | no data | 735 | -630 | 149.7143 | 95.35% | 150.8869 | 91.7% | 98.56% | 94.54% | 74.227 | 151.74 |  | 204.822 | 943.5063 |  | 8805.0446
| Week 13 | 84.65 | 0.54483 | 97 | 72.6667 | 144 | 0 | 144 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 3612.5714 | 3205.6667 | 3205.6667 | 18890 | 19505 | 42.6667 | No outage | 296 | no data | 384 | no data | 615 | -344 | 143 | 94.75% | 147.9861 | 88.65% | #DIV/0! | 90.8% | 61.306 | 152.395 |  | 165.041 | 944.156 |  | 8742.5398
| Date | Plant Status Whether Normal Operation or Tripping (State full detail for trippings/return to normal).
| 2017-03-01 | Plant load remained 139~149 MW to remain within allocated HBTU gas quota by M/S SNGPL.
| 2017-03-02 | Plant load remained 144~149 MW to remain within allocated HBTU gas quota by M/S SNGPL.
| 2017-03-03 | Plant load remained 144~148 MW to remain within allocated HBTU gas quota by M/S SNGPL.
| 2017-03-04 | Plant load remained 144~147 MW to remain within allocated HBTU gas quota by M/S SNGPL.
| 2017-03-05 | Plant load gradually reduced from 148 MW to 136 MW by decreasing duct burners firing at 0007 hrs to remain within restricted plant heat rate.
| 2017-03-06 | Plant load increased from 134 MW to 144 MW at 1105 hrs by increasing duct burner firing to achieve maximum export within allowable HBTU gas quota.
| 2017-03-07 | CT-2 de-synch @ 0021 hrs & synch @ 1604 hrs to avail "Approved Scheduled Outage - 2017".
| 2017-03-08 | CT-1 de-synch @ 0021 hrs & synch @ 1707 hrs to avail "Approved Scheduled Outage - 2017".
| 2017-03-09 | Plant load remained 140~150 MW to remain within allocated HBTU gas quota by SNGPL.
| 2017-03-10 | Plant load remained 145~149 MW to keep within allocated HBTU gas quota by SNGPL.
| 2017-03-11 | Plant load remained 145~150 MW to keep within HBTU gas quota by M/S SNGPL. Wapda Load Despatch of 135 MW received from 0039~0553 hrs.
| 2017-03-12 | Plant load remained 146~149 MW to keep within allocated HBTU gas quota by M/S SNGPL.
| 2017-03-13 | Plant load remained 145~149 MW to keep within allocated HBTU gas quota by M/S SNGPL.
| 2017-03-14 | Plant load remained 145~149 MW to keep within allocated HBTU gas quota by M/S SNGPL.
| 2017-03-15 | Plant load remained 145~149 MW to keep within allocated HBTU gas quota by M/S SNGPL.
| 2017-03-16 | Complex load increased from 146 to 151 MW @ 0813 hrs to achieve ambient corrected maximum export.
| 2017-03-17 | Normal operation, plant remained at base load throughout the day.
| 2017-03-18 | Normal operation, plant remained at base load throughout the day.
| 2017-03-19 | Plant load gradually reduced from 148 MW to 138 MW by decreasing duct burners firing at 0010 hrs to remain within restricted plant heat rate.
| 2017-03-20 | Plant load increased from 131 MW to 142 MW at 1105 hrs by increasing duct burner firing to achieve maximum export within allowable HBTU gas quota.
| 2017-03-21 | Complex Tripped at 0612 hrs due to WAPDA supply failure.After restoration of WAPDA supply at 0622 hrs, CT-2 synch @ 0733 hrs, CT-1 @ 0753 hrs & STG @ 0954 hrs.
| 2017-03-22 | Plant load remained 139~148 MW to keep within allocated HBTU gas quota by M/S SNGPL.
| 2017-03-23 | Plant load remained 139~148 MW to keep within allocated HBTU gas quota by M/S SNGPL.
| 2017-03-24 | Plant load remained 140~148 MW to keep within allocated HBTU gas quota by M/S SNGPL.
| 2017-03-25 | Plant load remained 129~143 MW to keep within allocated HBTU gas quota by SNGPL. Duct burners taken out of service at 2300 hrs to remain within restricted plant heat rate.
| 2017-03-26 | Plant load remained restricted 121~131 MW from 0000~2400 hrs as both duct burners remained off to remain within restricted plant heat rate.
| 2017-03-27 | Plant load increased from 124 to 136 MW by increasing duct burners firing at 1100 hrs and again reduced from 137 to 129 MW by decreasing duct burners firing at 2300 hrs to keep within restricted plant heat rate.
| 2017-03-28 | Plant load increased from 127 to 136 MW by increasing duct burners firing at 1700 hrs and again reduced from 139 to 130 MW by decreasing duct burners firing at 2300 hrs to keep within restricted plant heat rate.
| 2017-03-29 | Plant load increased from 129 to 139 MW by increasing duct firing at 1100 hrs to achieve maximum export within allowable gas quota.
| 2017-03-30 | Plant load decreased from 142 to 130 MW at 0900 hrs and from 130 to 126 MW at 2300 hrs by decreasing duct burners firing to remain within restricted plant heat rate.
| 2017-03-31 | Plant load remained 123~137 MW to remain within restricted plant heat rate.

## Apr
Monthly Operational Returns Kabirwala
2017-04-01
| Date | Site Avg. Ambient Temp.F | Site Avg. Relative Humidty % | Site Ambient Temp |  | Base load hours |  |  |  | Standby hours |  |  |  | Plant ambient corrected Max Load |  | Corrected Plant Capacity | Ambient Corrected Daclared Avail'y (MWH) | Plant WAPDA Dispatch (MWH) | Net Plant Export (MWH) | Gross Generation | CT1 Average Cap (MW) | CT1 Unavail minutes | CT2 Average Cap (MW) | CT2 Unavail minutes | ST Average Cap (MW) | ST Unavail minutes | Plant Aux Load including Colony Load MWH | Differenece (+/-) MW | Maximum Daily Generation | Daily Load Factor | Avg. Corrected Plant Capacity | Plant Capacity Factor | Plant Availability Factor | Equivalent Plant Availability | LBtu gas flow (mmscf/day) | 1 LBtu gas (Average Btu/scf) | LBTU MMBTU | 1 HBtu gas flow (mmscf/day) | 1 HBtu gas (Average Btu/scf) | HBTU MMBTU | HHV Net Heat Rate (Btu/Kwh) | Avg. declared availability | CT1 Derated MW | CT1 derated mintutes | CT-2 derated MW | CT-2 derated mintutes | ST derated MW | ST derated mintutes | WAPDA Backfeed (MWH) | CT-1 Gross Generation (MWH) | CT-2 Gross Generation (MWH) | STG Gross Generation (MWH) | CT-1 & CT-2 MWH difference | Base load Heat Rate | STG load | DB1 | DB2 | CT1 | CT1 Gas flow | CT2 Gas flow |  | Pamb | Freq. Hz | LBTU Gas Specific gravity | CT-1 compressor efficiency(%) | CT-2 compressor efficiency(%) |  | CT-1 Heat Rate (Btu/Kwh) | CT-2 Heat Rate (Btu/Kwh) |  | DB(1+2) | DB-1 Ops Hours | DB-2 Ops Hours | CT-1 Wetcomprssion Ops Hours | RO Operation Hours
[6 empty] | CT1 |  | CT2 |  | CT1 |  | CT2 | [43 empty] | mmscf/d | mmscf/d | WetC flow | HBTU KPPH | HBTU KPPH | LBTU KPPH | mbar | Hz | [7 empty] | mmscf/d
|  |  |  | Max | Min | hrs | min | hrs | min | hrs | min | hrs | min | hrs | min | [42 empty] | gpm
Week 13 | 2017-03-26 | 82.4 | 53.7% | 97 | 70 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3573 | 3073 | 3073 | 3013 | 3109 | 43 | 0 | 43 | 0 | 64 | 0 | 96 | -60 | 135 | 95.96% | 148.875 | 84.33% | 100% | 86% | 10.555 | 151.35 | 1597.4992 | 25.974 | 945 | 24545.43 | 8676.7107 | 128.0417 | 0 | 0 | 0 | 0 | 21 | 1440 | 0 | 1042 | 1029 | 1038 | -13 | 8676.7107 | 43.25 | 0 | 0 | 30.04 | 27.6 | 21.93 | 27.22 | 993.38 | 49.97 | 0.9275 | 93.89 | 85.67 | -8.22 | 12595 | 12556 | -39 | 0 | 0 | 0 | 24 | 7.72
| 2017-03-27 | 83.5 | 55.8% | 96 | 71 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3565 | 3209 | 3209 | 3153 | 3256 | 43 | 0 | 42 | 0 | 64 | 0 | 103 | -56 | 142 | 95.54% | 148.5417 | 88.44% | 100% | 90.6% | 10.53 | 150.79 | 1587.8187 | 27.423 | 944 | 25887.312 | 8713.9647 | 133.7083 | 0 | 0 | 0 | 0 | 14 | 1440 | 0 | 1033 | 1016 | 1207 | -17 | 8713.9647 | 50.2917 | 0.996 | 1 | 29.9 | 27.4 | 21.8 | 26.9 | 991.5 | 49.95 | 0.9287 | 94.1 | 85.7 | -8.4 | 12631 | 12653 | 22 | 1.996 | 13 | 13 | 24 | 6.92
| 2017-03-28 | 83.8 | 58.5% | 94 | 73 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3558 | 3212 | 3212 | 3160 | 3263 | 43 | 0 | 42 | 0 | 64 | 0 | 103 | -52 | 142 | 95.75% | 148.25 | 88.81% | 100% | 91.28% | 10.33 | 153.03 | 1580.7999 | 27.59 | 944 | 26044.96 | 8742.3291 | 133.8333 | 0 | 0 | 0 | 0 | 13 | 1440 | 0 | 1027 | 1009 | 1227 | -18 | 8742.3291 | 51.125 | 1.131 | 1.131 | 29.9 | 27.3 | 21.7 | 26.7 | 990.3 | 49.97 | 0.9284 | 94.4 | 85.7 | -8.7 | 12638 | 12662 | 24 | 2.262 | 24 | 24 | 24 | 7.5
| 2017-03-29 | 85.8 | 53.8% | 98 | 74 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 3543 | 3312 | 3312 | 3253 | 3359 | 43 | 0 | 42 | 0 | 64 | 0 | 106 | -59 | 147 | 95.21% | 147.625 | 91.81% | 100% | 94.46% | 10.105 | 156.33 | 1579.7147 | 28.734 | 944 | 27124.896 | 8824.0426 | 138 | 0 | 0 | 0 | 0 | 9 | 1320 | 0 | 1021 | 1011 | 1327 | -10 | 8824.0426 | 55.2917 | 1.733 | 1.707 | 29.7 | 27.17 | 21.84 | 26.68 | 989.4 | 50.03 | 0.9275 | 93.17 | 85.59 | -7.58 | 12649 | 12689 | 40 | 3.44 | 24 | 24 | 24 | 7.3
| 2017-03-30 | 85.6 | 52.3% | 98 | 74 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3546 | 3269 | 3269 | 3208 | 3313 | 42 | 0 | 42 | 0 | 64 | 0 | 105 | -61 | 150 | 92.03% | 147.75 | 90.47% | 100% | 92.57% | 10 | 153.77 | 1537.7 | 28.153 | 944 | 26576.432 | 8763.7569 | 136.2083 | 0 | 0 | 0 | 0 | 11 | 1440 | 0 | 1022 | 1013 | 1278 | -9 | 8763.7569 | 53.25 | 1.404 | 1.402 | 29.7 | 27.17 | 21.74 | 26.92 | 988.71 | 49.99 | 0.9279 | 93.65 | 85.59 | -8.06 | 12644 | 12654 | 10 | 2.806 | 24 | 24 | 24 | 7.58
| 2017-03-31 | 86.8 | 52.8% | 99 | 74 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3525 | 3159 | 3159 | 3103 | 3205 | 42 | 0 | 42 | 0 | 64 | 0 | 102 | -56 | 142 | 94.04% | 146.875 | 88.03% | 100% | 89.86% | 9.786 | 149.1 | 1459.0926 | 27.168 | 944 | 25646.592 | 8735.3157 | 131.625 | 0 | 0 | 0 | 0 | 15 | 1440 | 0 | 1016 | 1008 | 1181 | -8 | 8735.3157 | 49.2083 | 0.937 | 0.891 | 29.54 | 27.08 | 21.69 | 26.77 | 989.13 | 50.02 | 0.9293 | 93.69 | 85.64 | -8.05 | 12674 | 12672 | -2 | 1.828 | 24 | 24 | 24 | 8.42
| 2017-04-01 | 86.1 | 53.6% | 98 | 76 | 24 | 0 | 11 | 34 | 0 | 0 | 0 | 0 | 10 | 0 | 3537 | 2529 | 2529 | 2511 | 2607 | 42 | 0 | 42 | 668 | 62 | 0 | 96 | -18 | 148 | 73.4% | 147.375 | 70.99% | 86.66% | 74.44% | 4.96 | 163.61 | 811.5056 | 23.698 | 943 | 22347.214 | 9222.907 | 105.375 | 0 | 0 | 17 | 78 | 29 | 840 | 0 | 1014 | 526 | 1067 | -488 | 9222.907 | 44.4583 | 2.434 | 1.112 | 29.6 | 27.09 | 22 | 23.83 | 988.08 | 49.98 | 0.9248 | 93.76 | 86.49 | -7.27 | 12683 | 12330 | -353 | 3.546 | 23.18 | 11.32 | 24 | 8.46
Week 14 | 2017-04-02 | 87.2 | 50.14% | 102 | 71 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3522 | 3038 | 3038 | 2983 | 3082 | 42 | 0 | 43 | 0 | 62 | 0 | 99 | -55 | 133 | 96.55% | 146.75 | 84.7% | 100% | 85.71% | 9 | 157.79 | 1420.11 | 26.012 | 944 | 24555.328 | 8707.8237 | 126.5833 | 0 | 0 | 0 | 0 | 21 | 1440 | 0 | 1017 | 1037 | 1028 | 20 | 8707.8237 | 42.8333 | 0 | 0 | 29.51 | 27.09 | 22.16 | 24 | 986.1 | 50.05 | 0.9267 | 93.1 | 86.41 | -6.69 | 12679 | 12261 | -418 | 0 | 0 | 0 | 24 | 6.95
| 2017-04-03 | 86.41 | 45.79% | 100 | 74 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 12 | 49 | 3536 | 3252 | 3252 | 3192 | 3297 | 42 | 0 | 43 | 0 | 62 | 0 | 105 | -60 | 146 | 94.09% | 147.3333 | 90.27% | 100% | 93.98% | 9.025 | 156.54 | 1412.7735 | 28.045 | 943 | 26446.435 | 8727.8222 | 135.5 | 0 | 0 | 0 | 0 | 19 | 671 | 0 | 1018 | 1042 | 1237 | 24 | 8727.8222 | 51.5417 | 1.171 | 1.171 | 29.59 | 27.12 | 22.31 | 24.37 | 985.9 | 49.99 | 0.927 | 92.89 | 86.37 | -6.52 | 12665 | 12319 | -346 | 2.342 | 12.98 | 12.95 | 24 | 7.66
| 2017-04-04 | 85 | 54% | 96 | 74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3549 | 3463 | 3463 | 30 | 31 | 42 | 1418 | 43 | 1418 | 62 | 1418 | 24 | -3433 | 31 | 4.167% | 147.875 | 0.8453% | 1.528% | 0.3222% | 0 | 156.54 | 0 | 0.714 | 943 | 673.302 | 22443.4 | 144.2917 | 33 | 22 | 34 | 22 | 49 | 22 | 23 | 9 | 9 | 13 | 0 | 22443.4 | 0.54167 | 0 | 0 | 0 | 0.536 | 0.631 | 0.169 | 984.21 | 50.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16667 | 0.17 | 0 | 0
| 2017-04-05 | 81.8 | 59% | 94 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3574 | 3473 | 3473 | 0 | 0 | 42 | 1440 | 43 | 1440 | 63 | 1440 | 19 | -3473 | 0 | no data | 148.9167 | no data | 0% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 144.7083 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 981.6 | 50.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6
| 2017-04-06 | 76 | 56% | 85 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3636 | 3480 | 3480 | 0 | 0 | 43 | 1440 | 44 | 1440 | 63 | 1440 | 13 | -3480 | 0 | no data | 151.5 | no data | 0% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 982.7 | 50.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2017-04-07 | 73 | 48% | 85 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3648 | 3487 | 3487 | 0 | 0 | 43 | 1440 | 44 | 1440 | 63 | 1440 | 12 | -3487 | 0 | no data | 152 | no data | 0% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 145.2917 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 988.5 | 50.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2017-04-08 | 75.2 | 47.4% | 88 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3635 | 3491 | 3491 | 0 | 0 | 43 | 1440 | 44 | 1440 | 63 | 1440 | 13 | -3491 | 0 | no data | 151.4583 | no data | 0% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 145.4583 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 993.92 | 50.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Week 15 | 2017-04-09 | 77.6 | 41.4% | 92 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3612 | 3492 | 3492 | 0 | 0 | 43 | 1440 | 44 | 1440 | 63 | 1440 | 13 | -3492 | 0 | no data | 150.5 | no data | 0% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 145.5 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 994.1 | 50.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2017-04-10 | 81.4 | 37.5% | 97 | 67 | 11 | 4 | 11 | 10 | 0 | 0 | 0 | 0 | 10 | 30 | 3581 | 3462 | 3462 | 1593 | 1650 | 43 | 741 | 44 | 635 | 60 | 762 | 63 | -1869 | 149 | 46.14% | 149.2083 | 44.48% | 50.15% | 47.71% | 4.3 | 162.46 | 698.578 | 14.452 | 957.573 | 13838.845 | 9125.8148 | 144.25 | 27 | 35 | 21 | 135 | 29 | 48 | 6 | 486 | 546 | 618 | 60 | 9125.8148 | 25.75 | 1.084 | 0.467 | 29.5 | 25.5 | 21.2 | 25.2 | 991.3 | 50.06 | 0.9265 | 91.5 | 85.9 | -5.6 | 12220 | 12132 | -88 | 1.551 | 11 | 10.83 | 9.97 | 0
| 2017-04-11 | 85.7 | 34.8% | 101 | 70 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3536 | 3460 | 3460 | 3397 | 3507 | 43 | 0 | 44 | 0 | 58 | 0 | 110 | -63 | 151 | 96.77% | 147.3333 | 96.07% | 100% | 100% | 8.889 | 154.45 | 1372.906 | 29.401 | 959 | 28195.559 | 8704.2876 | 144.1667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1041 | 1064 | 1402 | 23 | 8704.2876 | 58.4167 | 2.173 | 1.638 | 29.7 | 26.73 | 22.07 | 24.7 | 989.33 | 50.04 | 0.9287 | 91.95 | 86.01 | -5.94 | 12338 | 12155 | -183 | 3.811 | 24 | 23.05 | 24 | 2.75
| 2017-04-12 | 88.9 | 34.5% | 105 | 72 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 3506 | 3423 | 3423 | 3384 | 3497 | 43 | 0 | 44 | 0 | 59 | 0 | 113 | -39 | 153 | 95.23% | 146.0833 | 96.52% | 100% | 99.6% | 8.849 | 155.35 | 1374.6922 | 29.402 | 960 | 28225.92 | 8747.2258 | 142.625 | 0 | 0 | 0 | 0 | 14 | 60 | 0 | 1025 | 1053 | 1419 | 28 | 8747.2258 | 59.125 | 2.059 | 2.067 | 29.33 | 26.98 | 22.37 | 24.25 | 987.9 | 49.98 | 0.9293 | 91.71 | 85.98 | -5.73 | 12744 | 12551 | -193 | 4.126 | 24 | 24 | 24 | 6.95
| 2017-04-13 | 90.2 | 33.6% | 108 | 76 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3495 | 3158 | 3158 | 3105 | 3203 | 42 | 0 | 43 | 0 | 60 | 0 | 98 | -53 | 137 | 97.41% | 145.625 | 88.84% | 100% | 91.03% | 8.913 | 153.86 | 1371.3542 | 27.021 | 956 | 25832.076 | 8761.1691 | 131.5833 | 0 | 0 | 0 | 0 | 13 | 1440 | 0 | 1017 | 1044 | 1142 | 27 | 8761.1691 | 47.5833 | 0.632 | 0.531 | 29.18 | 26.89 | 22.17 | 24.38 | 987.1 | 49.95 | 0.9289 | 91.65 | 85.97 | -5.68 | 12795 | 12580 | -215 | 1.163 | 24 | 24 | 24 | 6.73
| 2017-04-14 | 90.66 | 35.13% | 106 | 76 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3488 | 3150 | 3150 | 3087 | 3187 | 42 | 0 | 43 | 0 | 60 | 0 | 100 | -63 | 137 | 96.93% | 145.3333 | 88.5% | 100% | 91.03% | 8.84 | 154.66 | 1367.1944 | 26.789 | 954 | 25556.706 | 8721.704 | 131.25 | 0 | 0 | 0 | 0 | 13 | 1440 | 0 | 1014 | 1036 | 1137 | 22 | 8721.704 | 47.375 | 0.629 | 0.522 | 29.13 | 26.74 | 21.9 | 24.22 | 984.79 | 49.95 | 0.928 | 91.93 | 85.91 | -6.02 | 12771 | 12563 | -208 | 1.151 | 24 | 24 | 24 | 8.1
| 2017-04-15 | 92.9 | 34.4% | 108 | 78 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3472 | 3132 | 3132 | 3066 | 3165 | 42 | 0 | 43 | 0 | 60 | 0 | 99 | -66 | 135 | 97.69% | 144.6667 | 88.31% | 100% | 91.03% | 8.85 | 154.57 | 1367.9445 | 26.94 | 940 | 25323.6 | 8705.657 | 130.5 | 0 | 0 | 0 | 0 | 13 | 1440 | 0 | 1004 | 1028 | 1133 | 24 | 8705.657 | 47.2083 | 0.602 | 0.543 | 28.9 | 27.09 | 22.33 | 24.1 | 983.6 | 49.95 | 0.9288 | 91.85 | 85.85 | -6 | 13060 | 12837 | -223 | 1.145 | 23 | 23 | 24 | 7.37
Week 16 | 2017-04-16 | 94.55 | 34.08% | 110 | 79 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3455 | 3007 | 3007 | 2944 | 3042 | 41 | 0 | 43 | 0 | 60 | 0 | 98 | -63 | 132 | 96.02% | 143.9583 | 85.21% | 100% | 88.19% | 8.896 | 157.51 | 1401.209 | 25.684 | 940 | 24142.96 | 8676.6878 | 125.2917 | 0 | 0 | 0 | 0 | 17 | 1440 | 0 | 995 | 1023 | 1024 | 28 | 8676.6878 | 42.6667 | 0 | 0 | 28.68 | 26.94 | 22.23 | 24.17 | 982.75 | 49.9 | 0.9283 | 91.33 | 85.6 | -5.73 | 13091 | 12869 | -222 | 0 | 0 | 0 | 24 | 7
| 2017-04-17 | 94.9 | 37% | 107 | 79 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3446 | 3074 | 3074 | 3020 | 3122 | 41 | 0 | 42 | 0 | 60 | 0 | 102 | -54 | 134 | 97.08% | 143.5833 | 87.64% | 100% | 90.21% | 8.901 | 155.6 | 1384.9956 | 26.308 | 945 | 24861.06 | 8690.7469 | 128.0833 | 0 | 0 | 0 | 0 | 14 | 1440 | 0 | 988 | 1021 | 1113 | 33 | 8690.7469 | 46.375 | 0.518 | 0.524 | 28.3 | 26.7 | 22.1 | 24.3 | 983.8 | 49.97 | 0.9289 | 90.9 | 85.4 | -5.5 | 13075 | 12827 | -248 | 1.042 | 13 | 13 | 23.7 | 7.6
| 2017-04-18 | 95.4 | 34.3% | 108 | 83 | 20 | 9 | 20 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 3437 | 3060 | 3060 | 2602 | 2692 | 41 | 187 | 42 | 133 | 60 | 206 | 92 | -458 | 134 | 83.71% | 143.2083 | 75.71% | 87.56% | 75.28% | 8.901 | 158.8 | 1413.4788 | 22.667 | 944 | 21397.648 | 8766.7666 | 127.5 | 17 | 44 | 14 | 78 | 19 | 1234 | 2 | 852 | 913 | 927 | 61 | 8766.7666 | 38.625 | 0.356 | 0.318 | 28.2 | 23.2 | 21.4 | 23.8 | 981.9 | 49.8 | 0.927 | 88.3 | 84.9 | -3.4 | 13280 | 12975 | -305 | 0.674 | 14.8 | 14.7 | 18.2 | 7.6
| 2017-04-19 | 96.4 | 34% | 108 | 85 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3430 | 2968 | 2968 | 2910 | 3010 | 41 | 0 | 42 | 0 | 60 | 0 | 100 | -58 | 130 | 96.47% | 142.9167 | 84.84% | 100% | 87.41% | 8.875 | 150.25 | 1333.4688 | 25.225 | 944 | 23812.4 | 8641.192 | 123.6667 | 0 | 0 | 0 | 0 | 18 | 1440 | 0 | 979 | 1018 | 1013 | 39 | 8641.192 | 42.2083 | 0 | 0 | 28.5 | 26.5 | 22.1 | 24.1 | 978.3 | 50 | 0.9288 | 90.6 | 85.7 | -4.9 | 12888 | 12663 | -225 | 0 | 0 | 0 | 24 | 7.5
| 2017-04-20 | 95.8 | 35.3% | 110 | 81 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3433 | 2962 | 2962 | 2903 | 3005 | 41 | 0 | 42 | 0 | 60 | 0 | 102 | -59 | 131 | 95.58% | 143.0417 | 84.56% | 100% | 87.41% | 8.891 | 145.45 | 1293.1959 | 25.147 | 944 | 23738.768 | 8622.7916 | 123.4167 | 0 | 0 | 0 | 0 | 18 | 1440 | 0 | 986 | 1010 | 1009 | 24 | 8622.7916 | 42.0417 | 0 | 0 | 28.5 | 26.5 | 22 | 24 | 977.63 | 50 | 0.9304 | 91.7 | 85.9 | -5.8 | 12676 | 12535 | -141 | 0 | 0 | 0 | 24 | 7.6
| 2017-04-21 | 95.2 | 36.5% | 107 | 82 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3446 | 2952 | 2952 | 2903 | 3000 | 41 | 0 | 42 | 0 | 60 | 0 | 97 | -49 | 129 | 96.9% | 143.5833 | 84.24% | 100% | 87.41% | 8.77 | 146.23 | 1282.4371 | 25.243 | 945 | 23854.635 | 8658.9983 | 123 | 0 | 0 | 0 | 0 | 18 | 1440 | 0 | 983 | 1009 | 1008 | 26 | 8658.9983 | 42 | 0 | 0 | 28.5 | 26.5 | 22 | 24.1 | 980.1 | 50.06 | 0.9301 | 91.9 | 85.9 | -6 | 12683 | 12537 | -146 | 0 | 0 | 0 | 23.9 | 6.9
| 2017-04-22 | 87.7 | 43.8% | 98 | 75 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3525 | 3032 | 3032 | 2970 | 3072 | 41 | 0 | 42 | 0 | 60 | 0 | 102 | -62 | 133 | 96.24% | 146.875 | 84.26% | 100% | 88.11% | 8.8 | 146 | 1284.8 | 25.741 | 945 | 24325.245 | 8622.9108 | 126.3333 | 0 | 0 | 0 | 0 | 17 | 1440 | 0 | 1021 | 1030 | 1021 | 9 | 8622.9108 | 42.5417 | 0 | 0 | 29.4 | 27.2 | 22.3 | 24.4 | 982 | 50.09 | 0.9297 | 93.2 | 86.2 | -7 | 12553 | 12466 | -87 | 0 | 0 | 0 | 24 | 7.83
Week 17 | 2017-04-23 | 82.7 | 56.9% | 93 | 74 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3572 | 3068 | 3068 | 3006 | 3104 | 43 | 0 | 43 | 0 | 60 | 0 | 98 | -62 | 133 | 97.24% | 148.8333 | 84.15% | 100% | 88.36% | 8.835 | 148.08 | 1308.2868 | 26.019 | 945 | 24587.955 | 8614.8509 | 127.8333 | 0 | 0 | 0 | 0 | 17 | 1440 | 0 | 1044 | 1032 | 1028 | -12 | 8614.8509 | 42.8333 | 0 | 0 | 30 | 27.69 | 22.39 | 24.51 | 984.1 | 50.07 | 0.9296 | 95.05 | 86.62 | -8.43 | 12489 | 12448 | -41 | 0 | 0 | 0 | 24 | 7.47
| 2017-04-24 | 81.9 | 54.5% | 93 | 70 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3575 | 3082 | 3082 | 3022 | 3120 | 44 | 0 | 43 | 0 | 60 | 0 | 98 | -60 | 134 | 97.01% | 148.9583 | 84.53% | 100% | 88.44% | 8.792 | 146.6 | 1288.9072 | 26.25 | 944 | 24780 | 8626.3756 | 128.4167 | 0 | 0 | 0 | 0 | 17 | 1440 | 0 | 1048 | 1039 | 1033 | -9 | 8626.3756 | 43.0417 | 0 | 0 | 30.1 | 27.8 | 22.59 | 24.42 | 988.3 | 50.04 | 0.9297 | 94.48 | 86.41 | -8.07 | 12476 | 12455 | -21 | 0 | 0 | 0 | 24 | 7.92
| 2017-04-25 | 86.1 | 45.6% | 98 | 74 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3534 | 3058 | 3058 | 3000 | 3098 | 43 | 0 | 43 | 0 | 60 | 0 | 98 | -58 | 133 | 97.06% | 147.25 | 84.89% | 100% | 88.36% | 8.82 | 144.65 | 1275.813 | 26.091 | 945 | 24655.995 | 8643.936 | 127.4167 | 0 | 0 | 0 | 0 | 17 | 1440 | 0 | 1032 | 1036 | 1030 | 4 | 8643.936 | 42.9167 | 0 | 0 | 29.64 | 27.49 | 22.58 | 24.35 | 989.5 | 50.05 | 0.9301 | 93.51 | 86.27 | -7.24 | 12530 | 12477 | -53 | 0 | 0 | 0 | 24
| 2017-04-26 | 89.69 | 41.13% | 102 | 78 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 3500 | 3206 | 3206 | 3149 | 3254 | 42 | 0 | 43 | 0 | 60 | 0 | 105 | -57 | 144 | 94.16% | 145.8333 | 89.97% | 100% | 94.14% | 8.83 | 145.85 | 1287.8555 | 27.578 | 944 | 26033.632 | 8676.2425 | 133.5833 | 0 | 0 | 0 | 0 | 17 | 720 | 0 | 1017 | 1029 | 1208 | 12 | 8676.2425 | 50.3333 | 1.05 | 1.02 | 29.24 | 27.23 | 22.45 | 24.22 | 988.17 | 50.09 | 0.93 | 92.86 | 86.03 | -6.83 | 12590 | 12504 | -86 | 2.07 | 13.06 | 12.983 | 24 | 4.75
| 2017-04-27 | 88.48 | 40.1% | 101 | 76 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 3510 | 3258 | 3258 | 3192 | 3301 | 43 | 0 | 43 | 0 | 60 | 0 | 109 | -66 | 144 | 95.52% | 146.25 | 90.94% | 100% | 94.86% | 8.825 | 147.75 | 1303.8937 | 27.915 | 944 | 26351.76 | 8664.0519 | 135.75 | 0 | 0 | 0 | 0 | 15 | 720 | 0 | 1026 | 1032 | 1243 | 6 | 8664.0519 | 51.7917 | 1.3 | 1.22 | 29.37 | 27.4 | 22.53 | 24.2 | 989.96 | 50.08 | 0.9296 | 92.92 | 86.02 | -6.9 | 12582 | 12508 | -74 | 2.52 | 24 | 24 | 24 | 7.1
| 2017-04-28 | 91.54 | 41.45% | 102 | 80 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 3485 | 3230 | 3230 | 3164 | 3270 | 42 | 0 | 43 | 0 | 60 | 0 | 106 | -66 | 145 | 93.97% | 145.2083 | 90.79% | 100% | 94.83% | 8.72 | 148.43 | 1294.3096 | 27.728 | 944 | 26175.232 | 8681.9032 | 134.5833 | 0 | 0 | 0 | 0 | 15 | 720 | 0 | 1008 | 1024 | 1238 | 16 | 8681.9032 | 51.5833 | 1.26 | 1.18 | 29.03 | 27.08 | 22.34 | 24.12 | 988.38 | 50.09 | 0.9293 | 92.6 | 85.81 | -6.79 | 12626 | 12519 | -107 | 2.44 | 23.766 | 23.266 | 24 | 7.82
| 2017-04-29 | 88 | 41% | 97 | 76 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 3517 | 3221 | 3221 | 3160 | 3268 | 42 | 0 | 43 | 0 | 60 | 0 | 108 | -61 | 145 | 93.91% | 146.5417 | 89.85% | 100% | 94.48% | 8.735 | 148.59 | 1297.9336 | 27.654 | 945 | 26133.03 | 8680.6847 | 134.2083 | 0 | 0 | 0 | 0 | 16 | 720 | 0 | 1024 | 1028 | 1216 | 4 | 8680.6847 | 50.6667 | 1.109 | 1.069 | 29.37 | 27.29 | 22.36 | 24.32 | 988.54 | 50.12 | 0.9293 | 92.9 | 86.03 | -6.87 | 12538 | 12476 | -62 | 2.178 | 12 | 12 | 24 | 6.95
Week 18 | 2017-04-30 | 88.7 | 38% | 100 | 78 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3510 | 3039 | 3039 | 2979 | 3078 | 43 | 0 | 43 | 0 | 60 | 0 | 99 | -60 | 132 | 97.16% | 146.25 | 84.87% | 100% | 88.36% | 8.6 | 146.73 | 1261.878 | 25.628 | 945 | 24218.46 | 8553.3192 | 126.625 | 0 | 0 | 0 | 0 | 17 | 1440 | 0 | 1023 | 1029 | 1026 | 6 | 8553.3192 | 42.75 | 0 | 0 | 29.3 | 27.3 | 22.4 | 24.2 | 990.3 | 50.03 | 0.9302 | 92.58 | 85.87 | -6.71 | 12559 | 12494 | -65 | 0 | 0 | 0 | 24 | 7.95
| 2017-05-01 | [25 empty] | 0 | 0 |  | no data | no data | no data | #DIV/0! | no data |  |  | 0 |  |  | 0 | no data | 0 | [10 empty] | 0 | no data | 0 | [11 empty] | 0 |  |  | 0 | 0
| 2017-05-02 | [25 empty] | 0 | 0 |  | no data | no data | no data | #DIV/0! | no data |  |  | 0 |  |  | 0 | no data | 0 | [10 empty] | 0 | no data | 0 | [11 empty] | 0 |  |  | 0 | 0
| 2017-05-03 | [25 empty] | 0 | 0 |  | no data | no data | no data | #DIV/0! | no data |  |  | 0 |  |  | 0 | no data | 0 | [10 empty] | 0 | no data | 0 | [11 empty] | 0 |  |  | 0 | 0
| 2017-05-04 | [25 empty] | 0 | 0 |  | no data | no data | no data | #DIV/0! | no data |  |  | 0 |  |  | 0 | no data | 0 | [10 empty] | 0 | no data | 0 | [11 empty] | 0 |  |  | 0 | 0
| 2017-05-05 | [25 empty] | 0 | 0 |  | no data | no data | no data | #DIV/0! | no data |  |  | 0 |  |  | 0 | no data | 0 | [10 empty] | 0 | no data | 0 | [11 empty] | 0 |  |  | 0 | 0
| 2017-05-06 | [25 empty] | 0 | 0 |  | no data | no data | no data | #DIV/0! | no data |  |  | 0 |  |  | 0 | no data | 0 | [10 empty] | 0 | no data | 0 | [11 empty] | 0 |  |  | 0 | 0
| Monthly | 87.171 | 42.63% | 99.9667 | 74.2667 | 559 | 13 | 547 | 13 | 0 | 0 | 0 | 0 | 7 | 19 | 105702 | 95707 | 95707 | 71425.92 | 73662 | 42.2 | 318.2 | 43 | 335.1333 | 60.6667 | 319.5333 | 2337.08 | -24435 | 111.7667 | 89.06% | 146.8083 | 67.57% | 77.53% | 84.43% | 203.817 | 126.8783 | 30909.521 | 623.352 | 788.7524 | 590063.765 | 8693.9487 |  | 77 | 101 | 86 | 313 | 452 | 25915 | 101 | 23671 | 23658 | 26333 | -13 | 8693.9487 | 1097.2083 | 16.377 | 13.382 | 700.57 | 644.586 | 532.911 | 582.429 | 986.0953 | 50.0183 | 0.74299 | 73.839 | 68.785 |  | 10153.0333 | 10016.0333 |  | 29.759 | 266.9527 | 253.269 | 555.77 | 162.96
| Totals | Avg.F | % Avg. | M Avg | m Avg | hrs | min | hrs | min | hrs | min | hrs | min | Avg Int Avi | Avg Ext Avi | MWhr Total | MWhr Total | MWhr Total | MWhr Total | MWhr Total | MW Avg | Total min | Avg MW | Total min | Avg MW | Total min | MWhr | Total MW | Av Max D/Gen | Av. DailyLF | Avg. | Avg. |  | Avg. | Total | Avg. |  | Total | Avg. |  | Avg. | [7 empty] | Total |  |  |  |  | Avg. | [18 empty] | 260.1108
| Weeks data | Site Avg. Amb. Temp F | Site Avg. Relative humidity % | Max: Site Maximum/Minumum Temperature; CT1 hrs: CT-1 Base Load Hours; CT2 hrs: CT-2 Base Load Hours; CT1 hrs: CT-1 stand by hours / min; CT2 hrs: CT-2 standby hours / min; CT2 hrs: Plant ambient Corrected maximum Load hours/min | Average Corrected Plant Capacity | Ambient Corrected Declared Avail'y (MWH) | Av Plant WAPDA Dispatch | Net Plant Export (MWH) | Gross Generation | CT1 Av Cap (MW) | CT1 Unavail minutes | CT2 Av Cap (MW) | CT2 Unavail minutes | ST Unavail minutes | ST Average Cap (MW) | Plant Aux Load including Colony Load MWH | Differenece (+/-) MW | Maximum Daily Generation | Daily Load Factor | Avg. Corrected Plant | Plant Capacity Facto | Plant Availability Factor | Equivalent Plant Availability | LBtu gas flow mmscf | 1 LBtu gas (Average Btu/scf) | LBTU MMBTU | PL gas flow (mscf/week) | 1 PL gas (Average Btu/scf) | HBTU MMBTU | Plant Net Heat Rate (Btu/Kwh) | [11 empty] | 39.25
| Week 50 | 84.8571 | 54.36% | 97.1429 | 73.1429 | 168 | 0 | 155 | 34 | 0 | 0 | 0 | 0 | 12 | 0 | 3549.5714 | 3109 | 3109 | 3057.2857 | 3158.8571 | 42.5714 | No outage | 42.1429 | 668 | 446 | no data | no data | -362 | 143.7143 | 91.7% | 147.8988 | 86.13% | 98.09% | 88.46% | 66.266 | 153.9971 | 10204.7747 | 188.74 | 944 | 178170.56 | 8811.2895
| Week 51 | 80.6586 | 51.48% | 92.8571 | 68.4286 | 48 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 3585.7143 | 3383.4286 | 3383.4286 | 6205 | 6410 | 42.4286 | 7178 | 304 | no data | 438 | no data | 285 | -17479 | 44.2857 | 64.94% | 149.4048 | 58.6% | 28.79% | 60% | 18.025 | 67.2671 | 1212.4902 | 54.771 | 404.2857 | 22143.1329 | 13293.0153 | [5 empty] | 0.27381
| Week 52 | 86.7657 | 35.9% | 102.4286 | 71.8571 | 131 | 4 | 131 | 10 | 0 | 0 | 0 | 0 | 57 | 30 | 3527.1429 | 3325.2857 | 3325.2857 | no data | no data | 42.5714 | 2181 | 305 | 296.4286 | 420 | 314.5714 | 596 | -5645 | no data | 88.36% | 146.9643 | 83.79% | no data | 86.74% | no data | no data | #VALUE! | no data | no data | #VALUE! | 8794.3097 | [5 empty] | 0.26672
| Week 53 | 94.2786 | 36.43% | 106.8571 | 80.5714 | 164 | 9 | 164 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 3453.1429 | 3007.8571 | 3007.8571 | 20252 | 20943 | 41 | 187 | 295 | no data | 420 | no data | 693 | -803 | 131.8571 | 94.57% | 143.881 | 83.78% | 98.22% | 86.29% | 62.034 | 151.4057 | 9392.3021 | 176.015 | 943.8571 | 166133.015 | 8668.5849
| Week 54 | 87.1388 | 0.44835 | 98.25 | 75.75 | 192 | 0 | 192 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 3525.375 | 3145.25 | 3145.25 | 24672 | 25493 | 42.75 | #REF! | #REF! | no data | #REF! | no data | 821 | -490 | 138.75 | 95.75% | 146.8906 | 87.5% | #DIV/0! | 91.48% | 70.157 | 147.085 | 10319.0423 | 214.863 | 944.5 | 202938.1035 | 8642.6705
| Date | Plant Status Whether Normal Operation or Tripping (State full detail for trippings/return to normal).
| 2017-04-01 | CT-2 de-synch @ 0023 hrs and synch @ 1131 hrs for "compressor offline washing".
| 2017-04-02 | Plant load restricted to 119~130 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual plant heat rate.
| 2017-04-03 | Plant load increased from 123 MW to 138 MW @ 1100 hrs by taking both duct burners into service to achieve ambient corrected export.
| 2017-04-04 | Plant load gradually decreased for complete shutdown due to suspension of HBTU gas by SNGPL. CT-1, CT-2 & STG de-synch @ 0022 hrs.
| 2017-04-05 | Plant remained shutdown due to suspension of HBTU gas supply by SNGPL.
| 2017-04-06 | Plant remained shutdown due to suspension of HBTU gas supply by SNGPL.
| 2017-04-07 | Plant remained shutdown due to suspension of HBTU gas supply by SNGPL.
| 2017-04-08 | Plant remained shutdown due to suspension of HBTU gas supply by SNGPL.
| 2017-04-09 | Plant remained shutdown due to suspension of HBTU gas supply by SNGPL.
| 2017-04-10 | After restoration of HBTU gas supply by SNGPL, CT-1 synch @ 1221hrs, CT-2 synch @ 1035hrs and STG synch @ 1242hrs.
| 2017-04-11 | Normal operation, plant remained at base load throughout the day.
| 2017-04-12 | Plant load reduced from 144 to 130 MW by decreasing duct burners firing to remain within restricted plant heat rate.
| 2017-04-13 | Plant load restricted from 125~132 MW throughout the day to keep within contractual plant heat rate.
| 2017-04-14 | Plant load remained 124~132 MW throughout the day to keep within contractual plant heat rate.
| 2017-04-15 | Plant load remained 125~131 MW and Duct burners taken out of service at 2300 hrs to keep within restricted plant heat rate.
| 2017-04-16 | Plant load restricted 118~128 MW from 0000~2400 hrs as both duct burners remained off to keep within restricted plant heat rate.
| 2017-04-17 | Plant load remained 119~130 MW throughout the day to keep within contractual plant heat rate.
| 2017-04-18 | Plant tripped @ 0926 hrs due to “Wapda Supply Failure”. WAPDA supply restored at 0940hrs. CT-2 synch @ 1032 hrs, CT-1 synch @ 1055 hrs & STG synch @ 1106 hrs. Again Plant tripped @ 1639 hrs due to “Wapda Supply Failure”. After restoration of Wapda Supply @ 1654 hrs, CT-2 synch @ 1746 hrs, CT-1 synch @ 1817 hrs & STG synch @ 1825 hrs.
| 2017-04-19 | Plant load restricted to 117~126 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-04-20 | Plant load restricted to 116~127 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-04-21 | Plant load restricted to 118~125 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-04-22 | Plant load restricted to 120~128 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-04-23 | Plant load restricted to 122~129 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-04-24 | Plant load restricted to 122~130 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-04-25 | Plant load restricted to 121~129 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-04-26 | Plant load increased from 122 to 135 MW by taking duct burners into service at 1100 hrs to achieve maximum export, at 2300 hrs plant load reduced from 139 to 129 MW by decreasing duct burners firing to keep within restricted plant heat rate.
| 2017-04-27 | Plant load increased from 126 to 137 MW by taking duct burners into service at 1100 hrs to achieve maximum export. At 2300 hrs, plant load reduced from 140 to 127 MW by decreasing duct burners firing to keep within contractual plant heat rate.
| 2017-04-28 | Plant load increased from 123 to 134 MW by increasing duct firing at 1100 hrs to achieve maximum export. At 2300 hrs, plant load reduced from 140 to 128 MW by taking duct burners out of service to keep within contractual plant heat rate.
| 2017-04-29 | Plant load increased from 124 to 137 MW by increasing duct firing at 1100 hrs to achieve maximum export. At 2300 hrs, plant load reduced from 140 to 127 MW by taking duct burners out of service to keep within contractual plant heat rate.
| 2017-04-30 | Plant load restricted to 120~128 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.

## May
Monthly Operational Returns Kabirwala
2017-05-01
| Date | Site Avg. Ambient Temp.F | Site Avg. Relative Humidty % | Site Ambient Temp |  | Base load hours |  |  |  | Standby hours |  |  |  | Plant ambient corrected Max Load |  | Corrected Plant Capacity | Ambient Corrected Daclared Avail'y (MWH) | Plant WAPDA Dispatch (MWH) | Net Plant Export (MWH) | Gross Generation | CT1 Average Cap (MW) | CT1 Unavail minutes | CT2 Average Cap (MW) | CT2 Unavail minutes | ST Average Cap (MW) | ST Unavail minutes | Plant Aux Load including Colony Load MWH | Differenece (+/-) MW | Maximum Daily Generation | Daily Load Factor | Avg. Corrected Plant Capacity | Plant Capacity Factor | Plant Availability Factor | Equivalent Plant Availability | LBtu gas flow (mmscf/day) | 1 LBtu gas (Average Btu/scf) | LBTU MMBTU | 1 HBtu gas flow (mmscf/day) | 1 HBtu gas (Average Btu/scf) | HBTU MMBTU | HHV Net Heat Rate (Btu/Kwh) | Avg. declared availability | CT1 Derated MW | CT1 derated mintutes | CT-2 derated MW | CT-2 derated mintutes | ST derated MW | ST derated mintutes | WAPDA Backfeed (MWH) | CT-1 Gross Generation (MWH) | CT-2 Gross Generation (MWH) | STG Gross Generation (MWH) | CT-1 & CT-2 MWH difference | Base load Heat Rate | STG load | DB1 | DB2 | CT1 | CT1 Gas flow | CT2 Gas flow |  | Pamb | Freq. Hz | LBTU Gas Specific gravity | CT-1 compressor efficiency(%) | CT-2 compressor efficiency(%) |  | CT-1 Heat Rate (Btu/Kwh) | CT-2 Heat Rate (Btu/Kwh) |  | DB(1+2) | DB-1 Ops Hours | DB-2 Ops Hours | CT-1 Wetcomprssion Ops Hours | RO Operation Hours
[6 empty] | CT1 |  | CT2 |  | CT1 |  | CT2 | [43 empty] | mmscf/d | mmscf/d | WetC flow | HBTU KPPH | HBTU KPPH | LBTU KPPH | mbar | Hz | [7 empty] | mmscf/d
|  |  |  | Max | Min | hrs | min | hrs | min | hrs | min | hrs | min | hrs | min | [42 empty] | gpm
Week 18 | 2017-04-30 | 88.7 | 38% | 100 | 78 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3510 | 3039 | 3039 | 2979 | 3078 | 43 | 0 | 43 | 0 | 60 | 0 | 99 | -60 | 132 | 97.16% | 146.25 | 84.87% | 100% | 88.36% | 8.6 | 146.29 | 1258.094 | 25.628 | 945 | 24218.46 | 8552.049 | 126.625 | 0 | 0 | 0 | 0 | 17 | 1440 | 0 | 1023 | 1029 | 1026 | 6 | 8552.049 | 42.75 | 0 | 0 | 29.3 | 27.3 | 22.4 | 24.2 | 990.3 | 50.03 | 0.9302 | 92.58 | 85.87 | -6.71 | 12559 | 12494 | -65 | 0 | 0 | 0 | 24 | 7.95
| 2017-05-01 | 89 | 38% | 103 | 74 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 3510 | 3159 | 3159 | 3118 | 3226 | 41 | 0 | 43 | 0 | 60 | 0 | 108 | -41 | 146 | 92.07% | 146.25 | 88.83% | 100% | 94.1% | 8.605 | 148.29 | 1276.0355 | 27.514 | 944 | 25973.216 | 8739.3366 | 131.625 | 0 | 0 | 0 | 0 | 17 | 720 | 0 | 981 | 1027 | 1218 | 46 | 8739.3366 | 50.75 | 1.112 | 1.101 | 29.3 | 26.5 | 22.5 | 24.2 | 991.1 | 50.05 | 0.9299 | 89.9 | 85.74 | -4.16 | 12713 | 12537 | -176 | 2.213 | 13 | 13 | 16.2 | 6.8
| 2017-05-02 | 91.8 | 33.8% | 105 | 77 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 3478 | 3217 | 3217 | 3151 | 3259 | 42 | 0 | 43 | 0 | 60 | 0 | 108 | -66 | 143 | 94.96% | 144.9167 | 90.6% | 100% | 94.83% | 8.651 | 149.34 | 1291.9403 | 27.798 | 944 | 26241.312 | 8737.9411 | 134.0417 | 0 | 0 | 0 | 0 | 15 | 720 | 0 | 1010 | 1027 | 1222 | 17 | 8737.9411 | 50.9167 | 1.122 | 1.046 | 29 | 27.1 | 22.4 | 24.2 | 990.08 | 50.06 | 0.9295 | 91.5 | 85.6 | -5.9 | 12619 | 12530 | -89 | 2.168 | 24 | 24 | 24 | 6.75
| 2017-05-03 | 87.7 | 37.9% | 98 | 81 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 3521 | 3232 | 3232 | 3176 | 3283 | 43 | 0 | 43 | 0 | 60 | 0 | 107 | -56 | 145 | 94.34% | 146.7083 | 90.2% | 100% | 94.86% | 8.601 | 149.93 | 1289.5479 | 27.982 | 945 | 26442.99 | 8731.9074 | 134.6667 | 0 | 0 | 0 | 0 | 15 | 720 | 0 | 1020 | 1029 | 1234 | 9 | 8731.9074 | 51.4167 | 1.166 | 1.156 | 29.4 | 27.3 | 22.5 | 24.2 | 991.88 | 50.07 | 0.9293 | 92.3 | 85.9 | -6.4 | 12572 | 12518.3 | -53.7 | 2.322 | 24 | 24 | 24 | 7.13
| 2017-05-04 | 88.1 | 41.1% | 101 | 73 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 3515 | 3223 | 3223 | 3165 | 3272 | 43 | 0 | 43 | 0 | 60 | 0 | 107 | -58 | 143 | 95.34% | 146.4583 | 90.04% | 100% | 94.86% | 8.626 | 148.22 | 1278.5457 | 27.895 | 945 | 26360.775 | 8732.8028 | 134.2917 | 0 | 0 | 0 | 0 | 15 | 720 | 0 | 1025 | 1030 | 1217 | 5 | 8732.8028 | 50.7083 | 1.04 | 0.989 | 29.4 | 27.3 | 22.5 | 24.1 | 992.83 | 50.09 | 0.9298 | 92.6 | 85.8 | -6.8 | 12554 | 12510 | -44 | 2.029 | 24 | 24 | 24 | 7.1
| 2017-05-05 | 92.8 | 37.8% | 106 | 80 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 3471 | 3202 | 3202 | 3137 | 3247 | 42 | 0 | 42 | 0 | 60 | 0 | 110 | -65 | 143 | 94.61% | 144.625 | 90.38% | 100% | 94.79% | 8.592 | 147.24 | 1265.0861 | 27.745 | 944 | 26191.28 | 8752.4278 | 133.4167 | 0 | 0 | 0 | 0 | 15 | 720 | 0 | 1003 | 1017 | 1227 | 14 | 8752.4278 | 51.125 | 1.185 | 1.179 | 28.89 | 26.91 | 22.34 | 24.19 | 990.5 | 50.06 | 0.9301 | 92.04 | 85.67 | -6.37 | 12633 | 12610 | -23 | 2.364 | 24 | 24 | 24 | 7.25
| 2017-05-06 | 94.7 | 37.4% | 109 | 82 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 3450 | 3173 | 3173 | 3115 | 3221 | 41 | 0 | 42 | 0 | 60 | 0 | 106 | -58 | 142 | 94.51% | 143.75 | 90.29% | 100% | 94.76% | 8.577 | 144.84 | 1242.2927 | 27.585 | 944 | 26040.24 | 8758.4375 | 132.2083 | 0 | 0 | 0 | 0 | 15 | 720 | 0 | 991 | 1006 | 1224 | 15 | 8758.4375 | 51 | 1.192 | 1.145 | 28.7 | 26.74 | 22.4 | 24.12 | 989.29 | 50.07 | 0.9308 | 91.81 | 85.6 | -6.21 | 12683 | 12774 | 91 | 2.337 | 23 | 23 | 24 | 8.08
Week 19 | 2017-05-07 | 95.9 | 37.7% | 109 | 83 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3432 | 2949 | 2949 | 2891 | 2991 | 41 | 0 | 42 | 0 | 60 | 0 | 100 | -58 | 128 | 97.36% | 143 | 84.24% | 100% | 87.41% | 8.515 | 146.46 | 1247.1069 | 24.981 | 944 | 23582.064 | 8588.4368 | 122.875 | 0 | 0 | 0 | 0 | 18 | 1440 | 0 | 985 | 997 | 1009 | 12 | 8588.4368 | 42.0417 | 0 | 0 | 28.5 | 26.58 | 22.14 | 24.18 | 988.58 | 50.02 | 0.9306 | 91.84 | 85.56 | -6.28 | 12703 | 12769 | 66 | 0 | 0 | 0 | 24 | 7.5
| 2017-05-08 | 97.97 | 35.91% | 111 | 84 | 21 | 53 | 22 | 19 | 0 | 0 | 0 | 0 | 3 | 30 | 3413 | 3039.5 | 3039.5 | 2728 | 2825 | 41 | 110 | 42 | 82 | 60 | 117 | 99 | -311.5 | 138 | 85.3% | 142.2083 | 79.93% | 92.73% | 82.53% | 8.515 | 149.61 | 1273.9292 | 24.179 | 944 | 22824.976 | 8833.9095 | 126.6458 | 19 | 17 | 20 | 19 | 18 | 1128 | 2 | 899 | 937 | 989 | 38 | 8833.9095 | 41.2083 | 0.469 | 0.385 | 28.34 | 24.44 | 21.09 | 22.73 | 987.1 | 50.02 | 0.929 | 91.84 | 85.52 | -6.32 | 12726 | 12817 | 91 | 0.854 | 4.5 | 3.58 | 20.53 | 7.03
| 2017-05-09 | 96.76 | 33.9% | 109 | 85 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 3428 | 3148 | 3148 | 3083 | 3192 | 41 | 0 | 42 | 0 | 60 | 0 | 109 | -65 | 141 | 94.33% | 142.8333 | 89.94% | 100% | 94.06% | 8.555 | 149.93 | 1282.6511 | 27.143 | 945 | 25650.135 | 8735.9021 | 131.1667 | 0 | 0 | 0 | 0 | 17 | 720 | 0 | 982 | 1005 | 1205 | 23 | 8735.9021 | 50.2083 | 1.101 | 1.091 | 28.45 | 26.46 | 22.38 | 24.04 | 985.54 | 50.08 | 0.93 | 91.22 | 85.53 | -5.69 | 12673 | 12760 | 87 | 2.192 | 13.08 | 13.166 | 24 | 7.9
| 2017-05-10 | 94.66 | 40.1% | 107 | 83 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 3455 | 3161 | 3161 | 3095 | 3205 | 41 | 0 | 42 | 0 | 62 | 0 | 110 | -66 | 143 | 93.39% | 143.9583 | 89.58% | 100% | 94.48% | 8.54 | 145.61 | 1243.5094 | 27.355 | 944 | 25823.12 | 8745.2761 | 131.7083 | 0 | 0 | 0 | 0 | 16 | 720 | 0 | 987 | 999 | 1219 | 12 | 8745.2761 | 50.7917 | 1.236 | 1.183 | 28.67 | 26.58 | 22.27 | 24.01 | 985.38 | 50.05 | 0.9311 | 92.29 | 85.77 | -6.52 | 12679 | 12805 | 126 | 2.419 | 24 | 24 | 24 | 7.866
| 2017-05-11 | 90.1 | 46.9% | 101 | 79 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 3495 | 3169 | 3169 | 3112 | 3219 | 42 | 0 | 42 | 0 | 60 | 0 | 107 | -57 | 140 | 95.8% | 145.625 | 89.04% | 100% | 94.44% | 8.535 | 142.72 | 1218.1152 | 27.571 | 943 | 25999.453 | 8746.0052 | 132.0417 | 0 | 0 | 0 | 0 | 16 | 720 | 0 | 1007 | 1012 | 1200 | 5 | 8746.0052 | 50 | 1.059 | 0.983 | 28.9 | 27.06 | 22.6 | 24.1 | 990.8 | 50 | 0.9316 | 93.69 | 86 | -7.69 | 12634 | 12769 | 135 | 2.042 | 24 | 24 | 24 | 7.1
| 2017-05-12 | 95 | 43% | 107 | 82 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 3451 | 3160 | 3160 | 3099 | 3206 | 42 | 0 | 42 | 0 | 60 | 0 | 107 | -61 | 142 | 94.07% | 143.7917 | 89.8% | 100% | 94.44% | 8.565 | 145.1 | 1242.7815 | 27.465 | 943 | 25899.495 | 8758.3984 | 131.6667 | 0 | 0 | 0 | 0 | 16 | 720 | 0 | 991 | 1005 | 1210 | 14 | 8758.3984 | 50.4167 | 1.154 | 1.152 | 28.4 | 26.8 | 22.5 | 24.1 | 990.8 | 50.09 | 0.931 | 92.89 | 85.9 | -6.99 | 12704 | 12811 | 107 | 2.306 | 24 | 24 | 24 | 7.4
| 2017-05-13 | 95 | 39% | 107 | 82 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 3447 | 3157 | 3157 | 3096 | 3205 | 42 | 0 | 42 | 0 | 60 | 0 | 109 | -61 | 141 | 94.71% | 143.625 | 89.82% | 100% | 94.44% | 8.57 | 146.81 | 1258.1617 | 27.441 | 942 | 25849.422 | 8755.6795 | 131.5417 | 0 | 0 | 0 | 0 | 16 | 720 | 0 | 987 | 1008 | 1210 | 21 | 8755.6795 | 50.4167 | 1.137 | 1.137 | 28.6 | 26.7 | 22.5 | 24.1 | 988 | 50.08 | 0.9304 | 92.16 | 85.7 | -6.46 | 12720 | 12793 | 73 | 2.274 | 23 | 23 | 24 | 7.5
Week 20 | 2017-05-14 | 97.2 | 38.7% | 109 | 85 | 22 | 22 | 22 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 3419 | 2979 | 2979 | 2679 | 2773 | 42 | 98 | 42 | 73 | 60 | 110 | 94 | -300 | 128 | 90.27% | 142.4583 | 78.36% | 93.35% | 81.38% | 8.561 | 144.12 | 1233.8113 | 23.751 | 942 | 22373.442 | 8811.9647 | 124.125 | 24 | 22 | 21 | 17 | 18 | 1330 | 0 | 906 | 944 | 923 | 38 | 8811.9647 | 38.4583 | 0 | 0 | 28.5 | 24.7 | 21.3 | 22.4 | 985.2 | 50.07 | 0.9315 | 92.3 | 85.8 | -6.5 | 12740 | 12811 | 71 | 0 | 0 | 0 | 21.03 | 7.47
| 2017-05-15 | 97.6 | 37.9% | 108 | 87 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 3423 | 3122 | 3122 | 3052 | 3162 | 41 | 0 | 42 | 0 | 60 | 0 | 110 | -70 | 140 | 94.11% | 142.625 | 89.16% | 100% | 93.71% | 8.524 | 148.06 | 1262.0634 | 27.055 | 941 | 25458.755 | 8755.183 | 130.0833 | 0 | 0 | 0 | 0 | 18 | 720 | 0 | 974 | 1006 | 1182 | 32 | 8755.183 | 49.25 | 1.004 | 1.004 | 28.3 | 26.4 | 22.5 | 23.9 | 983.88 | 50.1 | 0.9298 | 91.6 | 85.7 | -5.9 | 12764 | 12791 | 27 | 2.008 | 13 | 13 | 24 | 6.47
| 2017-05-16 | 93.7 | 42.8% | 105 | 81 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 3468 | 3164 | 3164 | 3104 | 3213 | 42 | 0 | 42 | 0 | 60 | 0 | 109 | -60 | 143 | 93.62% | 144.5 | 89.5% | 100% | 94.44% | 8.469 | 147.71 | 1250.956 | 27.551 | 942 | 25953.042 | 8764.1746 | 131.8333 | 0 | 0 | 0 | 0 | 16 | 720 | 0 | 982 | 1014 | 1217 | 32 | 8764.1746 | 50.7083 | 1.16 | 1.16 | 29.3 | 26.5 | 22.5 | 24.1 | 983.7 | 50.14 | 0.9303 | 91.6 | 85.9 | -5.7 | 12719 | 12675 | -44 | 2.32 | 24 | 24 | 15.2 | 6.23
| 2017-05-17 | 89.4 | 50.1% | 99 | 78 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 3502 | 3194 | 3194 | 3133 | 3241 | 42 | 0 | 42 | 0 | 60 | 0 | 108 | -61 | 141 | 95.77% | 145.9167 | 89.46% | 100% | 94.79% | 8.44 | 144.97 | 1223.5468 | 27.782 | 943 | 26198.426 | 8752.6246 | 133.0833 | 0 | 0 | 0 | 0 | 15 | 720 | 0 | 1008 | 1013 | 1220 | 5 | 8752.6246 | 50.8333 | 1.187 | 1.185 | 29.3 | 27.05 | 22.51 | 24.29 | 985.63 | 50.14 | 0.9303 | 93.95 | 86.27 | -7.68 | 12630 | 12622 | -8 | 2.372 | 24 | 24 | 24 | 7.22
| 2017-05-18 | 94.1 | 46.3% | 106 | 82 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 3455 | 3153 | 3153 | 3086 | 3194 | 41 | 0 | 41 | 0 | 60 | 0 | 108 | -67 | 143 | 93.07% | 143.9583 | 89.32% | 100% | 94.37% | 8.515 | 145.27 | 1236.9741 | 27.375 | 942 | 25787.25 | 8757.0395 | 131.375 | 0 | 0 | 0 | 0 | 16 | 720 | 0 | 979 | 1000 | 1215 | 21 | 8757.0395 | 50.625 | 1.242 | 1.215 | 28.9 | 26.5 | 22.29 | 24.16 | 985.21 | 50.09 | 0.9304 | 92.22 | 86.09 | -6.13 | 12743 | 12701 | -42 | 2.457 | 24 | 24 | 14.43 | 5.77
| 2017-05-19 | 97.5 | 38.9% | 109 | 85 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 3420 | 3153 | 3153 | 3085 | 3191 | 40 | 0 | 42 | 0 | 60 | 0 | 106 | -68 | 141 | 94.3% | 142.5 | 90.2% | 100% | 94.37% | 8.513 | 147.12 | 1252.4326 | 27.285 | 945 | 25784.325 | 8763.9409 | 131.375 | 0 | 0 | 0 | 0 | 16 | 720 | 0 | 968 | 996 | 1227 | 28 | 8763.9409 | 51.125 | 1.284 | 1.234 | 28.05 | 26.23 | 22.15 | 24.12 | 984.17 | 50.1 | 0.9299 | 91.06 | 85.83 | -5.23 | 12749 | 12651 | -98 | 2.518 | 24 | 24 | 11.83 | 5.5
| 2017-05-20 | 95.98 | 39.41% | 106 | 84 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 3437 | 3163 | 3163 | 3098 | 3208 | 41 | 0 | 42 | 0 | 60 | 0 | 110 | -65 | 142 | 94.13% | 143.2083 | 90.14% | 100% | 94.41% | 8.557 | 148.35 | 1269.4309 | 27.398 | 944 | 25863.712 | 8758.2773 | 131.7917 | 0 | 0 | 0 | 0 | 16 | 720 | 0 | 979 | 1006 | 1223 | 27 | 8758.2773 | 50.9583 | 1.227 | 1.181 | 28.41 | 26.48 | 22.37 | 24.06 | 983.42 | 50.11 | 0.9301 | 91.9 | 85.86 | -6.04 | 12721 | 12644 | -77 | 2.408 | 23.1 | 23.116 | 24 | 6.78
Week 21 | 2017-05-21 | 88.92 | 44.69% | 97 | 82 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3514 | 3021 | 3021 | 2954 | 3052 | 42 | 0 | 43 | 0 | 60 | 0 | 98 | -67 | 130 | 97.82% | 146.4167 | 84.06% | 100% | 87.59% | 8.58 | 147.85 | 1268.553 | 25.661 | 943 | 24198.323 | 8621.1496 | 125.875 | 0 | 0 | 0 | 0 | 18 | 1440 | 0 | 1013 | 1022 | 1017 | 9 | 8621.1496 | 42.375 | 0 | 0 | 29.31 | 27.14 | 22.61 | 24.32 | 985.3 | 50.15 | 0.9302 | 93.11 | 86.25 | -6.86 | 12607 | 12566 | -41 | 0 | 0 | 0 | 24 | 6.51
| 2017-05-22 | 89.89 | 46.72% | 101 | 77 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3495 | 3013 | 3013 | 2946 | 3046 | 42 | 0 | 43 | 0 | 60 | 0 | 100 | -67 | 131 | 96.88% | 145.625 | 84.29% | 100% | 88.28% | 8.615 | 149.46 | 1287.5979 | 25.541 | 943 | 24085.163 | 8612.614 | 125.5417 | 0 | 0 | 0 | 0 | 17 | 1440 | 0 | 1008 | 1019 | 1019 | 11 | 8612.614 | 42.4583 | 0 | 0 | 29.37 | 27.07 | 22.64 | 24.21 | 987.96 | 50.12 | 0.9295 | 93.09 | 86.1 | -6.99 | 12632 | 12599 | -33 | 0 | 0 | 0 | 23.32 | 7.43
| 2017-05-23 | 95.3 | 42.7% | 105 | 83 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3447 | 2963 | 2963 | 2895 | 2994 | 41 | 0 | 42 | 0 | 60 | 0 | 99 | -68 | 129 | 96.71% | 143.625 | 83.99% | 100% | 87.41% | 8.54 | 146.35 | 1249.829 | 25.108 | 943 | 23676.844 | 8610.2497 | 123.4583 | 0 | 0 | 0 | 0 | 18 | 1440 | 0 | 985 | 1003 | 1006 | 18 | 8610.2497 | 41.9167 | 0 | 0 | 28.6 | 26.65 | 22.3 | 24.2 | 986.7 | 50.15 | 0.9306 | 92.4 | 86 | -6.4 | 12721 | 12652 | -69 | 0 | 0 | 0 | 23.9 | 6.85
| 2017-05-24 | 97 | 43% | 108 | 86 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3427 | 2935 | 2935 | 2868 | 2969 | 40 | 0 | 41 | 0 | 60 | 0 | 101 | -67 | 127 | 97.41% | 142.7917 | 83.69% | 100% | 87.23% | 8.545 | 146.46 | 1251.5007 | 24.919 | 944 | 23523.536 | 8638.4368 | 122.2917 | 0 | 0 | 0 | 0 | 18 | 1440 | 0 | 972 | 996 | 1001 | 24 | 8638.4368 | 41.7083 | 0 | 0 | 28.3 | 26.4 | 22.2 | 24.1 | 985.1 | 50.07 | 0.9307 | 92.3 | 85.9 | -6.4 | 12774 | 12687 | -87 | 0 | 0 | 0 | 23.9 | 7
| 2017-05-25 | 100.4 | 38.3% | 113 | 86 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3392 | 2916 | 2916 | 2851 | 2951 | 40 | 0 | 41 | 0 | 60 | 0 | 100 | -65 | 126 | 97.59% | 141.3333 | 84.05% | 100% | 87.23% | 8.53 | 145.63 | 1242.2239 | 24.811 | 943 | 23396.773 | 8642.2297 | 121.5 | 0 | 0 | 0 | 0 | 18 | 1440 | 0 | 963 | 990 | 998 | 27 | 8642.2297 | 41.5833 | 0 | 0 | 28 | 26.2 | 22.1 | 24.01 | 983.1 | 50.08 | 0.9309 | 91.4 | 85.8 | -5.6 | 12788 | 12694 | -94 | 0 | 0 | 0 | 24 | 7.5
| 2017-05-26 | 102.2 | 34.2% | 115 | 89 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 3372 | 3096 | 3096 | 3028 | 3138 | 40 | 0 | 41 | 0 | 60 | 0 | 110 | -68 | 139 | 94.06% | 140.5 | 89.8% | 100% | 93.62% | 8.51 | 140.78 | 1198.0378 | 26.959 | 946 | 25503.214 | 8818.1149 | 129 | 0 | 0 | 0 | 0 | 18 | 720 | 0 | 955 | 989 | 1194 | 34 | 8818.1149 | 49.75 | 1.12 | 1.18 | 27.8 | 25.9 | 22 | 23.9 | 981.13 | 50.06 | 0.9328 | 90.6 | 85.7 | -4.9 | 12779 | 12697 | -82 | 2.3 | 13 | 13 | 24 | 7.35
| 2017-05-27 | 100.6 | 42.4% | 111 | 90 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 3387 | 3106 | 3106 | 3035 | 3142 | 40 | 0 | 41 | 0 | 60 | 0 | 107 | -71 | 139 | 94.18% | 141.125 | 89.61% | 100% | 93.97% | 8.52 | 140.61 | 1197.9972 | 27.021 | 948 | 25615.908 | 8834.8946 | 129.4167 | 0 | 0 | 0 | 0 | 17 | 720 | 0 | 956 | 976 | 1210 | 20 | 8834.8946 | 50.4167 | 1.328 | 1.282 | 28 | 26 | 21.7 | 24 | 979 | 50.04 | 0.9324 | 92.3 | 85.9 | -6.4 | 12758 | 12734 | -24 | 2.61 | 23 | 23 | 24 | 7.88
Week 22 | 2017-05-28 | 100.6 | 42.7% | 112 | 88 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3392 | 2884 | 2884 | 2818 | 2919 | 40 | 0 | 41 | 0 | 60 | 0 | 101 | -66 | 124 | 98.08% | 141.3333 | 83.08% | 100% | 86.52% | 8.525 | 144.77 | 1234.1643 | 24.441 | 949 | 23194.509 | 8668.7982 | 120.1667 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 957 | 976 | 986 | 19 | 8668.7982 | 41.0833 | 0 | 0 | 28 | 25.9 | 21.6 | 23.9 | 979 | 50.08 | 0.9316 | 92.2 | 85.8 | -6.4 | 12749 | 12689 | -60 | 0 | 0 | 0 | 24 | 7.52
| 2017-05-29 | 95 | 43.2% | 105 | 84 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3447 | 2943 | 2943 | 2876 | 2972 | 41 | 0 | 41 | 0 | 60 | 0 | 96 | -67 | 127 | 97.51% | 143.625 | 83.43% | 100% | 86.62% | 8.511 | 143.71 | 1223.1158 | 24.982 | 945 | 23607.99 | 8633.9033 | 122.625 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 976 | 997 | 999 | 21 | 8633.9033 | 41.625 | 0 | 0 | 28.64 | 26.47 | 22.18 | 24.03 | 981.1 | 50.1 | 0.9317 | 92.7 | 86.05 | -6.65 | 12702 | 12654 | -48 | 0 | 0 | 0 | 24 | 6.77
| 2017-05-30 | 95.7 | 46.8% | 108 | 84 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3440 | 2926 | 2926 | 2860 | 2964 | 41 | 0 | 41 | 0 | 60 | 0 | 104 | -66 | 127 | 97.24% | 143.3333 | 83.14% | 100% | 86.62% | 8.557 | 141.02 | 1206.7081 | 24.823 | 945 | 23457.735 | 8623.9312 | 121.9167 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 978 | 992 | 994 | 14 | 8623.9312 | 41.4167 | 0 | 0 | 28.57 | 26.35 | 22.03 | 23.95 | 979.5 | 50.09 | 0.9322 | 92.98 | 86.12 | -6.86 | 12706 | 12667 | -39 | 0 | 0 | 0 | 24 | 7.17
| 2017-05-31 | 92.1 | 48% | 99 | 84 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 3479 | 3134 | 3134 | 3074 | 3186 | 41 | 0 | 42 | 0 | 60 | 0 | 112 | -60 | 143 | 92.83% | 144.9583 | 88.36% | 100% | 93.71% | 8.565 | 139.92 | 1198.4148 | 27.255 | 946 | 25783.23 | 8777.3731 | 130.5833 | 0 | 0 | 0 | 0 | 18 | 720 | 0 | 993 | 1001 | 1192 | 8 | 8777.3731 | 49.6667 | 1.109 | 1.103 | 28.9 | 26.6 | 22.3 | 23.9 | 980.8 | 50.17 | 0.9325 | 93.46 | 86.38 | -7.08 | 12642 | 12640 | -2 | 2.212 | 13 | 13 | 24 | 7.33
| 2017-06-01 | [25 empty] | 0 | 0 |  | no data | no data | no data | #DIV/0! | no data |  |  | 0 |  |  | 0 | no data | 0 | [10 empty] | 0 | no data | 0 | [11 empty] | 0 |  |  | 0 | 0
| 2017-06-02 | [25 empty] | 0 | 0 |  | no data | no data | no data | #DIV/0! | no data |  |  | 0 |  |  | 0 | no data | 0 | [10 empty] | 0 | no data | 0 | [11 empty] | 0 |  |  | 0 | 0
| 2017-06-03 | [25 empty] | 0 | 0 |  | no data | no data | no data | #DIV/0! | no data |  |  | 0 |  |  | 0 | no data | 0 | [10 empty] | 0 | no data | 0 | [11 empty] | 0 |  |  | 0 | 0
| Monthly | 94.6026 | 40.95% | 106.0968 | 82.5806 | 740 | 15 | 741 | 6 | 0 | 0 | 0 | 0 | 3 | 30 | 106982 | 95854.5 | 95854.5 | 93606.87 | 96666 | 41.2581 | 208 | 41.9355 | 155 | 60.0645 | 227 | 3061.13 | -2446.5 | 137.2581 | 94.72% | 143.793 | 87.5% | 99.55% | 91.49% | 265.024 | 146.0084 | 38697.0608 | 822.372 | 944.0323 | 776340.655 | 8707.0288 |  | 43 | 39 | 41 | 36 | 523 | 29818 | 2 | 30420 | 31039 | 35207 | 619 | 8707.0288 | 1466.9583 | 23.634 | 23.091 | 28.671 | 26.4842 | 22.2387 | 23.9942 | 985.8639 | 50.0839 | 0.93066 | 92.1694 | 85.8626 |  | 12694.7419 | 12683.1387 |  | 46.725 | 425.68 | 424.862 | 698.34 | 220.156
| Totals | Avg.F | % Avg. | M Avg | m Avg | hrs | min | hrs | min | hrs | min | hrs | min | Avg Int Avi | Avg Ext Avi | MWhr Total | MWhr Total | MWhr Total | MWhr Total | MWhr Total | MW Avg | Total min | Avg MW | Total min | Avg MW | Total min | MWhr | Total MW | Av Max D/Gen | Av. DailyLF | Avg. | Avg. |  | Avg. | Total | Avg. |  | Total | Avg. |  | Avg. | [7 empty] | Total |  |  |  |  | Avg. | [18 empty] | 425.271
| Weeks data | Site Avg. Amb. Temp F | Site Avg. Relative humidity % | Max: Site Maximum/Minumum Temperature; CT1 hrs: CT-1 Base Load Hours; CT2 hrs: CT-2 Base Load Hours; CT1 hrs: CT-1 stand by hours / min; CT2 hrs: CT-2 standby hours / min; CT2 hrs: Plant ambient Corrected maximum Load hours/min | Average Corrected Plant Capacity | Ambient Corrected Declared Avail'y (MWH) | Av Plant WAPDA Dispatch | Net Plant Export (MWH) | Gross Generation | CT1 Av Cap (MW) | CT1 Unavail minutes | CT2 Av Cap (MW) | CT2 Unavail minutes | ST Unavail minutes | ST Average Cap (MW) | Plant Aux Load including Colony Load MWH | Differenece (+/-) MW | Maximum Daily Generation | Daily Load Factor | Avg. Corrected Plant | Plant Capacity Facto | Plant Availability Factor | Equivalent Plant Availability | LBtu gas flow mmscf | 1 LBtu gas (Average Btu/scf) | LBTU MMBTU | PL gas flow (mscf/week) | 1 PL gas (Average Btu/scf) | HBTU MMBTU | Plant Net Heat Rate (Btu/Kwh) | [11 empty] | 20
| Week 18 | 90.4 | 37.71% | 103.1429 | 77.8571 | 168 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 3493.5714 | 3177.8571 | 3177.8571 | 3120.1429 | 3226.5714 | 42.1429 | No outage | 42.7143 | No outage | 420 | no data | no data | -404 | 142 | 94.71% | 145.5655 | 89.32% | 100% | 93.79% | 60.252 | 147.7357 | 8901.3723 | 192.147 | 944.4286 | 181469.1167 | 8714.986
| Week 19 | 95.0557 | 39.5% | 107.2857 | 82.5714 | 165 | 51 | 166 | 19 | 0 | 0 | 0 | -60 | 63 | 0 | 3445.8571 | 3111.9286 | 3111.9286 | 21104 | 21843 | 41.4286 | 110 | 294 | no data | 422 | no data | 741 | -679.5 | 139 | 93.57% | 143.5774 | 87.48% | 98.96% | 91.69% | 59.795 | 146.6057 | 8766.2887 | 186.135 | 943.5714 | 175631.6679 | 8737.6582 | [5 empty] | 0.27381
| Week 20 | 95.0686 | 42.02% | 106 | 83.1429 | 166 | 22 | 166 | 47 | 0 | 0 | 0 | 0 | 72 | 0 | 3446.2857 | 3132.5714 | 3132.5714 | 21237 | 21982 | 41.2857 | 98 | 293 | 10.4286 | 420 | 15.7143 | 745 | -691 | 139.7143 | 93.61% | 143.5952 | 88.02% | 99.05% | 92.49% | 59.579 | 146.5143 | 8729.1746 | 160.799 | 942.5 | 151553.0575 | 8766.1721 | [5 empty] | 0.26672
| Week 21 | 96.33 | 41.72% | 107.1429 | 84.7143 | 168 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3433.4286 | 3007.1429 | 3007.1429 | 20577 | 21292 | 40.7143 | No outage | 292 | no data | 420 | no data | 715 | -473 | 131.5714 | 96.38% | 143.0595 | 85.64% | 100% | 89.33% | 59.84 | 145.3057 | 8695.0939 | 180.02 | 944.2857 | 169990.3143 | 8682.5271
| Week 22 | 95.85 | 0.45175 | 106 | 85 | 96 | 0 | 96 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 3439.5 | 2971.75 | 2971.75 | 11628 | 12041 | 40.75 | #REF! | #REF! | no data | #REF! | no data | 413 | -259 | 130.25 | 96.42% | 143.3125 | 84.5% | #DIV/0! | 88.37% | 34.158 | 142.355 | 4862.5621 | 101.501 | 946.25 | 96045.3213 | 8676.0014
| Date | Plant Status Whether Normal Operation or Tripping (State full detail for trippings/return to normal).
| 2017-05-01 | Plant load increased from 122 to 137 MW by taking duct burners into service at 1100 hrs to achieve maximum export. At 2300 hrs, plant load reduced from 141 to 128 MW by decreasing duct burners firing to keep within restricted plant heat rate.
| 2017-05-02 | Plant load increased from 124 to 136 MW by increasing duct firing at 1100 hrs to achieve maximum export. At 2300 hrs, plant load reduced from 137 to 125 MW by decreasing duct burners firing to keep within contractual plant heat rate.
| 2017-05-03 | Plant load increased from 124 to 136 MW by increasing duct firing at 1100 hrs to achieve maximum export. At 2300 hrs, plant load reduced from 141 to 127 MW by decreasing duct burners firing to keep within contractual plant heat rate.
| 2017-05-04 | Plant load increased from 124 to 136 MW by increasing duct firing at 1100 hrs to achieve maximum export. At 2300 hrs, plant load reduced from 141 to 127 MW by decreasing duct burners firing to keep within contractual plant heat rate.
| 2017-05-05 | Plant load increased from 122 to 136 MW by increasing duct firing at 1100 hrs to achieve maximum export. At 2300 hrs, plant load reduced from 138 to 126 MW by decreasing duct burners firing to keep within contractual plant heat rate.
| 2017-05-06 | Plant load increased from 122 to 136 MW by increasing duct firing at 1100 hrs to achieve maximum export. At 2300 hrs, plant load reduced from 136 to 123 MW by taking duct burners out of service to keep within contractual plant heat rate.
| 2017-05-07 | Plant load restricted to 117~124 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-05-08 | Plant load increased to maximum (134MW) at 1150hrs by taking DBs into service. Plant tripped at 1520 hrs due to WAPDA supply failure. After restoration of WAPDA supply at 1525hrs, CT-2 synch @ 1642hrs, CT-1 synch @ 1710hrs and STG synch @ 1717hrs.
| 2017-05-09 | Plant load increased from 121 to 134 MW by taking duct burners into service at 1100 hrs to achieve maximum export. At 2300 hrs, plant load reduced from 136 to 124 MW by decreasing duct burners firing to keep within contractual plant heat rate.
| 2017-05-10 | Plant load increased from 120 to 132 MW by increasing duct firing at 1100 hrs to achieve maximum export. At 2300 hrs, plant load reduced from 138 to 126 MW by decreasing duct burners firing to keep within contractual plant heat rate.
| 2017-05-11 | Plant load increased from 121 to 133 MW by increasing duct firing at 1100 hrs to achieve maximum export. At 2300 hrs, plant load reduced from 136 to 126 MW by decreasing duct burners firing to keep within contractual plant heat rate.
| 2017-05-12 | Plant load increased from 121 to 133 MW by increasing duct firing at 1100 hrs to achieve maximum export. At 2300 hrs, plant load reduced from 137 to 127 MW by decreasing duct burners firing to keep within contractual plant heat rate.
| 2017-05-13 | Plant load increased from 121 to 133 MW by increasing duct firing at 1100 hrs to achieve maximum export. At 2300 hrs, plant load reduced from 136 to 124 MW by taking duct burners out of service to keep within contractual plant heat rate.
| 2017-05-14 | Plant tripped at 1440 hrs due to WAPDA supply failure. After restoration of WAPDA supply at 1504hrs, CT-2 synch @ 1553hrs, CT-1 synch @ 1618hrs and STG synch @ 1630hrs
| 2017-05-15 | Plant load increased from 119 to 133 MW by taking duct burners into service at 1100 hrs to achieve maximum export. At 2300 hrs, plant load reduced from 135 to 123 MW by decreasing duct burners firing to keep within contractual plant heat rate.
| 2017-05-16 | Plant load increased from 120 to 133 MW by increasing duct firing at 1100 hrs to achieve maximum export. At 2300 hrs, plant load reduced from 139 to 126 MW by decreasing duct burners firing to keep within contractual plant heat rate.
| 2017-05-17 | Plant load increased from 123 to 137 MW by increasing duct firing at 1100 hrs to achieve maximum export. At 2300 hrs, plant load reduced from 137 to 125 MW by decreasing duct burners firing to keep within contractual plant heat rate.
| 2017-05-18 | Plant load increased from 119 to 133 MW by increasing duct firing at 1100 hrs to achieve maximum export. At 2300 hrs, plant load reduced from 138 to 126 MW by decreasing duct burners firing to keep within contractual plant heat rate.
| 2017-05-19 | Plant load increased from 118 to 132 MW by increasing duct firing at 1100 hrs to achieve maximum export. At 2300 hrs, plant load reduced from 137 to 124 MW by decreasing duct burners firing to keep within contractual plant heat rate.
| 2017-05-20 | Plant load increased from 121 to 133 MW by increasing duct firing at 1100 hrs to achieve maximum export. At 2300 hrs, plant load reduced from 137 to 124 MW by taking duct burners out of service to keep within contractual plant heat rate.
| 2017-05-21 | Plant load restricted to 120~126 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-05-22 | Plant load restricted to 119~127 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-05-23 | Plant load restricted to 117~125 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-05-24 | Plant load restricted to 116~123 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-05-25 | Plant load restricted to 116~122 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-05-26 | Plant load increased from 117 to 133 MW by taking duct burners into service at 1100 hrs to achieve maximum export. At 2300 hrs, plant load reduced from 137 to 121 MW by decreasing duct burners firing to keep within contractual plant heat rate.
| 2017-05-27 | Plant load increased from 118 to 133 MW by increasing duct firing at 1100 hrs to achieve maximum export. At 2300 hrs, plant load reduced from 134 to 117 MW by taking duct burners out of service to keep within contractual plant heat rate.
| 2017-05-28 | Plant load restricted to 114~120 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-05-29 | Plant load restricted to 117~123 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-05-30 | Plant load restricted to 116~122 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-05-31 | Plant load increased from 117 to 133 MW by taking duct burners into service at 1100 hrs to achieve maximum export. At 2300 hrs, plant load reduced from 137 to 123 MW by decreasing duct burners firing to keep within contractual plant heat rate.
Note on BY28: ops.e: Remained off from 0927~1008 hrs for replacement of inlet cartridge filter.

## Jun
Monthly Operational Returns Kabirwala
2017-06-01
| Date | Site Avg. Ambient Temp.F | Site Avg. Relative Humidty % | Site Ambient Temp |  | Base load hours |  |  |  | Standby hours |  |  |  | Plant ambient corrected Max Load |  | Corrected Plant Capacity | Ambient Corrected Daclared Avail'y (MWH) | Plant WAPDA Dispatch (MWH) | Net Plant Export (MWH) | Gross Generation | CT1 Average Cap (MW) | CT1 Unavail minutes | CT2 Average Cap (MW) | CT2 Unavail minutes | ST Average Cap (MW) | ST Unavail minutes | Plant Aux Load including Colony Load MWH | Differenece (+/-) MW | Maximum Daily Generation | Daily Load Factor | Avg. Corrected Plant Capacity | Plant Capacity Factor | Plant Availability Factor | Equivalent Plant Availability | LBtu gas flow (mmscf/day) | 1 LBtu gas (Average Btu/scf) | LBTU MMBTU | 1 HBtu gas flow (mmscf/day) | 1 HBtu gas (Average Btu/scf) | HBTU MMBTU | HHV Net Heat Rate (Btu/Kwh) | Avg. declared availability | CT1 Derated MW | CT1 derated mintutes | CT-2 derated MW | CT-2 derated mintutes | ST derated MW | ST derated mintutes | WAPDA Backfeed (MWH) | CT-1 Gross Generation (MWH) | CT-2 Gross Generation (MWH) | STG Gross Generation (MWH) | CT-1 & CT-2 MWH difference | Base load Heat Rate | STG load | DB1 | DB2 | CT1 | CT1 Gas flow | CT2 Gas flow |  | Pamb | Freq. Hz | LBTU Gas Specific gravity | CT-1 compressor efficiency(%) | CT-2 compressor efficiency(%) | CT-1 Heat Rate (Btu/Kwh) | CT-2 Heat Rate (Btu/Kwh) |  | DB(1+2) | DB-1 Ops Hours | DB-2 Ops Hours | CT-1 Wetcomprssion Ops Hours | RO Operation Hours
[6 empty] | CT1 |  | CT2 |  | CT1 |  | CT2 | [43 empty] | mmscf/d | mmscf/d | WetC flow | HBTU KPPH | HBTU KPPH | LBTU KPPH | mbar | Hz | [6 empty] | mmscf/d
|  |  |  | Max | Min | hrs | min | hrs | min | hrs | min | hrs | min | hrs | min | [42 empty] | gpm
Week 22 | 2017-05-28 | 100.6 | 42.7% | 112 | 88 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3392 | 2884 | 2884 | 2818 | 2919 | 40 | 0 | 41 | 0 | 60 | 0 | 101 | -66 | 124 | 98.08% | 141.3333 | 83.08% | 100% | 86.52% | 8.525 | 144.77 | 1234.1643 | 24.441 | 949 | 23194.509 | 8668.7982 | 120.1667 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 957 | 976 | 986 | 19 | 8668.7982 | 41.0833 | 0 | 0 | 28 | 25.9 | 21.6 | 23.9 | 979 | 50.08 | 0.9316 | 92.2 | 85.8 | 12749 | 12689 | -60 | 0 | 0 | 0 | 24 | 7.52
| 2017-05-29 | 95 | 43.2% | 105 | 84 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3447 | 2943 | 2943 | 2876 | 2972 | 41 | 0 | 41 | 0 | 60 | 0 | 96 | -67 | 127 | 97.51% | 143.625 | 83.43% | 100% | 86.62% | 8.511 | 143.71 | 1223.1158 | 24.982 | 945 | 23607.99 | 8633.9033 | 122.625 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 976 | 997 | 999 | 21 | 8633.9033 | 41.625 | 0 | 0 | 28.64 | 26.47 | 22.18 | 24.03 | 981.1 | 50.1 | 0.9317 | 92.7 | 86.05 | 12702 | 12654 | -48 | 0 | 0 | 0 | 24 | 6.77
| 2017-05-30 | 95.7 | 46.8% | 108 | 84 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3440 | 2926 | 2926 | 2860 | 2964 | 41 | 0 | 41 | 0 | 60 | 0 | 104 | -66 | 127 | 97.24% | 143.3333 | 83.14% | 100% | 86.62% | 8.557 | 141.02 | 1206.7081 | 24.823 | 945 | 23457.735 | 8623.9312 | 121.9167 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 978 | 992 | 994 | 14 | 8623.9312 | 41.4167 | 0 | 0 | 28.57 | 26.35 | 22.03 | 23.95 | 979.5 | 50.09 | 0.9322 | 92.98 | 86.12 | 12706 | 12667 | -39 | 0 | 0 | 0 | 24 | 7.17
| 2017-05-31 | 92.1 | 48% | 99 | 84 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 3479 | 3134 | 3134 | 3074 | 3186 | 41 | 0 | 42 | 0 | 60 | 0 | 112 | -60 | 143 | 92.83% | 144.9583 | 88.36% | 100% | 93.71% | 8.565 | 139.92 | 1198.4148 | 27.255 | 946 | 25783.23 | 8777.3731 | 130.5833 | 0 | 0 | 0 | 0 | 18 | 720 | 0 | 993 | 1001 | 1192 | 8 | 8777.3731 | 49.6667 | 1.109 | 1.103 | 28.9 | 26.6 | 22.3 | 23.9 | 980.8 | 50.17 | 0.9325 | 93.46 | 86.38 | 12642 | 12640 | -2 | 2.212 | 13 | 13 | 24 | 7.33
| 2017-06-01 | 92.03 | 46.47% | 101 | 81 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 3477 | 3179 | 3179 | 3113 | 3220 | 40 | 0 | 42 | 0 | 60 | 0 | 107 | -66 | 142 | 94.48% | 144.875 | 89.53% | 100% | 94.37% | 8.58 | 144.05 | 1235.949 | 27.739 | 943 | 26157.877 | 8799.8156 | 132.4583 | 0 | 0 | 0 | 0 | 16 | 720 | 0 | 993 | 1005 | 1222 | 12 | 8799.8156 | 50.9167 | 1.259 | 1.211 | 28.96 | 26.81 | 22.46 | 23.96 | 985.13 | 50.12 | 0.931 | 93.26 | 86.22 | 12690 | 12668 | -22 | 2.47 | 23 | 23 | 24 | 7.8
| 2017-06-02 | 99.15 | 39.7% | 111 | 86 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 3402 | 3125 | 3125 | 3050 | 3161 | 40 | 0 | 41 | 0 | 60 | 0 | 111 | -75 | 140 | 94.08% | 141.75 | 89.65% | 100% | 93.62% | 8.55 | 144.64 | 1236.672 | 27.197 | 945 | 25701.165 | 8832.0777 | 130.2083 | 0 | 0 | 0 | 0 | 18 | 720 | 0 | 966 | 993 | 1202 | 27 | 8832.0777 | 50.0833 | 1.149 | 1.143 | 28.19 | 26.26 | 22.19 | 23.71 | 983.75 | 50.12 | 0.9316 | 91.83 | 85.88 | 12794 | 12700 | -94 | 2.292 | 13 | 13 | 24 | 7.56
| 2017-06-03 | 101.9 | 41.9% | 114 | 91 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 3376 | 3104 | 3104 | 3033 | 3141 | 40 | 0 | 41 | 0 | 60 | 0 | 108 | -71 | 140 | 93.48% | 140.6667 | 89.84% | 100% | 93.97% | 8.57 | 146.95 | 1259.3615 | 26.903 | 946 | 25450.238 | 8806.3302 | 129.3333 | 0 | 0 | 0 | 0 | 17 | 720 | 0 | 948 | 982 | 1211 | 34 | 8806.3302 | 50.4583 | 1.301 | 1.208 | 27.88 | 25.87 | 22 | 23.69 | 981.63 | 50.08 | 0.9314 | 91.32 | 85.72 | 12832 | 12715 | -117 | 2.509 | 23 | 23 | 24 | 7.016
Week 23 | 2017-06-04 | 100 | 43% | 110 | 90 | 24 | 0 | 12 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 3391 | 2186 | 2186 | 2136 | 2229 | 40 | 0 | 41 | 625 | 60 | 0 | 93 | -50 | 123 | 75.51% | 141.2917 | 62.99% | 87.38% | 66.34% | 4.645 | 149.69 | 695.31 | 19.827 | 945 | 18736.515 | 9097.2964 | 91.0833 | 0 | 0 | 18 | 53 | 29 | 1440 | 0 | 947 | 542 | 740 | -405 | 9097.2964 | 30.8333 | 0 | 0 | 28.1 | 25.8 | 12.5 | 13.1 | 978.9 | 50.05 | 0.9302 | 90.6 | 85.8 | 12836 | 12682 | -154 | 0 | 0 | 0 | 24 | 8.4
| 2017-06-05 | 100 | 53% | 108 | 92 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 3394 | 3066 | 3066 | 3002 | 3112 | 40 | 0 | 41 | 0 | 60 | 0 | 110 | -64 | 138 | 93.96% | 141.4167 | 88.45% | 100% | 93.26% | 8.55 | 145.34 | 1242.657 | 26.602 | 944 | 25112.288 | 8779.1289 | 127.75 | 0 | 0 | 0 | 0 | 19 | 720 | 0 | 947 | 980 | 1185 | 33 | 8779.1289 | 49.375 | 1.162 | 1.162 | 28.1 | 25.9 | 21.9 | 23.8 | 979.2 | 50.06 | 0.9314 | 92.6 | 86.35 | 12859 | 12722 | -137 | 2.324 | 12 | 12 | 24 | 7.3
| 2017-06-06 | 97.8 | 55% | 105 | 91 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 3417 | 3071 | 3071 | 3009 | 3122 | 40 | 0 | 41 | 0 | 60 | 0 | 113 | -62 | 138 | 94.26% | 142.375 | 88.06% | 100% | 93.26% | 8.56 | 147.53 | 1262.8568 | 26.665 | 943 | 25145.095 | 8776.3216 | 127.9583 | 0 | 0 | 0 | 0 | 19 | 720 | 0 | 960 | 984 | 1178 | 24 | 8776.3216 | 49.0833 | 1.139 | 1.137 | 28.3 | 26.2 | 21.9 | 23.8 | 980.4 | 50.08 | 0.9306 | 93.8 | 86.54 | 12828 | 12705 | -123 | 2.276 | 12 | 12 | 24 | 7
| 2017-06-07 | 91 | 56.7% | 100 | 80 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 3495 | 3142 | 3142 | 3077 | 3187 | 41 | 0 | 42 | 0 | 60 | 0 | 110 | -65 | 140 | 94.85% | 145.625 | 88.04% | 100% | 93.71% | 8.53 | 142.55 | 1215.9515 | 27.305 | 945 | 25803.225 | 8781.0128 | 130.9167 | 0 | 0 | 0 | 0 | 18 | 720 | 0 | 991 | 1004 | 1192 | 13 | 8781.0128 | 49.6667 | 1.116 | 1.116 | 29.1 | 26.7 | 22.3 | 23.8 | 985.75 | 50.11 | 0.9318 | 94.7 | 86.7 | 12698 | 12616 | -82 | 2.232 | 12 | 12 | 24 | 7.33
| 2017-06-08 | 90.9 | 58% | 99 | 85 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3494 | 2961 | 2961 | 2896 | 2998 | 41 | 0 | 42 | 0 | 60 | 0 | 102 | -65 | 130 | 96.09% | 145.5833 | 82.88% | 100% | 87.41% | 8.47 | 138.21 | 1170.6387 | 25.399 | 944 | 23976.656 | 8683.4581 | 123.375 | 0 | 0 | 0 | 0 | 18 | 1440 | 0 | 991 | 1008 | 999 | 17 | 8683.4581 | 41.625 | 0 | 0 | 29.1 | 26.8 | 22.3 | 23.8 | 984.8 | 50.15 | 0.9327 | 94.8 | 86.8 | 12711 | 12583 | -128 | 0 | 0 | 0 | 24 | 7.7
| 2017-06-09 | 90.8 | 48.1% | 102 | 79 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3491 | 2988 | 2988 | 2925 | 3025 | 41 | 0 | 42 | 0 | 60 | 0 | 100 | -63 | 131 | 96.22% | 145.4583 | 83.79% | 100% | 87.41% | 8.35 | 139.91 | 1168.2485 | 25.371 | 948 | 24051.708 | 8622.2074 | 124.5 | 0 | 0 | 0 | 0 | 18 | 1440 | 0 | 996 | 1018 | 1011 | 22 | 8622.2074 | 42.125 | 0 | 0 | 29.1 | 26.8 | 22.6 | 23.8 | 984.6 | 50.09 | 0.9327 | 93.6 | 86.5 | 12676 | 12537 | -139 | 0 | 0 | 0 | 24 | 7.42
| 2017-06-10 | 91.6 | 54.8% | 108 | 75 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3482 | 2968 | 2968 | 2901 | 3000 | 41 | 0 | 42 | 0 | 60 | 0 | 99 | -67 | 131 | 95.42% | 145.0833 | 83.31% | 100% | 87.41% | 8.33 | 139.19 | 1159.4527 | 25.441 | 944 | 24016.304 | 8678.3029 | 123.6667 | 0 | 0 | 0 | 0 | 18 | 1440 | 0 | 990 | 1009 | 1001 | 19 | 8678.3029 | 41.7083 | 0 | 0 | 29 | 26.75 | 22.47 | 23.72 | 983.67 | 50.12 | 0.9327 | 94.23 | 86.55 | 12720 | 12609 | -111 | 0 | 0 | 0 | 24 | 6.83
Week 24 | 2017-06-11 | 85.1 | 65.2% | 96 | 75 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3541 | 3012 | 3012 | 2943 | 3041 | 42 | 0 | 42 | 0 | 60 | 0 | 98 | -69 | 130 | 97.47% | 147.5417 | 83.11% | 100% | 87.5% | 8.305 | 139.48 | 1158.3814 | 25.679 | 945 | 24266.655 | 8639.1561 | 125.5 | 0 | 0 | 0 | 0 | 18 | 1440 | 0 | 1014 | 1017 | 1010 | 3 | 8639.1561 | 42.0833 | 0 | 0 | 29.73 | 27.27 | 22.64 | 23.99 | 984.71 | 50.12 | 0.9323 | 95.63 | 86.91 | 12644 | 12566 | -78 | 0 | 0 | 0 | 24 | 7.42
| 2017-06-12 | 93.7 | 52.2% | 104 | 83 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3458 | 2942 | 2942 | 2874 | 2980 | 41 | 0 | 42 | 0 | 60 | 0 | 106 | -68 | 128 | 97.01% | 144.0833 | 83.11% | 100% | 86.71% | 8.3 | 138.65 | 1150.795 | 25.079 | 945 | 23699.655 | 8646.6423 | 122.5833 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 979 | 1004 | 997 | 25 | 8646.6423 | 41.5417 | 0 | 0 | 28.8 | 26.58 | 22.29 | 23.87 | 981.96 | 50.1 | 0.9328 | 93.88 | 86.58 | 12779 | 12633 | -146 | 0 | 0 | 0 | 24 | 6
| 2017-06-13 | 97.69 | 47.42% | 107 | 88 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3421 | 2912 | 2912 | 2841 | 2946 | 40 | 0 | 41 | 0 | 60 | 0 | 105 | -71 | 125 | 98.2% | 142.5417 | 83.05% | 100% | 86.52% | 8.314 | 142.93 | 1188.32 | 24.804 | 944 | 23414.976 | 8660.0831 | 121.3333 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 963 | 992 | 991 | 29 | 8660.0831 | 41.2917 | 0 | 0 | 28.3 | 26.27 | 22.08 | 23.77 | 980.58 | 50.12 | 0.9315 | 93.41 | 86.47 | 12835 | 12645 | -190 | 0 | 0 | 0 | 24 | 6.33
| 2017-06-14 | 95.01 | 50.91% | 108 | 89 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3451 | 2929 | 2929 | 2864 | 2968 | 41 | 0 | 42 | 0 | 60 | 0 | 104 | -65 | 129 | 95.87% | 143.7917 | 82.99% | 100% | 86.71% | 8.309 | 141.29 | 1173.9786 | 25.056 | 943 | 23627.808 | 8659.8417 | 122.0417 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 974 | 1000 | 994 | 26 | 8659.8417 | 41.4167 | 0 | 0 | 28.49 | 26.49 | 22.23 | 23.67 | 982.42 | 50.14 | 0.932 | 94.12 | 86.59 | 12791 | 12619 | -172 | 0 | 0 | 0 | 24 | 6.92
| 2017-06-15 | 95.44 | 53.5% | 106 | 83 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3441 | 2924 | 2924 | 2855 | 2959 | 41 | 0 | 42 | 0 | 60 | 0 | 104 | -69 | 129 | 95.57% | 143.375 | 82.97% | 100% | 86.71% | 8.304 | 140.28 | 1164.8851 | 24.999 | 943 | 23574.057 | 8665.1286 | 121.8333 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 972 | 995 | 992 | 23 | 8665.1286 | 41.3333 | 0 | 0 | 28.59 | 26.47 | 22.16 | 23.66 | 981.88 | 50.11 | 0.9323 | 94.15 | 86.55 | 12813 | 12638 | -175 | 0 | 0 | 0 | 24 | 7.316
| 2017-06-16 | 97 | 58% | 105 | 86 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3432 | 2879 | 2879 | 2814 | 2917 | 40 | 0 | 41 | 0 | 60 | 0 | 103 | -65 | 124 | 98.02% | 143 | 81.99% | 100% | 86.52% | 8.308 | 140.82 | 1169.9326 | 24.698 | 943 | 23290.214 | 8692.3051 | 119.9583 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 962 | 977 | 978 | 15 | 8692.3051 | 40.75 | 0 | 0 | 28.43 | 26.3 | 21.8 | 23.6 | 979.7 | 50.1 | 0.9323 | 95.06 | 86.7 | 12843 | 12704 | -139 | 0 | 0 | 0 | 24 | 7.5
| 2017-06-17 | 94.8 | 60.4% | 101 | 89 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3449 | 2894 | 2894 | 2830 | 2933 | 40 | 0 | 41 | 0 | 60 | 0 | 103 | -64 | 125 | 97.77% | 143.7083 | 82.05% | 100% | 86.52% | 8.302 | 139.01 | 1154.061 | 24.845 | 943 | 23428.835 | 8686.5357 | 120.5833 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 969 | 983 | 981 | 14 | 8686.5357 | 40.875 | 0 | 0 | 28.6 | 26.4 | 21.9 | 23.7 | 980.88 | 50.14 | 0.9328 | 95.54 | 86.82 | 12810 | 12684 | -126 | 0 | 0 | 0 | 24 | 7.36
Week 25 | 2017-06-18 | 96 | 57% | 106 | 84 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3440 | 2898 | 2898 | 2836 | 2937 | 40 | 0 | 41 | 0 | 60 | 0 | 101 | -62 | 126 | 97.12% | 143.3333 | 82.44% | 100% | 86.52% | 8.305 | 139.2 | 1156.056 | 24.886 | 943 | 23467.498 | 8682.4944 | 120.75 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 967 | 985 | 985 | 18 | 8682.4944 | 41.0417 | 0 | 0 | 28.75 | 26.4 | 21.97 | 23.7 | 980.5 | 50.09 | 0.9328 | 94.85 | 86.64 | 12830 | 12685 | -145 | 0 | 0 | 0 | 24 | 7.26
| 2017-06-19 | 95.2 | 56.4% | 104 | 88 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3451 | 2905 | 2905 | 2832 | 2936 | 40 | 0 | 41 | 0 | 60 | 0 | 104 | -73 | 126 | 97.09% | 143.7917 | 82.06% | 100% | 86.52% | 8.31 | 138.1 | 1147.611 | 24.869 | 944 | 23476.336 | 8694.8965 | 121.0417 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 964 | 988 | 984 | 24 | 8694.8965 | 41 | 0 | 0 | 28.6 | 26.3 | 22 | 23.8 | 978.1 | 50.11 | 0.933 | 94.5 | 86.6 | 12815.1 | 12667 | -148.1 | 0 | 0 | 0 | 24 | 7.75
| 2017-06-20 | 87.6 | 68% | 101 | 72 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3523 | 2961 | 2961 | 2898 | 2997 | 41 | 0 | 42 | 0 | 60 | 0 | 99 | -63 | 130 | 96.06% | 146.7917 | 82.26% | 100% | 87.41% | 8.15 | 139.9 | 1140.185 | 25.338 | 946 | 23969.748 | 8664.5732 | 123.375 | 0 | 0 | 0 | 0 | 18 | 1440 | 0 | 995 | 1005 | 997 | 10 | 8664.5732 | 41.5417 | 0 | 0 | 29.5 | 26.8 | 22.2 | 23.9 | 980.2 | 50.1 | 0.9321 | 95.6 | 86.8 | 12673 | 12571 | -102 | 0 | 0 | 0 | 24 | 7.63
| 2017-06-21 | 83.3 | 72.6% | 89 | 75 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3516 | 3007 | 3007 | 2938 | 3039 | 41 | 0 | 42 | 0 | 60 | 0 | 101 | -69 | 130 | 97.4% | 146.5 | 83.56% | 100% | 87.41% | 8.11 | 139.48 | 1131.1828 | 25.519 | 948 | 24192.012 | 8619.195 | 125.2917 | 0 | 0 | 0 | 0 | 18 | 1440 | 0 | 1016 | 1014 | 1009 | -2 | 8619.195 | 42.0417 | 0 | 0 | 29.9 | 27.3 | 22.4 | 24 | 982.6 | 50.11 | 0.9323 | 96.4 | 86.9 | 12633 | 12555 | -78 | 0 | 0 | 0 | 24 | 7.15
| 2017-06-22 | 87 | 70.1% | 93 | 81 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3529 | 2960 | 2960 | 2897 | 2997 | 42 | 0 | 41 | 0 | 60 | 0 | 100 | -63 | 127 | 98.33% | 147.0417 | 82.09% | 100% | 86.71% | 8.015 | 140.61 | 1126.9892 | 25.455 | 943 | 24004.065 | 8674.8547 | 123.3333 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 1000 | 1001 | 996 | 1 | 8674.8547 | 41.5 | 0 | 0 | 29.52 | 26.98 | 22.25 | 24.05 | 983.54 | 50.1 | 0.932 | 96.35 | 87.01 | 12708 | 12623 | -85 | 0 | 0 | 0 | 24 | 5.03
| 2017-06-23 | 91.9 | 64.2% | 100 | 83 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3478 | 2927 | 2927 | 2859 | 2960 | 41 | 0 | 41 | 0 | 60 | 0 | 101 | -68 | 126 | 97.88% | 144.9167 | 82.2% | 100% | 86.62% | 8.005 | 140.14 | 1121.8207 | 25.089 | 944 | 23684.016 | 8676.4032 | 121.9583 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 980 | 989 | 991 | 9 | 8676.4032 | 41.2917 | 0 | 0 | 28.97 | 26.63 | 22.08 | 23.77 | 983.1 | 50.09 | 0.9326 | 95.65 | 86.87 | 12786 | 12672 | -114 | 0 | 0 | 0 | 24 | 3.58
| 2017-06-24 | 94.5 | 59.6% | 103 | 85 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3452 | 2904 | 2904 | 2836 | 2938 | 40 | 0 | 41 | 0 | 60 | 0 | 102 | -68 | 125 | 97.93% | 143.8333 | 82.16% | 100% | 86.52% | 8.01 | 142.43 | 1140.8643 | 24.942 | 942 | 23495.364 | 8686.9634 | 121 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 968 | 985 | 985 | 17 | 8686.9634 | 41.0417 | 0 | 0 | 28.69 | 26.45 | 21.99 | 23.73 | 980.17 | 50.11 | 0.9319 | 95.11 | 86.71 | 12842 | 12715 | -127 | 0 | 0 | 0 | 24 | 3.08
Week 26 | 2017-06-25 | 97.03 | 56.21% | 106 | 86 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3430 | 2885 | 2885 | 2817 | 2916 | 40 | 0 | 41 | 0 | 60 | 0 | 99 | -68 | 125 | 97.2% | 142.9167 | 82.13% | 100% | 86.52% | 8 | 143.96 | 1151.68 | 24.741 | 945 | 23380.245 | 8708.5286 | 120.2083 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 959 | 975 | 982 | 16 | 8708.5286 | 40.9167 | 0 | 0 | 28.41 | 26.21 | 21.87 | 23.5 | 979.54 | 50.05 | 0.9314 | 94.65 | 86.63 | 12840 | 12738 | -102 | 0 | 0 | 0 | 24 | 0
| 2017-06-26 | 98.89 | 55.74% | 109 | 90 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 3405 | 3071 | 3071 | 2998 | 3106 | 40 | 0 | 40 | 0 | 60 | 0 | 108 | -73 | 140 | 92.44% | 141.875 | 88.05% | 100% | 93.21% | 8.152 | 143.8 | 1172.2576 | 26.83 | 943.5513 | 25315.4819 | 8835.1366 | 127.9583 | 0 | 0 | 0 | 0 | 19 | 720 | 0 | 953 | 970 | 1183 | 17 | 8835.1366 | 49.2917 | 1.2 | 1.196 | 28.19 | 26.09 | 21.8 | 23.76 | 980.25 | 50.09 | 0.9308 | 94.67 | 86.68 | 12894 | 12798 | -96 | 2.396 | 13 | 13 | 24 | 5.766
| 2017-06-27 | 95.43 | 60.94% | 100 | 90 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 3442 | 3103 | 3103 | 3030 | 3137 | 40 | 0 | 41 | 0 | 60 | 0 | 107 | -73 | 138 | 94.72% | 143.4167 | 88.03% | 100% | 93.97% | 8.009 | 140.82 | 1127.8274 | 27.159 | 944 | 25638.096 | 8833.6381 | 129.2917 | 0 | 0 | 0 | 0 | 17 | 720 | 0 | 960 | 975 | 1202 | 15 | 8833.6381 | 50.0833 | 1.32 | 1.238 | 28.57 | 26.28 | 21.92 | 23.71 | 980.25 | 50.15 | 0.9328 | 95.38 | 86.85 | 12855 | 12773 | -82 | 2.558 | 24 | 24 | 24 | 0
| 2017-06-28 | 84.5 | 78.9% | 92 | 78 | 23 | 39 | 24 | 0 | 0 | 0 | 0 | 0 | 11 | 3 | 3555 | 3163 | 3119 | 3091 | 3197 | 42 | 0 | 41 | 0 | 60 | 0 | 106 | -28 | 142 | 93.81% | 148.125 | 86.95% | 100% | 93.46% | 7.956 | 138.53 | 1102.1447 | 27.631 | 944 | 26083.664 | 8795.15 | 131.7917 | 12 | 21 | 0 | 0 | 17 | 777 | 0 | 997 | 1001 | 1199 | 4 | 8795.15 | 49.9583 | 1.131 | 1.171 | 28.25 | 26.98 | 22.38 | 23.9 | 983.71 | 50.15 | 0.9326 | 96.29 | 87.09 | 12750 | 12678 | -72 | 2.302 | 23.25 | 24 | 24 | 0
| 2017-06-29 | 87 | 74% | 95 | 80 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 3530 | 3141 | 3141 | 3080 | 3186 | 41 | 0 | 41 | 0 | 60 | 0 | 106 | -61 | 140 | 94.82% | 147.0833 | 87.25% | 100% | 94.01% | 8.006 | 140.04 | 1121.1602 | 27.519 | 942 | 25922.898 | 8780.5384 | 130.875 | 0 | 0 | 0 | 0 | 17 | 720 | 0 | 994 | 994 | 1198 | 0 | 8780.5384 | 49.9167 | 1.177 | 1.152 | 29.5 | 26.99 | 22.2 | 23.8 | 982.8 | 50.16 | 0.9323 | 96.4 | 87.1 | 12764 | 12696 | -68 | 2.329 | 23 | 23 | 24 | 0
| 2017-06-30 | 87 | 74% | 93 | 80 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3526 | 2949 | 2949 | 2877 | 2974 | 41 | 0 | 41 | 0 | 60 | 0 | 97 | -72 | 126 | 98.35% | 146.9167 | 81.59% | 100% | 86.62% | 8 | 139.19 | 1113.52 | 25.095 | 943 | 23664.585 | 8612.48 | 122.875 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 991 | 993 | 990 | 2 | 8612.48 | 41.25 | 0 | 0 | 29.5 | 26.8 | 22.11 | 23.71 | 980.5 | 50.13 | 0.9327 | 96.42 | 87.1 | 12729 | 12634 | -95 | 0 | 0 | 0 | 24 | 9.5
| 2017-07-01 | [25 empty] | 0 | 0 |  | no data | no data | no data | #DIV/0! | no data |  |  | 0 |  |  | 0 | no data | 0 | [10 empty] | 0 | no data | 0 | [13 empty] | 0 | 0
| Monthly | 93.309 | 57.73% | 102.5333 | 83.8333 | 719 | 39 | 708 | 42 | 0 | 0 | 0 | 0 | 59 | 3 | 103889 | 89156 | 89112 | 87321.91 | 90259 | 40.6 | 0 | 41.3333 | 625 | 60 | 0 | 2937.09 | -1960 | 131.4667 | 95.38% | 144.2903 | 84.05% | 99.58% | 88.45% | 244.305 | 141.5573 | 34560.7503 | 768.682 | 944.1517 | 725747.2799 | 8706.956 | 123.8278 | 12 | 21 | 18 | 53 | 561 | 36057 | 0 | 29306 | 29368 | 31585 | -62 | 8706.956 | 1316.0417 | 11.954 | 11.734 | 28.7707 | 26.5293 | 21.8297 | 23.4257 | 981.8407 | 50.1083 | 0.93205 | 94.4933 | 86.622 | 12775.9367 | 12661.0333 |  | 23.688 | 178.25 | 179 | 720 | 179.948
| Totals | Avg.F | % Avg. | M Avg | m Avg | hrs | min | hrs | min | hrs | min | hrs | min | Avg Int Avi | Avg Ext Avi | MWhr Total | MWhr Total | MWhr Total | MWhr Total | MWhr Total | MW Avg | Total min | Avg MW | Total min | Avg MW | Total min | MWhr | Total MW | Av Max D/Gen | Av. DailyLF | Avg. | Avg. |  | Avg. | Total | Avg. |  | Total | Avg. |  | Avg. | [7 empty] | Total
| Weeks data | Site Avg. Amb. Temp F | Site Avg. Relative humidity % | Max: Site Maximum/Minumum Temperature; CT1 hrs: CT-1 Base Load Hours; CT2 hrs: CT-2 Base Load Hours; CT1 hrs: CT-1 stand by hours / min; CT2 hrs: CT-2 standby hours / min; CT2 hrs: Plant ambient Corrected maximum Load hours/min | Average Corrected Plant Capacity | Ambient Corrected Declared Avail'y (MWH) | Av Plant WAPDA Dispatch | Net Plant Export (MWH) | Gross Generation | CT1 Av Cap (MW) | CT1 Unavail minutes | CT2 Av Cap (MW) | CT2 Unavail minutes | ST Unavail minutes | ST Average Cap (MW) | Plant Aux Load including Colony Load MWH | Differenece (+/-) MW | Maximum Daily Generation | Daily Load Factor | Avg. Corrected Plant | Plant Capacity Facto | Plant Availability Factor | Equivalent Plant Availability | LBtu gas flow mmscf | 1 LBtu gas (Average Btu/scf) | LBTU MMBTU | PL gas flow (mscf/week) | 1 PL gas (Average Btu/scf) | HBTU MMBTU | Plant Net Heat Rate (Btu/Kwh)
| Week 22 | 96.64 | 44.11% | 107.1429 | 85.4286 | 168 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 3430.4286 | 3042.1429 | 3042.1429 | 2974.8571 | 3080.4286 | 40.4286 | No outage | 41.2857 | No outage | 420 | no data | no data | -471 | 134.7143 | 95.39% | 142.9345 | 86.72% | 100% | 90.78% | 59.858 | 143.58 | 8594.4116 | 183.34 | 945.5714 | 173361.0657 | 8734.6042
| Week 23 | 94.5857 | 52.66% | 104.5714 | 84.5714 | 168 | -2 | 156 | 42 | 0 | 0 | 0 | 0 | 36 | 0 | 3452 | 2911.7143 | 2911.7143 | 19946 | 20673 | 40.5714 | No outage | 291 | 89.2857 | 420 | no data | 727 | -436 | 133 | 92.33% | 143.8333 | 82.5% | 98.2% | 86.97% | 55.435 | 143.2029 | 7938.4504 | 176.61 | 944.7143 | 166845.99 | 8773.9612
| Week 24 | 94.1057 | 55.38% | 103.8571 | 84.7143 | 168 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3456.1429 | 2927.4286 | 2927.4286 | 20021 | 20744 | 40.7143 | No outage | 291 | no data | 420 | no data | 723 | -471 | 127.1429 | 97.13% | 144.006 | 82.75% | 100% | 86.74% | 58.142 | 140.3514 | 8160.3128 | 150.315 | 943.8333 | 141872.3075 | 8664.2418
| Week 25 | 90.7857 | 63.99% | 99.4286 | 81.1429 | 168 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3484.1429 | 2937.4286 | 2937.4286 | 20096 | 20804 | 40.7143 | No outage | 289 | no data | 420 | no data | 708 | -466 | 127.1429 | 97.4% | 145.1726 | 82.4% | 100% | 86.82% | 56.905 | 139.98 | 7965.5619 | 176.098 | 944.2857 | 166286.8257 | 8671.3401
| Week 26 | 91.6417 | 0.66632 | 99.1667 | 84 | 143 | 39 | 144 | 0 | 0 | 0 | 0 | 0 | 47 | 3 | 3481.3333 | 3052 | 3044.6667 | 17893 | 18516 | 40.6667 | #REF! | #REF! | no data | #REF! | no data | 623 | -375 | 135.1667 | 95.22% | 145.0556 | 85.67% | #DIV/0! | 91.3% | 48.123 | 141.0567 | 6788.07 | 158.975 | 943.5919 | 150007.5202 | 8760.9119
| Date | Plant Status Whether Normal Operation or Tripping (State full detail for trippings/return to normal).
| 2017-06-01 | Plant load increased from 122 to 134 MW by increasing duct firing at 1100 hrs to achieve maximum export. At 2300 hrs, plant load reduced from 136 to 122 MW by taking duct burners out of service to keep within contractual plant heat rate.
| 2017-06-02 | Plant load increased from 118 to 131 MW by taking duct burners into service at 1100 hrs to achieve maximum export. At 2300 hrs, plant load reduced from 135 to 123 MW by decreasing duct burners firing to keep within contractual plant heat rate.
| 2017-06-03 | Plant load increased from 117 to 130 MW by increasing duct firing at 1100 hrs to achieve maximum export. At 2300 hrs, plant load reduced from 135 to 121 MW by taking duct burners out of service to keep within contractual plant heat rate.
| 2017-06-04 | Gas turbine CT-2 de-synch @ 0022hrs and again synch@ 1047hrs after compressor offline washing.
| 2017-06-05 | Plant load increased from 117 to 133 MW by taking DBs into service at 1100 hrs to achieve maximum export. At 2300 hrs, plant load reduced from 134 to 118 MW by taking duct burners out of service to keep within contractual plant heat rate.
| 2017-06-06 | Plant load increased from 118 to 133 MW by taking DBs into service at 1100 hrs to achieve maximum export. At 2300 hrs, plant load reduced from 133 to 118 MW by taking duct burners out of service to keep within contractual plant heat rate.
| 2017-06-07 | Plant load increased from 120 to 135 MW by taking DBs into service at 1100 hrs to achieve maximum export. At 2300 hrs, plant load reduced from 136 to 120 MW by taking duct burners out of service to keep within contractual plant heat rate.
| 2017-06-08 | Plant load restricted to 118~126 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-06-09 | Plant load restricted to 119~127 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-06-10 | Plant load restricted to 116~126 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-06-11 | Plant load restricted to 120~126 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-06-12 | Plant load restricted to 117~123 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-06-13 | Plant load restricted to 116~121 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-06-14 | Plant load restricted to 115~124 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-06-15 | Plant load restricted to 115~124 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-06-16 | Plant load restricted to 115~120 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-06-17 | Plant load restricted to 115~121 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-06-18 | Plant load restricted to 115~122 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-06-19 | Plant load restricted to 115~121 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-06-20 | Plant load restricted to 116~126 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-06-21 | Plant load restricted to 120~126 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-06-22 | Plant load restricted to 119~123 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-06-23 | Plant load restricted to 117~122 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-06-24 | Plant load restricted to 116~120 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-06-25 | Plant load restricted to 115~120 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-06-26 | Plant load increased from 117 to 131 MW by taking duct burners into service at 1100 hrs to achieve maximum export. At 2300 hrs, plant load reduced from 135 to 121 MW by decreasing duct burners firing to keep within contractual plant heat rate.
| 2017-06-27 | Plant load increased from 119 to 132 MW by increasing duct firing at 1100 hrs to achieve maximum export. At 2300 hrs, plant load reduced from 133 to 120 MW by decreasing duct burners firing to keep within contractual plant heat rate.
| 2017-06-28 | Plant load increased from 125 to 138 MW at 1100 hrs to achieve maximum export. At 2300 hrs, plant load reduced from 137 to 124 MW to keep within contractual plant heat rate. Wapda Load despatch of 97 MW received from 1923 hrs to 2020 hrs.
| 2017-06-29 | Plant load increased from 122 to 134 MW by increasing duct firing at 1100 hrs to achieve maximum export. At 2300 hrs, plant load reduced from 135 to 121 MW by taking duct burners out of service to keep within contractual plant heat rate.
| 2017-06-30 | Plant load restricted to 118~122 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.

## Jul
Monthly Operational Returns Kabirwala
2017-07-01
| Date | Site Avg. Ambient Temp.F | Site Avg. Relative Humidty % | Site Ambient Temp |  | Base load hours |  |  |  | Standby hours |  |  |  | Plant ambient corrected Max Load |  | Corrected Plant Capacity | Ambient Corrected Daclared Avail'y (MWH) | Plant WAPDA Dispatch (MWH) | Net Plant Export (MWH) | Gross Generation | CT1 Average Cap (MW) | CT1 Unavail minutes | CT2 Average Cap (MW) | CT2 Unavail minutes | ST Average Cap (MW) | ST Unavail minutes | Plant Aux Load including Colony Load MWH | Differenece (+/-) MW | Maximum Daily Generation | Daily Load Factor | Avg. Corrected Plant Capacity | Plant Capacity Factor | Plant Availability Factor | Equivalent Plant Availability | LBtu gas flow (mmscf/day) | 1 LBtu gas (Average Btu/scf) | LBTU MMBTU | 1 HBtu gas flow (mmscf/day) | 1 HBtu gas (Average Btu/scf) | HBTU MMBTU | HHV Net Heat Rate (Btu/Kwh) | Avg. declared availability | CT1 Derated MW | CT1 derated mintutes | CT-2 derated MW | CT-2 derated mintutes | ST derated MW | ST derated mintutes | WAPDA Backfeed (MWH) | CT-1 Gross Generation (MWH) | CT-2 Gross Generation (MWH) | STG Gross Generation (MWH) | CT-1 & CT-2 MWH difference | Base load Heat Rate | STG load | DB1 | DB2 | CT1 | CT1 Gas flow | CT2 Gas flow |  | Pamb | Freq. Hz | LBTU Gas Specific gravity | CT-1 compressor efficiency(%) | CT-2 compressor efficiency(%) |  | CT-1 Heat Rate (Btu/Kwh) | CT-2 Heat Rate (Btu/Kwh) |  | DB(1+2) | DB-1 Ops Hours | DB-2 Ops Hours | CT-1 Wetcomprssion Ops Hours | RO Operation Hours
[6 empty] | CT1 |  | CT2 |  | CT1 |  | CT2 | [43 empty] | mmscf/d | mmscf/d | WetC flow | HBTU KPPH | HBTU KPPH | LBTU KPPH | mbar | Hz | [7 empty] | mmscf/d
|  |  |  | Max | Min | hrs | min | hrs | min | hrs | min | hrs | min | hrs | min | [42 empty] | gpm
Week 26 | 2017-06-25 | 97.03 | 56.21% | 106 | 86 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3430 | 2885 | 2885 | 2817 | 2916 | 40 | 0 | 41 | 0 | 60 | 0 | 99 | -68 | 125 | 97.2% | 142.9167 | 82.13% | 100% | 86.52% | 8 | 143.96 | 1151.68 | 24.741 | 945 | 23380.245 | 8708.5286 | 120.2083 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 959 | 975 | 982 | 16 | 8708.5286 | 40.9167 | 0 | 0 | 28.41 | 26.21 | 21.87 | 23.5 | 979.54 | 50.05 | 0.9314 | 94.65 | 86.63 | 12840 | 12840 | 12738 | -102 | 0 | 0 | 0 | 24 | 0
| 2017-06-26 | 98.89 | 55.74% | 109 | 90 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 3405 | 3071 | 3071 | 2998 | 3106 | 40 | 0 | 40 | 0 | 60 | 0 | 108 | -73 | 140 | 92.44% | 141.875 | 88.05% | 100% | 93.21% | 8.152 | 143.8 | 1172.2576 | 26.83 | 943.5513 | 25315.4819 | 8835.1366 | 127.9583 | 0 | 0 | 0 | 0 | 19 | 720 | 0 | 953 | 970 | 1183 | 17 | 8835.1366 | 49.2917 | 1.2 | 1.196 | 28.19 | 26.09 | 21.8 | 23.76 | 980.25 | 50.09 | 0.9308 | 94.67 | 86.68 | 12894 | 12894 | 12798 | -96 | 2.396 | 13 | 13 | 24 | 5.766
| 2017-06-27 | 95.43 | 60.94% | 100 | 90 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 3442 | 3103 | 3103 | 3030 | 3137 | 40 | 0 | 41 | 0 | 60 | 0 | 107 | -73 | 138 | 94.72% | 143.4167 | 88.03% | 100% | 93.97% | 8.009 | 140.82 | 1127.8274 | 27.159 | 944 | 25638.096 | 8833.6381 | 129.2917 | 0 | 0 | 0 | 0 | 17 | 720 | 0 | 960 | 975 | 1202 | 15 | 8833.6381 | 50.0833 | 1.32 | 1.238 | 28.57 | 26.28 | 21.92 | 23.71 | 980.25 | 50.15 | 0.9328 | 95.38 | 86.85 | 12855 | 12855 | 12773 | -82 | 2.558 | 24 | 24 | 24 | 0
| 2017-06-28 | 84.5 | 78.9% | 92 | 78 | 23 | 39 | 24 | 0 | 0 | 0 | 0 | 0 | 11 | 3 | 3555 | 3163 | 3119 | 3091 | 3197 | 42 | 0 | 41 | 0 | 60 | 0 | 106 | -28 | 142 | 93.81% | 148.125 | 86.95% | 100% | 93.46% | 7.956 | 138.53 | 1102.1447 | 27.631 | 944 | 26083.664 | 8795.15 | 131.7917 | 12 | 21 | 0 | 0 | 17 | 777 | 0 | 997 | 1001 | 1199 | 4 | 8795.15 | 49.9583 | 1.131 | 1.171 | 28.25 | 26.98 | 22.38 | 23.9 | 983.71 | 50.15 | 0.9326 | 96.29 | 87.09 | 12750 | 12750 | 12678 | -72 | 2.302 | 23.25 | 24 | 24 | 0
| 2017-06-29 | 87 | 74% | 95 | 80 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 3530 | 3141 | 3141 | 3080 | 3186 | 41 | 0 | 41 | 0 | 60 | 0 | 106 | -61 | 140 | 94.82% | 147.0833 | 87.25% | 100% | 94.01% | 8.006 | 140.04 | 1121.1602 | 27.519 | 942 | 25922.898 | 8780.5384 | 130.875 | 0 | 0 | 0 | 0 | 17 | 720 | 0 | 994 | 994 | 1198 | 0 | 8780.5384 | 49.9167 | 1.177 | 1.152 | 29.5 | 26.99 | 22.2 | 23.8 | 982.8 | 50.16 | 0.9323 | 96.4 | 87.1 | 12764 | 12764 | 12696 | -68 | 2.329 | 23 | 23 | 24 | 0
| 2017-06-30 | 87 | 74% | 93 | 80 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3526 | 2949 | 2949 | 2877 | 2974 | 41 | 0 | 41 | 0 | 60 | 0 | 97 | -72 | 126 | 98.35% | 146.9167 | 81.59% | 100% | 86.62% | 8 | 139.19 | 1113.52 | 25.095 | 943 | 23664.585 | 8612.48 | 122.875 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 991 | 993 | 990 | 2 | 8612.48 | 41.25 | 0 | 0 | 29.5 | 26.8 | 22.11 | 23.71 | 980.5 | 50.13 | 0.9327 | 96.42 | 87.1 | 12729 | 12729 | 12634 | -95 | 0 | 0 | 0 | 24 | 9.5
| 2017-07-01 | 92.6 | 67.2% | 99 | 84 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3465 | 2896 | 2896 | 2824 | 2925 | 40 | 0 | 41 | 0 | 60 | 0 | 101 | -72 | 125 | 97.5% | 144.375 | 81.5% | 100% | 86.52% | 8.064 | 139.94 | 1128.4762 | 24.891 | 945 | 23521.995 | 8728.9204 | 120.6667 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 963 | 981 | 981 | 18 | 8728.9204 | 40.875 | 0 | 0 | 28.8 | 26.3 | 21.9 | 23.8 | 979.7 | 50.11 | 0.933 | 95.2 | 87 | -8.2 | 12850 | 12739 | -111 | 0 | 0 | 0 | 24 | 0
Week 27 | 2017-07-02 | 95.4 | 63.4% | 103 | 86 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3446 | 2877 | 2877 | 2811 | 2911 | 40 | 0 | 41 | 0 | 60 | 0 | 100 | -66 | 124 | 97.82% | 143.5833 | 81.57% | 100% | 86.52% | 8.095 | 141.05 | 1141.7998 | 24.861 | 945 | 23493.645 | 8763.9433 | 119.875 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 962 | 971 | 977 | 9 | 8763.9433 | 40.7083 | 0 | 0 | 28.6 | 26.3 | 21.8 | 23.7 | 978.83 | 50.1 | 0.9322 | 95.5 | 86.8 | -8.7 | 12839 | 12755 | -84 | 0 | 0 | 0 | 24 | 0
| 2017-07-03 | 96.1 | 63.2% | 105 | 88 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 3439 | 3069 | 3069 | 2993 | 3103 | 40 | 0 | 40 | 0 | 60 | 0 | 110 | -76 | 139 | 93.02% | 143.2917 | 87.03% | 100% | 93.21% | 8.092 | 138.64 | 1121.8749 | 26.781 | 945 | 25308.045 | 8830.578 | 127.875 | 0 | 0 | 0 | 0 | 19 | 720 | 0 | 959 | 968 | 1176 | 9 | 8830.578 | 49 | 1.175 | 1.141 | 28.5 | 26.2 | 21.8 | 23.6 | 978.6 | 50.13 | 0.933 | 95.6 | 86.8 | -8.8 | 12847 | 12796 | -51 | 2.316 | 12 | 12 | 24 | 6.72
| 2017-07-04 | 93.8 | 64.1% | 100 | 86 | 11 | 29 | 12 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 3459 | 1734 | 1734 | 1416 | 1465 | 40 | 727 | 41 | 693 | 60 | 695 | 65 | -318 | 123 | 49.63% | 144.125 | 40.94% | 51.15% | 43.44% | 4.172 | 136.6 | 569.8952 | 12.811 | 945 | 12106.395 | 8952.1823 | 72.25 | 0 | 0 | 0 | 0 | 21 | 745 | 16 | 472 | 501 | 492 | 29 | 8952.1823 | 20.5 | 0 | 0 | 25.84 | 13.06 | 11.35 | 12.18 | 97.46 | 50.07 | 0.9334 | 95.74 | 86.92 | -8.82 | 12801 | 12693 | -108 | 0 | 0 | 0 | 11.48 | 0
| 2017-07-05 | 92.1 | 67.8% | 99 | 87 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 3474 | 3326 | 3326 | 86 | 94 | 40 | 1440 | 41 | 1293 | 60 | 1388 | 34 | -3240 | 55 | 7.121% | 144.75 | 2.476% | 4.505% | 2.796% | 0.637 | 149.73 | 95.378 | 1.321 | 940 | 1241.74 | 15547.8838 | 138.5833 | 0 | 0 | 13 | 99 | 42 | 52 | 26 | 0 | 79 | 15 | 79 | 15547.8838 | 0.625 | 0 | 0 | 0 | 0 | 3.22 | 2.16 | 978.25 | 50.1 | 0.9286 | 0 | 87.62 | 87.62 | 0 | 13619 | 13619 | 0 | 0 | 0 | 0 | 0.5
| 2017-07-06 | 90.2 | 71.2% | 101 | 80 | 22 | 12 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3500 | 2827 | 2827 | 2762 | 2863 | 39 | 67 | 41 | 0 | 60 | 0 | 101 | -65 | 127 | 93.93% | 145.8333 | 78.91% | 98.7% | 83.93% | 8.091 | 141.89 | 1148.032 | 24.687 | 931 | 22983.597 | 8737.0127 | 117.7917 | 24 | 41 | 0 | 0 | 20 | 1440 | 0 | 920 | 996 | 947 | 76 | 8737.0127 | 39.4583 | 0 | 0 | 25.66 | 25.49 | 22.43 | 24.12 | 980.5 | 50.15 | 0.9316 | 95.8 | 87.12 | 12845 | 12845 | 12664 | -181 | 0 | 0 | 0 | 21.18 | 7.25
| 2017-07-07 | 90.26 | 64.84% | 100 | 79 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3489 | 2964 | 2964 | 2892 | 2996 | 42 | 0 | 42 | 0 | 60 | 0 | 104 | -72 | 128 | 97.53% | 145.375 | 82.89% | 100% | 87.5% | 8.1 | 137.53 | 1113.993 | 25.489 | 942 | 24010.638 | 8687.6317 | 123.5 | 0 | 0 | 0 | 0 | 18 | 1440 | 0 | 995 | 1003 | 998 | 8 | 8687.6317 | 41.5833 | 0 | 0 | 29.15 | 27.04 | 22.45 | 23.98 | 983.38 | 50.09 | 0.9332 | 95.67 | 87.05 | -8.62 | 12784 | 12584 | -200 | 0 | 0 | 0 | 24 | 4.9
| 2017-07-08 | 95.9 | 61.87% | 104 | 87 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3439 | 2914 | 2914 | 2844 | 2943 | 41 | 0 | 41 | 0 | 60 | 0 | 99 | -70 | 125 | 98.1% | 143.2917 | 82.7% | 100% | 86.62% | 8.085 | 140.68 | 1137.3978 | 24.891 | 947 | 23571.777 | 8688.1768 | 121.4167 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 971 | 987 | 985 | 16 | 8688.1768 | 41.0417 | 0 | 0 | 28.53 | 26.44 | 21.98 | 23.94 | 983.17 | 50.11 | 0.9323 | 95.31 | 86.94 | -8.37 | 12789 | 12559 | -230 | 0 | 0 | 0 | 24 | 0
Week 28 | 2017-07-09 | 95.46 | 59.5% | 103 | 86 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3444 | 2917 | 2917 | 2844 | 2944 | 40 | 0 | 41 | 0 | 60 | 0 | 100 | -73 | 125 | 98.13% | 143.5 | 82.58% | 100% | 86.52% | 8.15 | 143.46 | 1169.199 | 24.928 | 945 | 23556.96 | 8694.1487 | 121.5417 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 969 | 989 | 986 | 20 | 8694.1487 | 41.0833 | 0 | 0 | 28.58 | 26.41 | 22.03 | 23.84 | 980.33 | 50.14 | 0.9318 | 94.93 | 86.86 | 12794 | 12794 | 12547 | -247 | 0 | 0 | 0 | 24 | 0
| 2017-07-10 | 95 | 58% | 103 | 89 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3444 | 2913 | 2913 | 2844 | 2948 | 40 | 0 | 41 | 0 | 60 | 0 | 104 | -69 | 125 | 98.27% | 143.5 | 82.58% | 100% | 86.52% | 8.13 | 139.71 | 1135.8423 | 24.954 | 944 | 23556.576 | 8682.2849 | 121.375 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 970 | 991 | 987 | 21 | 8682.2849 | 41.125 | 0 | 0 | 28.6 | 26.4 | 22 | 23.88 | 980.8 | 50.11 | 0.9328 | 94.88 | 86.9 | -7.98 | 12791 | 12528 | -263 | 0 | 0 | 0 | 24 | 6.95
| 2017-07-11 | 94.7 | 62% | 101 | 90 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3443 | 2899 | 2899 | 2834 | 2935 | 40 | 0 | 41 | 0 | 60 | 0 | 101 | -65 | 125 | 97.83% | 143.4583 | 82.31% | 100% | 86.52% | 8.121 | 138.7 | 1126.3827 | 24.871 | 945 | 23503.095 | 8690.712 | 120.7917 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 969 | 983 | 983 | 14 | 8690.712 | 40.9583 | 0 | 0 | 28.6 | 26.4 | 21.9 | 23.77 | 980.3 | 50.11 | 0.9329 | 95.35 | 86.95 | -8.4 | 12800 | 12558 | -242 | 0 | 0 | 0 | 24 | 2.2
| 2017-07-12 | 94 | 63% | 101 | 86 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3456 | 2919 | 2919 | 2850 | 2955 | 40 | 0 | 41 | 0 | 60 | 0 | 105 | -69 | 126 | 97.72% | 144 | 82.47% | 100% | 86.52% | 8.135 | 140.02 | 1139.0627 | 24.971 | 945 | 23597.595 | 8679.529 | 121.625 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 978 | 991 | 986 | 13 | 8679.529 | 41.0833 | 0 | 0 | 28.78 | 26.5 | 22 | 23.7 | 981.9 | 50.16 | 0.9325 | 95.5 | 86.9 | -8.6 | 12747 | 12511 | -236 | 0 | 0 | 0 | 24 | 6.5
| 2017-07-13 | 90 | 67.2% | 97 | 82 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3502 | 2942 | 2942 | 2870 | 2973 | 41 | 0 | 41 | 0 | 60 | 0 | 103 | -72 | 127 | 97.54% | 145.9167 | 81.95% | 100% | 86.62% | 8.145 | 139.33 | 1134.8428 | 25.189 | 944 | 23778.416 | 8680.578 | 122.5833 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 990 | 994 | 989 | 4 | 8680.578 | 41.2083 | 0 | 0 | 29.2 | 26.8 | 22.2 | 23.8 | 984.3 | 50.12 | 0.933 | 96.1 | 87.1 | -9 | 12729 | 12541 | -188 | 0 | 0 | 0 | 24 | 8.83
| 2017-07-14 | 93.9 | 63.4% | 102 | 85 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3458 | 2923 | 2923 | 2853 | 2960 | 41 | 0 | 41 | 0 | 60 | 0 | 107 | -70 | 126 | 97.88% | 144.0833 | 82.5% | 100% | 86.62% | 8.137 | 139.39 | 1134.2164 | 25.06 | 944 | 23656.64 | 8689.3994 | 121.7917 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 983 | 987 | 990 | 4 | 8689.3994 | 41.25 | 0 | 0 | 28.7 | 26.7 | 22 | 23.6 | 983.33 | 50.18 | 0.9333 | 95.6 | 86.9 | -8.7 | 12764 | 12576 | -188 | 0 | 0 | 0 | 24 | 7.77
| 2017-07-15 | 95.4 | 61.4% | 103 | 87 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3445 | 2920 | 2920 | 2849 | 2952 | 41 | 0 | 41 | 0 | 60 | 0 | 103 | -71 | 126 | 97.62% | 143.5417 | 82.7% | 100% | 86.62% | 8.14 | 140.12 | 1140.5768 | 24.997 | 943 | 23572.171 | 8674.1832 | 121.6667 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 982 | 981 | 989 | -1 | 8674.1832 | 41.2083 | 0 | 0 | 28.6 | 26.7 | 21.9 | 23.8 | 982.6 | 50.13 | 0.9332 | 95.5 | 86.9 | -8.6 | 12781 | 12584 | -197 | 0 | 0 | 0 | 24 | 6.32
Week 29 | 2017-07-16 | 96.1 | 62.2% | 103 | 88 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3442 | 2898 | 2898 | 2831 | 2936 | 41 | 0 | 41 | 0 | 60 | 0 | 105 | -67 | 125 | 97.87% | 143.4167 | 82.25% | 100% | 86.62% | 8.09 | 140.97 | 1140.4473 | 24.989 | 942 | 23539.638 | 8717.7977 | 120.75 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 977 | 975 | 984 | -2 | 8717.7977 | 41 | 0 | 0 | 28.5 | 26.7 | 21.83 | 23.52 | 980.7 | 50.11 | 0.9327 | 95.58 | 86.87 | -8.71 | 12841 | 12622 | -219 | 0 | 0 | 0 | 24 | 6.67
| 2017-07-17 | 95.5 | 62.4% | 104 | 87 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3446 | 2909 | 2909 | 2839 | 2942 | 41 | 0 | 41 | 0 | 60 | 0 | 103 | -70 | 125 | 98.07% | 143.5833 | 82.39% | 100% | 86.62% | 8.112 | 143.63 | 1165.1266 | 24.921 | 943 | 23500.503 | 8688.14 | 121.2083 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 978 | 977 | 987 | -1 | 8688.14 | 41.125 | 0 | 0 | 28.05 | 26.63 | 21.81 | 23.62 | 981.54 | 50.13 | 0.9319 | 95.52 | 86.89 | -8.63 | 12781 | 12577 | -204 | 0 | 0 | 0 | 24 | 7.83
| 2017-07-18 | 89.8 | 72.3% | 104 | 82 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3504 | 2954 | 2954 | 2881 | 2987 | 41 | 0 | 41 | 0 | 60 | 0 | 106 | -73 | 128 | 97.23% | 146 | 82.22% | 100% | 86.62% | 8.08 | 140.27 | 1133.3816 | 25.251 | 944 | 23836.944 | 8667.2425 | 123.0833 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 1001 | 991 | 995 | -10 | 8667.2425 | 41.4583 | 0 | 0 | 29.2 | 27.05 | 22.03 | 23.6 | 982.8 | 50.14 | 0.933 | 96.42 | 87.06 | -9.36 | 12715 | 12535 | -180 | 0 | 0 | 0 | 24 | 7.92
| 2017-07-19 | 91.16 | 72.85% | 99 | 82 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3480 | 2928 | 2928 | 2857 | 2957 | 41 | 0 | 41 | 0 | 60 | 0 | 100 | -71 | 126 | 97.78% | 145 | 82.1% | 100% | 86.62% | 8.075 | 139.23 | 1124.2822 | 25.091 | 943 | 23660.813 | 8675.2171 | 122 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 992 | 977 | 988 | -15 | 8675.2171 | 41.1667 | 0 | 0 | 29.05 | 26.93 | 21.84 | 23.44 | 982.71 | 50.09 | 0.9336 | 96.69 | 87.08 | -9.61 | 12756 | 12570 | -186 | 0 | 0 | 0 | 24 | 5.61
| 2017-07-20 | 90.14 | 73.34% | 104 | 87 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3497 | 2943 | 2943 | 2869 | 2973 | 42 | 0 | 41 | 0 | 60 | 0 | 104 | -74 | 126 | 98.31% | 145.7083 | 82.04% | 100% | 86.71% | 8.01 | 140.05 | 1121.8005 | 25.241 | 943 | 23802.263 | 8687.3696 | 122.625 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 997 | 984 | 992 | -13 | 8687.3696 | 41.3333 | 0 | 0 | 29.16 | 27.05 | 21.97 | 23.45 | 980.4 | 50.11 | 0.9329 | 96.69 | 87.07 | -9.62 | 12748 | 12555 | -193 | 0 | 0 | 0 | 24 | 7.15
| 2017-07-21 | 91.39 | 71.47% | 99 | 83 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3483 | 2930 | 2930 | 2858 | 2961 | 41 | 0 | 41 | 0 | 60 | 0 | 103 | -72 | 126 | 97.92% | 145.125 | 82.06% | 100% | 86.62% | 8 | 140.68 | 1125.44 | 25.145 | 943 | 23711.735 | 8690.4041 | 122.0833 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 992 | 980 | 989 | -12 | 8690.4041 | 41.2083 | 0 | 0 | 28.97 | 26.96 | 21.88 | 23.57 | 980.9 | 50.1 | 0.9321 | 96.52 | 87.02 | -9.5 | 12770 | 12591 | -179 | 0 | 0 | 0 | 24 | 7.15
| 2017-07-22 | 94 | 68% | 101 | 87 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3459 | 2908 | 2908 | 2839 | 2940 | 41 | 0 | 40 | 0 | 60 | 0 | 101 | -69 | 124 | 98.79% | 144.125 | 82.08% | 100% | 86.52% | 8.007 | 140.56 | 1125.4639 | 24.968 | 943 | 23544.824 | 8689.7809 | 121.1667 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 983 | 974 | 983 | -9 | 8689.7809 | 40.9583 | 0 | 0 | 28.75 | 26.78 | 21.75 | 23.5 | 980.67 | 50.12 | 0.9328 | 96.22 | 86.92 | -9.3 | 12797 | 12591 | -206 | 0 | 0 | 0 | 24 | 6.85
Week 30 | 2017-07-23 | 93 | 70% | 99 | 86 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3472 | 2912 | 2912 | 2848 | 2950 | 41 | 0 | 40 | 0 | 60 | 0 | 102 | -64 | 125 | 98.33% | 144.6667 | 82.03% | 100% | 86.52% | 8.014 | 140.49 | 1125.8869 | 24.999 | 944 | 23599.056 | 8681.5108 | 121.3333 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 987 | 977 | 986 | -10 | 8681.5108 | 41.0833 | 0 | 0 | 28.88 | 26.82 | 21.8 | 23.4 | 981 | 50.11 | 0.933 | 96.41 | 86.96 | -9.45 | 12765 | 12566 | -199 | 0 | 0 | 0 | 24 | 7.4
| 2017-07-24 | 93 | 67% | 100 | 86 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 10 | 30 | 3470 | 3091 | 3091 | 3031 | 3140 | 41 | 0 | 40 | 0 | 60 | 0 | 109 | -60 | 140 | 93.45% | 144.5833 | 87.35% | 100% | 92.42% | 8.012 | 140.27 | 1123.8432 | 27.091 | 945 | 25600.995 | 8817.1687 | 128.7917 | 0 | 0 | 0 | 0 | 19 | 810 | 0 | 987 | 978 | 1175 | -9 | 8817.1687 | 48.9583 | 1.137 | 1.025 | 28.84 | 26.8 | 21.87 | 23.3 | 979.6 | 50.13 | 0.9326 | 96.11 | 86.9 | -9.21 | 12761 | 12571 | -190 | 2.162 | 12 | 10.5 | 24 | 7.26
| 2017-07-25 | 93.5 | 67.7% | 100 | 86 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3465 | 2908 | 2908 | 2842 | 2946 | 41 | 0 | 41 | 0 | 60 | 0 | 104 | -66 | 125 | 98.2% | 144.375 | 82.02% | 100% | 86.62% | 8.05 | 137.53 | 1107.1165 | 24.858 | 945 | 23490.81 | 8655.1466 | 121.1667 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 984 | 976 | 986 | -8 | 8655.1466 | 41.0833 | 0 | 0 | 28.8 | 26.7 | 21.7 | 23.4 | 979.5 | 50.14 | 0.9336 | 96.2 | 86.9 | -9.3 | 12769 | 12545 | -224 | 0 | 0 | 0 | 24 | 7.58
| 2017-07-26 | 94.23 | 65.13% | 100 | 87 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3452 | 2904 | 2904 | 2837 | 2939 | 41 | 0 | 41 | 0 | 60 | 0 | 102 | -67 | 125 | 97.97% | 143.8333 | 82.18% | 100% | 86.62% | 8.071 | 137.24 | 1107.664 | 24.897 | 944 | 23502.768 | 8674.8086 | 121 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 978 | 974 | 987 | -4 | 8674.8086 | 41.125 | 0 | 0 | 28.6 | 26.7 | 21.7 | 23.1 | 982.7 | 50.14 | 0.9332 | 95.6 | 86.7 | -8.9 | 12809 | 12563 | -246 | 0 | 0 | 0 | 24 | 7.03
| 2017-07-27 | 95.4 | 63.4% | 104 | 87 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3447 | 2903 | 2903 | 2836 | 2939 | 41 | 0 | 41 | 0 | 60 | 0 | 103 | -67 | 125 | 97.97% | 143.625 | 82.27% | 100% | 86.62% | 8.032 | 138.51 | 1112.5123 | 24.878 | 944 | 23484.832 | 8673.2526 | 120.9583 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 978 | 974 | 987 | -4 | 8673.2526 | 41.125 | 0 | 0 | 28.6 | 26.7 | 21.7 | 23.1 | 982.7 | 50.14 | 0.9332 | 95.6 | 86.7 | -8.9 | 12809 | 12563 | -246 | 0 | 0 | 0 | 24 | 7.03
| 2017-07-28 | 90.9 | 71.5% | 102 | 83 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 3491 | 3100.5 | 3100.5 | 3036 | 3147 | 41 | 0 | 41 | 0 | 60 | 0 | 111 | -64.5 | 140 | 93.66% | 145.4583 | 86.97% | 100% | 93.31% | 8.033 | 138.35 | 1111.3655 | 27.045 | 944 | 25530.48 | 8775.3114 | 129.1875 | 0 | 0 | 0 | 0 | 19 | 720 | 0 | 994 | 983 | 1170 | -11 | 8775.3114 | 48.75 | 1.029 | 1.011 | 29.07 | 26.97 | 21.96 | 23.29 | 983.46 | 50.16 | 0.9333 | 96.39 | 86.88 | -9.51 | 12737 | 12561 | -176 | 2.04 | 12 | 12 | 24 | 7.1
| 2017-07-29 | 91.9 | 69.9% | 100 | 83 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3478 | 2928 | 2928 | 2858 | 2957 | 41 | 0 | 40 | 0 | 60 | 0 | 99 | -70 | 126 | 97.78% | 144.9167 | 82.17% | 100% | 86.52% | 8.03 | 139.87 | 1123.1561 | 24.975 | 945 | 23601.375 | 8650.9906 | 122 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 990 | 977 | 990 | -13 | 8650.9906 | 41.25 | 0 | 0 | 28.9 | 26.86 | 21.84 | 23.21 | 984.42 | 50.09 | 0.9328 | 96.34 | 86.83 | -9.51 | 12752 | 12566 | -186 | 0 | 0 | 0 | 24 | 7.75
| 2017-07-30 | 94.3 | 66.9% | 101 | 87 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3455 | 2909 | 2909 | 2838 | 2939 | 41 | 0 | 40 | 0 | 60 | 0 | 101 | -71 | 125 | 97.97% | 143.9583 | 82.14% | 100% | 86.52% | 8.01 | 138.6 | 1110.186 | 24.801 | 947 | 23486.547 | 8666.9249 | 121.2083 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 981 | 972 | 986 | -9 | 8666.9249 | 41.0833 | 0 | 0 | 28.7 | 26.69 | 21.75 | 23.02 | 982.92 | 50.09 | 0.9334 | 96.12 | 86.82 | -9.3 | 12782 | 12593 | -189 | 0 | 0 | 0 | 24 | 11.16
| 2017-07-31 | 95.5 | 66.9% | 104 | 88 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 11 | 30 | 3445 | 3078 | 3078 | 3008 | 3117 | 41 | 0 | 40 | 0 | 60 | 0 | 109 | -70 | 139 | 93.44% | 143.5417 | 87.31% | 100% | 92.98% | 8.005 | 136.43 | 1092.1222 | 27.003 | 947 | 25571.841 | 8864.3495 | 128.25 | 0 | 0 | 0 | 0 | 19 | 750 | 0 | 973 | 968 | 1176 | -5 | 8864.3495 | 49 | 1.08 | 1.08 | 28.57 | 26.62 | 21.8 | 23.1 | 981.79 | 50.08 | 0.9338 | 96.23 | 86.84 | -9.39 | 12845 | 12667 | -178 | 2.16 | 11.77 | 11.68 | 24 | 7.5
| Monthly | 93.3755 | 66.1% | 101.4516 | 85.5161 | 705 | 41 | 708 | 57 | 0 | 0 | 0 | 0 | 45 | 0 | 107389 | 90243.5 | 90243.5 | 84853.1 | 87737 | 40.7097 | 2234 | 40.8065 | 1986 | 60 | 2083 | 2925.9 | -5563.5 | 125.0323 | 92.72% | 144.3401 | 79.01% | 95.3% | 83.26% | 238.925 | 139.9829 | 33386.7645 | 746.855 | 943.7419 | 704924.709 | 8701.0548 |  | 24 | 41 | 13 | 99 | 614 | 39797 | 42 | 28855 | 29039 | 29842 | 184 | 8701.0548 | 1243.4167 | 4.421 | 4.257 | 27.6381 | 25.3452 | 20.9739 | 22.4997 | 952.9439 | 50.119 | 0.93273 | 92.7523 | 86.9419 |  | 12374.129 | 12628.7097 |  | 8.678 | 47.77 | 46.18 | 704.66 | 176.93
| Totals | Avg.F | % Avg. | M Avg | m Avg | hrs | min | hrs | min | hrs | min | hrs | min | Avg Int Avi | Avg Ext Avi | MWhr Total | MWhr Total | MWhr Total | MWhr Total | MWhr Total | MW Avg | Total min | Avg MW | Total min | Avg MW | Total min | MWhr | Total MW | Av Max D/Gen | Av. DailyLF | Avg. | Avg. |  | Avg. | Total | Avg. |  | Total | Avg. |  | Avg. | [7 empty] | Total |  |  |  |  | Avg. | [18 empty] | 46.975
| Weeks data | Site Avg. Amb. Temp F | Site Avg. Relative humidity % | Max: Site Maximum/Minumum Temperature; CT1 hrs: CT-1 Base Load Hours; CT2 hrs: CT-2 Base Load Hours; CT1 hrs: CT-1 stand by hours / min; CT2 hrs: CT-2 standby hours / min; CT2 hrs: Plant ambient Corrected maximum Load hours/min | Average Corrected Plant Capacity | Ambient Corrected Declared Avail'y (MWH) | Av Plant WAPDA Dispatch | Net Plant Export (MWH) | Gross Generation | CT1 Av Cap (MW) | CT1 Unavail minutes | CT2 Av Cap (MW) | CT2 Unavail minutes | ST Unavail minutes | ST Average Cap (MW) | Plant Aux Load including Colony Load MWH | Differenece (+/-) MW | Maximum Daily Generation | Daily Load Factor | Avg. Corrected Plant | Plant Capacity Facto | Plant Availability Factor | Equivalent Plant Availability | LBtu gas flow mmscf | 1 LBtu gas (Average Btu/scf) | LBTU MMBTU | PL gas flow (mscf/week) | 1 PL gas (Average Btu/scf) | HBTU MMBTU | Plant Net Heat Rate (Btu/Kwh) | [11 empty] | -9.75
| Week 26 | 91.7786 | 66.71% | 99.1429 | 84 | 167 | 39 | 168 | 0 | 0 | 0 | 0 | 0 | 47 | 3 | 3479 | 3029.7143 | 3023.4286 | 2959.5714 | 3063 | 40.5714 | No outage | 40.8571 | No outage | 420 | no data | no data | -447 | 133.7143 | 95.55% | 144.9583 | 85.07% | 100% | 90.62% | 56.187 | 140.8971 | 7916.5878 | 183.866 | 943.793 | 173531.4521 | 8756.3417
| Week 27 | 93.3943 | 65.2% | 101.7143 | 84.7143 | 129 | 39 | 132 | 57 | 0 | 0 | 0 | 0 | 12 | 3 | 3463.7143 | 2815.8571 | 2815.8571 | 15804 | 16375 | 40.2857 | 2234 | 287 | no data | 420 | no data | 613 | -3907 | 117.2857 | 76.73% | 144.3214 | 65.22% | 79.19% | 69.15% | 45.272 | 140.8743 | 6377.6607 | 140.841 | 942.1429 | 132692.3421 | 9743.9155 | [5 empty] | 0.27381
| Week 28 | 94.0657 | 62.07% | 101.4286 | 86.4286 | 168 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3456 | 2919 | 2919 | 19944 | 20667 | 40.4286 | No outage | 287 | no data | 420 | no data | 723 | -489 | 125.7143 | 97.86% | 144 | 82.44% | 100% | 86.57% | 56.958 | 140.1043 | 7980.0599 | 149.973 | 944.5 | 141649.4985 | 8684.405 | [5 empty] | 0.26672
| Week 29 | 92.5843 | 68.94% | 102 | 85.1429 | 168 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3473 | 2924.2857 | 2924.2857 | 19974 | 20696 | 41.1429 | No outage | 286 | no data | 420 | no data | 722 | -496 | 125.7143 | 98% | 144.7083 | 82.16% | 100% | 86.62% | 56.374 | 140.77 | 7935.768 | 175.606 | 943 | 165596.458 | 8687.9931
| Week 30 | 93.5256 | 0.67603 | 101.1111 | 85.8889 | 216 | 0 | 216 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 3463.8889 | 2970.3889 | 2970.3889 | 26134 | 27074 | 41 | #REF! | #REF! | no data | #REF! | no data | 940 | -599.5 | 130 | 96.53% | 144.3287 | 83.83% | 100% | 88.68% | 72.257 | 138.5878 | 10013.9371 | 230.547 | 945 | 217866.915 | 8717.7182
| Week 31 | 93.5673 | 0.6717 | 101.3835 | 85.8351 | 897 | 41 | 900 | 57 | 0 | 0 | 0 | 0 | 79 | 0 | 15010.2222 | 12673.8889 | 12673.8889 | 108139.1 | 111861 | 40.9677 | #REF! | #REF! | no data | #REF! | no data | 3763.9 | -6099 | 130.0036 | 95.91% | 144.2924 | 83.49% | 99.48% | 88.32% | 303.168 | 138.5314 | 41998.2977 | 952.403 | 944.9713 | 899993.526 | 8719.8897
| Date | Plant Status Whether Normal Operation or Tripping (State full detail for trippings/return to normal).
| 2017-07-01 | Plant load restricted to 115~120 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-07-02 | Plant load restricted to 116~120 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-07-03 | Plant load increased from 118 to 132 MW by taking DBs into service at 1100 hrs to achieve maximum export. At 2300 hrs, plant load reduced from 134 to 116 MW by taking duct burners out of service to keep within contractual plant heat rate.
| 2017-07-04 | CT-1 de-synch @ 1153 hrs, CT-2 de-synch @ 1227 hrs & STG de-synch @ 1225 hrs due to suspension of HBTU gas supply by SNGPL.
| 2017-07-05 | After restoration of HBTU gas supply by M/S SNGPL, CT-2 synch @ 2133 hrs & STG synch @ 2308 hrs.
| 2017-07-06 | CT-1 synch @ 0107 hrs, DBs remained OFF throughout the day to remain within contractual heat rate.
| 2017-07-07 | Plant load restricted to 118~124 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-07-08 | Plant load restricted to 116~121 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-07-09 | Plant load restricted to 116~121 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-07-10 | Plant load restricted to 116~120 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-07-11 | Plant load restricted to 116~120 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-07-12 | Plant load restricted to 116~122 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-07-13 | Plant load restricted to 117~122 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-07-14 | Plant load restricted to 117~121 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-07-15 | Plant load restricted to 117~121 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-07-16 | Plant load restricted to 116~121 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-07-17 | Plant load restricted to 115~121 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-07-18 | Plant load restricted to 116~123 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-07-19 | Plant load restricted to 116~122 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-07-20 | Plant load restricted to 116~122 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-07-21 | Plant load restricted to 117~122 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-07-22 | Plant load restricted to 116~120 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-07-23 | Plant load restricted to 117~120 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-07-24 | Plant load increased from 119 to 133 MW by taking DBs into service at 1230 hrs to achieve maximum export. At 2300 hrs, plant load reduced from 134 to 120 MW by taking duct burners out of service to keep within contractual plant heat rate.
| 2017-07-25 | Plant load restricted to 117~121 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-07-26 | Plant load restricted to 117~121 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-07-27 | Plant load restricted to 116~121 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-07-28 | Plant load increased from 118 to 133 MW by taking DBs into service at 1100 hrs to achieve maximum export. At 2300 hrs, plant load reduced from 134 to 122 MW by taking duct burners out of service to keep within contractual plant heat rate.
| 2017-07-29 | Plant load restricted to 116~122 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-07-30 | Plant load restricted to 116~120 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-07-31 | Plant load increased from 118 to 132 MW by taking DBs into service at 1100 hrs to achieve maximum export. At 2230 hrs, plant load reduced from 134 to 119 MW by taking duct burners out of service to keep within contractual plant heat rate.

## Aug
Monthly Operational Returns Kabirwala
2017-08-01
| Date | Site Avg. Ambient Temp.F | Site Avg. Relative Humidty % | Site Ambient Temp |  | Base load hours |  |  |  | Standby hours |  |  |  | Plant ambient corrected Max Load |  | Corrected Plant Capacity | Ambient Corrected Daclared Avail'y (MWH) | Plant WAPDA Dispatch (MWH) | Net Plant Export (MWH) | Gross Generation | CT1 Average Cap (MW) | CT1 Unavail minutes | CT2 Average Cap (MW) | CT2 Unavail minutes | ST Average Cap (MW) | ST Unavail minutes | Plant Aux Load including Colony Load MWH | Differenece (+/-) MW | Maximum Daily Generation | Daily Load Factor | Avg. Corrected Plant Capacity | Plant Capacity Factor | Plant Availability Factor | Equivalent Plant Availability | LBtu gas flow (mmscf/day) | 1 LBtu gas (Average Btu/scf) | LBTU MMBTU | 1 HBtu gas flow (mmscf/day) | 1 HBtu gas (Average Btu/scf) | HBTU MMBTU | HHV Net Heat Rate (Btu/Kwh) | Avg. declared availability | CT1 Derated MW | CT1 derated mintutes | CT-2 derated MW | CT-2 derated mintutes | ST derated MW | ST derated mintutes | WAPDA Backfeed (MWH) | CT-1 Gross Generation (MWH) | CT-2 Gross Generation (MWH) | STG Gross Generation (MWH) | CT-1 & CT-2 MWH difference | Base load Heat Rate | STG load | DB1 | DB2 | CT1 | CT1 Gas flow | CT2 Gas flow |  | Pamb | Freq. Hz | LBTU Gas Specific gravity | CT-1 compressor efficiency(%) | CT-2 compressor efficiency(%) |  | CT-1 Heat Rate (Btu/Kwh) | CT-2 Heat Rate (Btu/Kwh) |  | DB(1+2) | DB-1 Ops Hours | DB-2 Ops Hours | CT-1 Wetcomprssion Ops Hours | RO Operation Hours
[6 empty] | CT1 |  | CT2 |  | CT1 |  | CT2 | [43 empty] | mmscf/d | mmscf/d | WetC flow | HBTU KPPH | HBTU KPPH | LBTU KPPH | mbar | Hz | [7 empty] | mmscf/d
|  |  |  | Max | Min | hrs | min | hrs | min | hrs | min | hrs | min | hrs | min | [42 empty] | gpm
Week 31 | 2017-07-30 | 94.3 | 66.9% | 101 | 87 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3455 | 2909 | 2909 | 2838 | 2939 | 41 | 0 | 40 | 0 | 60 | 0 | 101 | -71 | 125 | 97.97% | 143.9583 | 82.14% | 100% | 86.52% | 8.01 | 138.6 | 1110.186 | 24.801 | 947 | 23486.547 | 8666.9249 | 121.2083 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 981 | 972 | 986 | -9 | 8666.9249 | 41.0833 | 0 | 0 | 28.7 | 26.69 | 21.75 | 23.02 | 982.92 | 50.09 | 0.9334 | 96.12 | 86.82 | -9.3 | 12782 | 12593 | -189 | 0 | 0 | 0 | 24 | 11.16
| 2017-07-31 | 95.5 | 66.9% | 104 | 88 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 11 | 30 | 3445 | 3078 | 3078 | 3008 | 3117 | 41 | 0 | 40 | 0 | 60 | 0 | 109 | -70 | 139 | 93.44% | 143.5417 | 87.31% | 100% | 92.98% | 8.005 | 136.43 | 1092.1222 | 27.003 | 947 | 25571.841 | 8864.3495 | 128.25 | 0 | 0 | 0 | 0 | 19 | 750 | 0 | 973 | 968 | 1176 | -5 | 8864.3495 | 49 | 1.08 | 1.08 | 28.57 | 26.62 | 21.8 | 23.1 | 981.79 | 50.08 | 0.9338 | 96.23 | 86.84 | -9.39 | 12845 | 12667 | -178 | 2.16 | 11.77 | 11.68 | 24 | 7.5
| 2017-08-01 | 94.26 | 65.72% | 102 | 89 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3455 | 2879 | 2879 | 2812 | 2915 | 40 | 0 | 41 | 0 | 60 | 0 | 103 | -67 | 124 | 97.95% | 143.9583 | 81.39% | 100% | 86.52% | 7.966 | 137.48 | 1095.1657 | 24.683 | 944 | 23300.752 | 8675.6464 | 119.9583 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 954 | 975 | 986 | 21 | 8675.6464 | 41.0833 | 0 | 0 | 25.92 | 26.21 | 21.81 | 23.31 | 982.42 | 50.06 | 0.9337 | 93.8 | 86.79 |  | 12924 | 12593 | -331 | 0 | 0 | 0 | 18.43 | 2.76
| 2017-08-02 | 92.89 | 66.79% | 99 | 88 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3472 | 2929 | 2929 | 2861 | 2962 | 41 | 0 | 41 | 0 | 60 | 0 | 101 | -68 | 126 | 97.95% | 144.6667 | 82.4% | 100% | 86.62% | 8.11 | 140.51 | 1139.5361 | 25.179 | 944 | 23768.976 | 8706.2258 | 122.0417 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 990 | 979 | 993 | -11 | 8706.2258 | 41.375 | 0 | 0 | 24 | 26.78 | 21.83 | 23.39 | 981.7 | 50.1 | 0.9327 | 95.88 | 86.8 |  | 12717 | 12546 | -171 | 0 | 0 | 0 | 24 | 8.96
| 2017-08-03 | 93 | 67% | 101 | 87 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3464 | 2922 | 2922 | 2854 | 2956 | 41 | 0 | 40 | 0 | 60 | 0 | 102 | -68 | 126 | 97.75% | 144.3333 | 82.39% | 100% | 86.52% | 8.091 | 139.38 | 1127.7236 | 25.045 | 943 | 23617.435 | 8670.3429 | 121.75 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 988 | 977 | 991 | -11 | 8670.3429 | 41.2917 | 0 | 0 | 24 | 26.75 | 21.78 | 23.3 | 979.6 | 50.07 | 0.9329 | 95.86 | 86.72 |  | 12725 | 12561 | -164 | 0 | 0 | 0 | 24 | 8.9
| 2017-08-04 | 93.5 | 67% | 101 | 87 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3459 | 2916 | 2916 | 2848 | 2948 | 41 | 0 | 40 | 0 | 60 | 0 | 100 | -68 | 125 | 98.27% | 144.125 | 82.34% | 100% | 86.52% | 8.07 | 134.71 | 1087.1097 | 25.032 | 945 | 23655.24 | 8687.6228 | 121.5 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 985 | 973 | 990 | -12 | 8687.6228 | 41.25 | 0 | 0 | 24 | 26.7 | 21.74 | 23.4 | 978.3 | 50.08 | 0.9343 | 95.85 | 86.71 |  | 12729 | 12572 | -157 | 0 | 0 | 0 | 24 | 4.7
| 2017-08-05 | 94 | 66% | 102 | 87 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3459 | 2926 | 2926 | 2856 | 2958 | 41 | 0 | 41 | 0 | 60 | 0 | 102 | -70 | 125 | 98.6% | 144.125 | 82.57% | 100% | 86.62% | 8.1 | 138.74 | 1123.794 | 25.024 | 946 | 23672.704 | 8682.2472 | 121.9167 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 987 | 979 | 992 | -8 | 8682.2472 | 41.3333 | 0 | 0 | 24 | 26.8 | 21.8 | 23.4 | 980.4 | 50.13 | 0.933 | 95.7 | 86.7 |  | 12731 | 12570 | -161 | 0 | 0 | 0 | 24 | 5.8
Week 32 | 2017-08-06 | 95 | 64.1% | 103 | 87 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3450 | 2922 | 2922 | 2858 | 2957 | 41 | 0 | 41 | 0 | 60 | 0 | 99 | -64 | 126 | 97.78% | 143.75 | 82.84% | 100% | 86.62% | 8.12 | 138.1 | 1121.372 | 25.079 | 945 | 23699.655 | 8684.754 | 121.75 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 987 | 978 | 992 | -9 | 8684.754 | 41.3333 | 0 | 0 | 24 | 26.8 | 21.9 | 23.3 | 982.63 | 50.09 | 0.9336 | 95.6 | 86.6 |  | 12762 | 12607 | -155 | 0 | 0 | 0 | 24 | 10.85
| 2017-08-07 | 95.2 | 63.1% | 103 | 88 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3448 | 2924 | 2924 | 2856 | 2958 | 41 | 0 | 41 | 0 | 60 | 0 | 102 | -68 | 125 | 98.6% | 143.6667 | 82.83% | 100% | 86.62% | 8.09 | 137.09 | 1109.0581 | 25.041 | 945 | 23663.745 | 8673.9507 | 121.8333 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 987 | 977 | 994 | -10 | 8673.9507 | 41.4167 | 0 | 0 | 24 | 26.8 | 21.9 | 23.3 | 983.7 | 50.09 | 0.9337 | 95.5 | 86.6 |  | 12756 | 12592 | -164 | 0 | 0 | 0 | 24 | 10.34
| 2017-08-08 | 95.2 | 61.3% | 104 | 88 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3447 | 2926 | 2926 | 2861 | 2961 | 41 | 0 | 41 | 0 | 60 | 0 | 100 | -65 | 125 | 98.7% | 143.625 | 83% | 100% | 86.62% | 8.08 | 136.08 | 1099.5264 | 25.161 | 944 | 23751.984 | 8686.3021 | 121.9167 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 987 | 979 | 995 | -8 | 8686.3021 | 41.4583 | 0 | 0 | 24 | 26.8 | 21.9 | 23.3 | 983.3 | 50.08 | 0.9339 | 95.3 | 86.6 |  | 12744 | 12594 | -150 | 0 | 0 | 0 | 24 | 10.76
| 2017-08-09 | 94.5 | 62.7% | 102 | 87 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3457 | 2923 | 2923 | 2862 | 2964 | 41 | 0 | 41 | 0 | 60 | 0 | 102 | -61 | 125 | 98.8% | 144.0417 | 82.79% | 100% | 86.62% | 8.09 | 137.75 | 1114.3975 | 25.143 | 944 | 23734.992 | 8682.526 | 121.7917 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 991 | 980 | 993 | -11 | 8682.526 | 41.375 | 0 | 0 | 24 | 26.81 | 21.88 | 23.39 | 981.92 | 50.08 | 0.9337 | 95.6 | 86.6 |  | 12735 | 12589 | -146 | 0 | 0 | 0 | 24 | 8.33
| 2017-08-10 | 94.2 | 63.5% | 101 | 88 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3452 | 2926 | 2926 | 2856 | 2959 | 41 | 0 | 41 | 0 | 60 | 0 | 103 | -70 | 125 | 98.63% | 143.8333 | 82.73% | 100% | 86.62% | 8.07 | 137.23 | 1107.4461 | 25.031 | 945 | 23654.295 | 8670.0774 | 121.9167 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 987 | 979 | 993 | -8 | 8670.0774 | 41.375 | 0 | 0 | 24 | 26.72 | 21.86 | 23.34 | 980.71 | 50.11 | 0.9339 | 95.49 | 86.63 |  | 12721 | 12573 | -148 | 0 | 0 | 0 | 24 | 5.86
| 2017-08-11 | 92.2 | 66.7% | 99 | 87 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3469 | 2924 | 2924 | 2857 | 2959 | 41 | 0 | 41 | 0 | 60 | 0 | 102 | -67 | 125 | 98.63% | 144.5417 | 82.36% | 100% | 86.62% | 8.08 | 138.41 | 1118.3528 | 25.041 | 946 | 23688.786 | 8682.9327 | 121.8333 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 988 | 980 | 991 | -8 | 8682.9327 | 41.2917 | 0 | 0 | 24 | 26.77 | 21.97 | 23.31 | 980.1 | 50.16 | 0.9334 | 95.4 | 86.6 |  | 12731 | 12595 | -136 | 0 | 0 | 0 | 24 | 12.2
| 2017-08-12 | 92.85 | 68.52% | 99 | 87 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3468 | 2922 | 2922 | 2855 | 2956 | 41 | 0 | 41 | 0 | 60 | 0 | 101 | -67 | 125 | 98.53% | 144.5 | 82.32% | 100% | 86.62% | 8.075 | 140.27 | 1132.6802 | 24.998 | 946 | 23648.108 | 8679.7857 | 121.75 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 987 | 978 | 991 | -9 | 8679.7857 | 41.2917 | 0 | 0 | 24 | 26.78 | 21.96 | 23.25 | 980.2 | 50.16 | 0.9329 | 95.63 | 86.67 |  | 12751 | 12621 | -130 | 0 | 0 | 0 | 24 | 6.83
Week 33 | 2017-08-13 | 92.29 | 66.27% | 101 | 87 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3478 | 2941 | 2941 | 2872 | 2975 | 41 | 0 | 41 | 0 | 60 | 0 | 103 | -69 | 127 | 97.6% | 144.9167 | 82.58% | 100% | 87.32% | 8.085 | 139.12 | 1124.7852 | 25.161 | 946 | 23802.306 | 8679.3493 | 122.5417 | 0 | 0 | 0 | 0 | 18 | 1440 | 0 | 994 | 985 | 996 | -9 | 8679.3493 | 41.5 | 0 | 0 | 24 | 26.92 | 22.09 | 23.41 | 981.67 | 50.19 | 0.933 | 95.41 | 86.59 |  | 12734 | 12610 | -124 | 0 | 0 | 0 | 24 | 4.5
| 2017-08-14 | 84.34 | 76.35% | 91 | 76 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3551 | 2999 | 2999 | 2928 | 3027 | 42 | 0 | 42 | 0 | 60 | 0 | 99 | -71 | 128 | 98.54% | 147.9583 | 82.46% | 100% | 87.5% | 8.075 | 137.17 | 1107.6477 | 25.689 | 946 | 24301.794 | 8678.088 | 124.9583 | 0 | 0 | 0 | 0 | 18 | 1440 | 0 | 1012 | 1003 | 1012 | -9 | 8678.088 | 42.1667 | 0 | 0 | 24 | 27.31 | 22.48 | 23.46 | 987.33 | 50.17 | 0.9334 | 95.44 | 86.78 |  | 12678 | 12557 | -121 | 0 | 0 | 0 | 24 | 10.16
| 2017-08-15 | 91 | 69% | 98 | 83 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3493 | 2956 | 2956 | 2888 | 2988 | 42 | 0 | 41 | 0 | 60 | 0 | 100 | -68 | 126 | 98.81% | 145.5417 | 82.68% | 100% | 87.41% | 8.06 | 137.68 | 1109.7008 | 25.309 | 946 | 23942.314 | 8674.5204 | 123.1667 | 0 | 0 | 0 | 0 | 18 | 1440 | 0 | 998 | 988 | 1002 | -10 | 8674.5204 | 41.75 | 0 | 0 | 24 | 27 | 22.2 | 23.38 | 986.8 | 50.15 | 0.9334 | 95.33 | 86.63 |  | 12721 | 12616 | -105 | 0 | 0 | 0 | 24 | 12.1
| 2017-08-16 | 93 | 67% | 101 | 84 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3470 | 2930 | 2930 | 2859 | 2958 | 41 | 0 | 41 | 0 | 60 | 0 | 99 | -71 | 126 | 97.82% | 144.5833 | 82.39% | 100% | 86.62% | 8.03 | 139.37 | 1119.1411 | 25.089 | 944 | 23684.016 | 8675.4659 | 122.0833 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 985 | 980 | 993 | -5 | 8675.4659 | 41.375 | 0 | 0 | 24 | 26.76 | 22.04 | 23.34 | 983.2 | 50.13 | 0.9332 | 95.13 | 86.59 |  | 12775 | 12646 | -129 | 0 | 0 | 0 | 22.9 | 10.6
| 2017-08-17 | 92 | 67% | 101 | 83 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3482 | 2938 | 2938 | 2873 | 2975 | 41 | 0 | 41 | 0 | 60 | 0 | 102 | -65 | 126 | 98.38% | 145.0833 | 82.51% | 100% | 86.62% | 8.02 | 138.61 | 1111.6522 | 25.191 | 945 | 23805.495 | 8672.8671 | 122.4167 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 993 | 985 | 997 | -8 | 8672.8671 | 41.5417 | 0 | 0 | 24 | 26.9 | 22.1 | 23.36 | 982.1 | 50.13 | 0.9334 | 95.55 | 86.63 |  | 12740 | 12632 | -108 | 0 | 0 | 0 | 24 | 8.3
| 2017-08-18 | 93 | 65.5% | 102 | 84 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3470 | 2937 | 2937 | 2868 | 2967 | 41 | 0 | 41 | 0 | 60 | 0 | 99 | -69 | 127 | 97.34% | 144.5833 | 82.65% | 100% | 87.32% | 8.015 | 137.61 | 1102.9442 | 25.332 | 945 | 23938.74 | 8731.4101 | 122.375 | 0 | 0 | 0 | 0 | 18 | 1440 | 0 | 989 | 982 | 996 | -7 | 8731.4101 | 41.5 | 0 | 0 | 24 | 26.8 | 22.1 | 23.2 | 982.83 | 50.1 | 0.9339 | 95.4 | 86.6 |  | 12740.1 | 12652 | -88.1 | 0 | 0 | 0 | 24 | 3.7
| 2017-08-19 | 92.7 | 64.6% | 103 | 83 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3473 | 2946 | 2946 | 2874 | 2974 | 41 | 0 | 41 | 0 | 60 | 0 | 100 | -72 | 126 | 98.35% | 144.7083 | 82.75% | 100% | 87.32% | 8.025 | 137.82 | 1106.0055 | 25.341 | 946 | 23972.586 | 8726.0235 | 122.75 | 0 | 0 | 0 | 0 | 18 | 1440 | 0 | 992 | 984 | 998 | -8 | 8726.0235 | 41.5833 | 0 | 0 | 24 | 26.9 | 22.2 | 23.2 | 984.88 | 50.17 | 0.934 | 95.2 | 86.5 |  | 12735 | 12662 | -73 | 0 | 0 | 0 | 24 | 9.5
Week 34 | 2017-08-20 | 90.2 | 73.8% | 98 | 84 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3495 | 2928 | 2928 | 2859 | 2957 | 41 | 0 | 41 | 0 | 60 | 0 | 98 | -69 | 125 | 98.57% | 145.625 | 81.8% | 100% | 86.62% | 8.002 | 136.9 | 1095.4738 | 25.119 | 945.6 | 23752.5264 | 8691.1508 | 122 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 988 | 977 | 992 | -11 | 8691.1508 | 41.3333 | 0 | 0 | 24 | 26.8 | 22.1 | 23.2 | 986.2 | 50.14 | 0.9342 | 95.7 | 86.7 |  | 12741 | 12678 | -63 | 0 | 0 | 0 | 24 | 10.82
| 2017-08-21 | 92.4 | 69.3% | 99 | 84 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 3470 | 3120 | 3120 | 3049 | 3159 | 41 | 0 | 40 | 0 | 60 | 0 | 110 | -71 | 141 | 93.35% | 144.5833 | 87.87% | 100% | 93.26% | 8.048 | 137.71 | 1108.2901 | 27.261 | 945 | 25761.645 | 8812.7042 | 130 | 0 | 0 | 0 | 0 | 19 | 720 | 0 | 984 | 976 | 1199 | -8 | 8812.7042 | 49.9583 | 1.229 | 1.217 | 22.84 | 26.74 | 22.13 | 23.13 | 984.5 | 50.18 | 0.9337 | 95.16 | 86.54 | 178 | 12780 | 12734 | -46 | 2.446 | 12 | 12 | 23.08 | 11.2
| 2017-08-22 | 93.4 | 67.3% | 101 | 85 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 3461 | 3067 | 3067 | 2990 | 3099 | 39 | 0 | 40 | 0 | 60 | 0 | 109 | -77 | 141 | 91.58% | 144.2083 | 86.39% | 100% | 93.17% | 8.05 | 139.22 | 1120.721 | 26.735 | 945.5 | 25277.9425 | 8828.9844 | 127.7917 | 0 | 0 | 0 | 0 | 19 | 720 | 0 | 932 | 971 | 1196 | 39 | 8828.9844 | 49.8333 | 1.246 | 1.246 | 11.83 | 25.71 | 21.99 | 23.09 | 984.21 | 50.13 | 0.9329 | 90.84 | 86.49 |  | 12967 | 12725 | -242 | 2.492 | 12 | 12 | 11.83 | 2.05
| 2017-08-23 | 93.6 | 68.3% | 102 | 85 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 3458 | 3076 | 3076 | 2997 | 3104 | 39 | 0 | 40 | 0 | 60 | 0 | 107 | -79 | 140 | 92.38% | 144.0833 | 86.67% | 100% | 93.17% | 8.035 | 137.14 | 1101.9199 | 26.912 | 944.5 | 25418.384 | 8848.9503 | 128.1667 | 0 | 0 | 0 | 0 | 19 | 720 | 0 | 943 | 968 | 1193 | 25 | 8848.9503 | 49.7083 | 1.213 | 1.213 | 14.94 | 25.97 | 22.01 | 23.13 | 985.08 | 50.12 | 0.9339 | 91.97 | 86.49 |  | 12942 | 12764 | -178 | 2.426 | 12 | 12 | 15.17 | 3.63
| 2017-08-24 | 94.4 | 66.7% | 103 | 86 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3457 | 2857 | 2857 | 2788 | 2889 | 40 | 0 | 40 | 0 | 60 | 0 | 101 | -69 | 124 | 97.08% | 144.0417 | 80.65% | 100% | 86.43% | 8.03 | 136.96 | 1099.7888 | 24.611 | 946.6864 | 23298.899 | 8751.3227 | 119.0417 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 934 | 972 | 983 | 38 | 8751.3227 | 40.9583 | 0 | 0 | 24 | 25.76 | 21.97 | 23.18 | 983.8 | 50.18 | 0.9339 | 91.25 | 86.5 |  | 12957 | 12721 | -236 | 0 | 0 | 0 | 12.82 | 6.37
| 2017-08-25 | 93.6 | 65.1% | 103 | 86 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3464 | 2926 | 2926 | 2858 | 2960 | 41 | 0 | 41 | 0 | 60 | 0 | 102 | -68 | 126 | 97.88% | 144.3333 | 82.51% | 100% | 86.62% | 8.02 | 133.5 | 1070.67 | 25.178 | 947 | 23843.566 | 8717.3674 | 121.9167 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 989 | 977 | 994 | -12 | 8717.3674 | 41.4167 | 0 | 0 | 24 | 26.76 | 22.16 | 22.99 | 982.6 | 50.19 | 0.9346 | 95.08 | 86.43 |  | 12722 | 12715 | -7 | 0 | 0 | 0 | 24 | 5.93
| 2017-08-26 | 89.3 | 70.7% | 96 | 83 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3505 | 2958 | 2958 | 2884 | 2982 | 42 | 0 | 41 | 0 | 60 | 0 | 98 | -74 | 126 | 98.61% | 146.0417 | 82.28% | 100% | 87.41% | 8.04 | 139.39 | 1120.6956 | 25.378 | 946.9997 | 24032.9597 | 8721.7945 | 123.25 | 0 | 0 | 0 | 0 | 18 | 1440 | 0 | 998 | 985 | 999 | -13 | 8721.7945 | 41.625 | 0 | 0 | 24 | 27.02 | 22.35 | 23.21 | 983.6 | 50.23 | 0.933 | 95.2 | 86.53 |  | 12715 | 12710 | -5 | 0 | 0 | 0 | 24 | 6.2
Week 35 | 2017-08-27 | 92.4 | 65.8% | 100 | 84 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3473 | 2932 | 2932 | 2861 | 2961 | 41 | 0 | 40 | 0 | 60 | 0 | 100 | -71 | 126 | 97.92% | 144.7083 | 82.38% | 100% | 86.52% | 8.015 | 136.18 | 1091.4827 | 25.268 | 946 | 23903.528 | 8736.4595 | 122.1667 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 990 | 976 | 995 | -14 | 8736.4595 | 41.4583 | 0 | 0 | 24 | 26.8 | 22.18 | 23.04 | 983.9 | 50.1 | 0.9342 | 95.1 | 86.4 |  | 12736 | 12746 | 10 | 0 | 0 | 0 | 24 | 6.5
| 2017-08-28 | 90 | 65% | 100 | 84 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3496 | 2965 | 2965 | 2893 | 2994 | 42 | 0 | 41 | 0 | 60 | 0 | 101 | -72 | 127 | 98.23% | 145.6667 | 82.75% | 100% | 87.41% | 8.025 | 140.49 | 1127.4323 | 25.583 | 945 | 24175.935 | 8746.4111 | 123.5417 | 0 | 0 | 0 | 0 | 18 | 1440 | 0 | 1000 | 991 | 1003 | -9 | 8746.4111 | 41.7917 | 0 | 0 | 23.81 | 27.19 | 22.59 | 23.19 | 984.8 | 50.16 | 0.9331 | 94.65 | 86.4 |  | 12769 | 12763 | -6 | 0 | 0 | 0 | 24 | 6.73
| 2017-08-29 | 88 | 70% | 95 | 81 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 3525 | 3155 | 3155 | 3084 | 3190 | 41 | 0 | 41 | 0 | 60 | 0 | 106 | -71 | 141 | 94.27% | 146.875 | 87.49% | 100% | 93.66% | 8 | 138.92 | 1111.36 | 28.048 | 934 | 26196.832 | 8854.7964 | 131.4583 | 0 | 0 | 0 | 0 | 18 | 720 | 0 | 1005 | 991 | 1194 | -14 | 8854.7964 | 49.75 | 1.143 | 1.143 | 24 | 27.6 | 23 | 23.02 | 986.46 | 50.18 | 0.9333 | 94.98 | 86.5 |  | 12929 | 12929 | 0 | 2.286 | 12 | 12 | 24 | 4.6
| 2017-08-30 | 82.9 | 82.1% | 88 | 79 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 3571 | 3161 | 3161 | 3086 | 3191 | 42 | 0 | 42 | 0 | 60 | 0 | 105 | -75 | 142 | 93.63% | 148.7917 | 86.42% | 100% | 93.75% | 8.01 | 133.29 | 1067.6529 | 28.009 | 935 | 26188.415 | 8832.1672 | 131.7083 | 0 | 0 | 0 | 0 | 18 | 720 | 0 | 1008 | 997 | 1186 | -11 | 8832.1672 | 49.4167 | 1.046 | 1.078 | 24 | 27.6 | 23 | 23.3 | 987 | 50.19 | 0.9343 | 95.3 | 86.7 |  | 12838 | 12854 | 16 | 2.124 | 12 | 12 | 24 | 5.17
| 2017-08-31 | 82.6 | 83.4% | 86 | 80 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 10.5 | 0 | 3575 | 3135 | 3135 | 3067 | 3170 | 42 | 0 | 41 | 0 | 60 | 0 | 103 | -68 | 141 | 93.68% | 148.9583 | 85.79% | 100% | 92.92% | 8.02 | 136.14 | 1091.8428 | 27.455 | 942 | 25862.61 | 8788.5402 | 130.625 | 0 | 0 | 0 | 0 | 18 | 810 | 0 | 1009 | 995 | 1166 | -14 | 8788.5402 | 48.5833 | 0.914 | 0.924 | 24 | 27.4 | 22.9 | 23.4 | 987 | 50.17 | 0.9331 | 95.3 | 86.7 |  | 12761 | 12812 | 51 | 1.838 | 10.5 | 10.5 | 24 | 8.43
| 2017-09-01 | [25 empty] | 0 | 0 |  | no data | no data | no data | #DIV/0! | no data |  |  | 0 |  |  | 0 | no data | 0 | [10 empty] | 0 | no data | [15 empty] | 0 | 0
| 2017-09-02 | [25 empty] | 0 | 0 |  | no data | no data | no data | #DIV/0! | no data |  |  | 0 |  |  | 0 | no data | 0 | [10 empty] | 0 | no data | [15 empty] | 0 | 0
| Monthly | 91.8687 | 67.92% | 99.4839 | 84.871 | 744 | 0 | 744 | 0 | 0 | 0 | 0 | 0 | 10.5 | 0 | 107867 | 91966 | 91966 | 89993.39 | 92973 | 41 | 0 | 40.8387 | 0 | 60 | 0 | 2979.61 | -2152 | 128.6452 | 97.23% | 145% | 83.43% | 100% | 88.07% | 249.547 | 137.7087 | 34365.3687 | 793.126 | 944.4608 | 749017.1655 | 8704.8897 |  | 0 | 0 | 0 | 0 | 579 | 40410 | 0 | 30561 | 30417 | 31995 | -144 | 8704.8897 | 1333.125 | 6.791 | 6.821 | 23.3335 | 26.7955 | 22.1265 | 23.2652 | 983.3206 | 50.1361 | 0.93355 | 94.9548 | 86.6039 | 178 | 12774.3903 | 12662.5484 | -111.8419 | 13.612 | 70.5 | 70.5 | 704.23 | 232.78
| Totals | Avg.F | % Avg. | M Avg | m Avg | hrs | min | hrs | min | hrs | min | hrs | min | Avg Int Avi | Avg Ext Avi | MWhr Total | MWhr Total | MWhr Total | MWhr Total | MWhr Total | MW Avg | Total min | Avg MW | Total min | Avg MW | Total min | MWhr | Total MW | Av Max D/Gen | Av. DailyLF | Avg. | Avg. |  | Avg. | Total | Avg. |  | Total | Avg. |  | Avg. | [7 empty] | Total |  |  |  |  | Avg. | [18 empty] | 70.5
| Weeks data | Site Avg. Amb. Temp F | Site Avg. Relative humidity % | Max: Site Maximum/Minumum Temperature; CT1 hrs: CT-1 Base Load Hours; CT2 hrs: CT-2 Base Load Hours; CT1 hrs: CT-1 stand by hours / min; CT2 hrs: CT-2 standby hours / min; CT2 hrs: Plant ambient Corrected maximum Load hours/min | Average Corrected Plant Capacity | Ambient Corrected Declared Avail'y (MWH) | Av Plant WAPDA Dispatch | Net Plant Export (MWH) | Gross Generation | CT1 Av Cap (MW) | CT1 Unavail minutes | CT2 Av Cap (MW) | CT2 Unavail minutes | ST Unavail minutes | ST Average Cap (MW) | Plant Aux Load including Colony Load MWH | Differenece (+/-) MW | Maximum Daily Generation | Daily Load Factor | Avg. Corrected Plant | Plant Capacity Facto | Plant Availability Factor | Equivalent Plant Availability | LBtu gas flow mmscf | 1 LBtu gas (Average Btu/scf) | LBTU MMBTU | PL gas flow (mscf/week) | 1 PL gas (Average Btu/scf) | HBTU MMBTU | Plant Net Heat Rate (Btu/Kwh) | [11 empty] | 23.5
| Week 31 | 93.9214 | 66.62% | 101.4286 | 87.5714 | 168 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 11 | 30 | 3458.4286 | 2937 | 2937 | 2868.1429 | 2970.7143 | 40.8571 | No outage | 40.4286 | No outage | 420 | no data | no data | -482 | 127.1429 | 97.42% | 144.1012 | 82.93% | 100% | 87.47% | 56.352 | 137.9786 | 7775.3685 | 176.767 | 945.1429 | 167070.0674 | 8707.6228
| Week 32 | 94.1643 | 64.27% | 101.5714 | 87.4286 | 168 | -2 | 168 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 3455.8571 | 2923.8571 | 2923.8571 | 20005 | 20714 | 41 | No outage | 287 | no data | 420 | no data | 709 | -462 | 125.1429 | 98.53% | 143.994 | 82.7% | 100% | 86.62% | 56.605 | 137.8471 | 7802.8375 | 175.494 | 945 | 165841.83 | 8680.047 | [5 empty] | 0.27381
| Week 33 | 91.19 | 67.96% | 99.5714 | 82.8571 | 168 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3488.1429 | 2949.5714 | 2949.5714 | 20162 | 20864 | 41.2857 | No outage | 288 | no data | 420 | no data | 702 | -485 | 126.5714 | 98.12% | 145.3393 | 82.57% | 100% | 87.16% | 56.31 | 138.1971 | 7781.8811 | 151.771 | 945.3333 | 143474.1853 | 8691.1035 | [5 empty] | 0.26672
| Week 34 | 92.4143 | 68.74% | 100.2857 | 84.7143 | 168 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 3472.8571 | 2990.2857 | 2990.2857 | 20425 | 21150 | 40.4286 | No outage | 283 | no data | 420 | no data | 725 | -507 | 131.8571 | 95.64% | 144.7024 | 84.02% | 100% | 89.52% | 56.225 | 137.26 | 7717.4435 | 181.194 | 945.898 | 171391.0461 | 8767.4678
| Week 35 | 87.18 | 0.7326 | 93.8 | 81.6 | 120 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 34.5 | 0 | 3528 | 3069.6 | 3069.6 | 14991 | 15506 | 41.6 | #REF! | #REF! | no data | #REF! | no data | 515 | -357 | 135.4 | 95.54% | 147 | 84.97% | #DIV/0! | 90.85% | 40.07 | 137.004 | 5489.7503 | 134.363 | 940.4 | 126354.9652 | 8791.6749
| Date | Plant Status Whether Normal Operation or Tripping (State full detail for trippings/return to normal).
| 2017-08-01 | Plant load restricted to 114~119 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-08-02 | Plant load restricted to 118~121 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-08-03 | Plant load restricted to 117~121 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-08-04 | Plant load restricted to 117~121 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-08-05 | Plant load restricted to 117~121 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-08-06 | Plant load restricted to 118~122 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-08-07 | Plant load restricted to 118~120 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-08-08 | Plant load restricted to 118~121 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-08-09 | Plant load restricted to 117~121 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-08-10 | Plant load restricted to 117~121 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-08-11 | Plant load restricted to 117~121 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-08-12 | Plant load restricted to 117~121 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-08-13 | Plant load restricted to 118~122 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-08-14 | Plant load restricted to 120~124 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-08-15 | Plant load restricted to 119~122 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-08-16 | Plant load restricted to 117~121 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-08-17 | Plant load restricted to 117~122 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-08-18 | Plant load restricted to 117~122 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-08-19 | Plant load restricted to 118~121 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-08-20 | Plant load restricted to 118~121 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-08-21 | Plant load increased from 122 to 135 MW by taking DBs into service at 1100 hrs to achieve maximum export. At 2300 hrs, plant load reduced from 136 to 121 MW by taking duct burners out of service to keep within contractual plant heat rate.
| 2017-08-22 | Plant load increased from 114 to 134 MW by taking DBs into service at 1100 hrs to achieve maximum export. At 2300 hrs, plant load reduced from 136 to 115 MW by taking duct burners out of service to keep within contractual plant heat rate.
| 2017-08-23 | Plant load increased from 120 to 136 MW by taking DBs into service at 1100 hrs to achieve maximum export. At 2300 hrs, plant load reduced from 135 to 115 MW by taking duct burners out of service to keep within contractual plant heat rate.
| 2017-08-24 | Plant load restricted to 113~119 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-08-25 | Plant load restricted to 117~121 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-08-26 | Plant load restricted to 118~122 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-08-27 | Plant load restricted to 118~121 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-08-28 | Plant load restricted to 118~123 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-08-29 | Plant load increased from 121 to 135 MW by taking DBs into service at 1100 hrs to achieve maximum export. At 2300 hrs, plant load reduced from 136 to 122 MW by taking duct burners out of service to keep within contractual plant heat rate.
| 2017-08-30 | Plant load increased from 122 to 136 MW by taking DBs into service at 1100 hrs to achieve maximum export. At 2300 hrs, plant load reduced from 137 to 121 MW by taking duct burners out of service to keep within contractual plant heat rate.
| 2017-08-31 | Plant load increased from 122 to 136 MW by taking DBs into service at 1100 hrs to achieve maximum export. At 2130 hrs, plant load reduced from 136 to 121 MW by taking duct burners out of service to keep within contractual plant heat rate.

## Sep
Monthly Operational Returns Kabirwala
2017-09-01
| Date | Site Avg. Ambient Temp.F | Site Avg. Relative Humidty % | Site Ambient Temp |  | Base load hours |  |  |  | Standby hours |  |  |  | Plant ambient corrected Max Load |  | Corrected Plant Capacity | Ambient Corrected Daclared Avail'y (MWH) | Plant WAPDA Dispatch (MWH) | Net Plant Export (MWH) | Gross Generation | CT1 Average Cap (MW) | CT1 Unavail minutes | CT2 Average Cap (MW) | CT2 Unavail minutes | ST Average Cap (MW) | ST Unavail minutes | Plant Aux Load including Colony Load MWH | Differenece (+/-) MW | Maximum Daily Generation | Daily Load Factor | Avg. Corrected Plant Capacity | Plant Capacity Factor | Plant Availability Factor | Equivalent Plant Availability | LBtu gas flow (mmscf/day) | 1 LBtu gas (Average Btu/scf) | LBTU MMBTU | 1 HBtu gas flow (mmscf/day) | 1 HBtu gas (Average Btu/scf) | HBTU MMBTU | HHV Net Heat Rate (Btu/Kwh) | Avg. declared availability | CT1 Derated MW | CT1 derated mintutes | CT-2 derated MW | CT-2 derated mintutes | ST derated MW | ST derated mintutes | WAPDA Backfeed (MWH) | CT-1 Gross Generation (MWH) | CT-2 Gross Generation (MWH) | STG Gross Generation (MWH) | CT-1 & CT-2 MWH difference | Base load Heat Rate | STG load | DB1 | DB2 | CT1 | CT1 Gas flow | CT2 Gas flow |  | Pamb | Freq. Hz | LBTU Gas Specific gravity | CT-1 compressor efficiency(%) | CT-2 compressor efficiency(%) |  | CT-1 Heat Rate (Btu/Kwh) | CT-2 Heat Rate (Btu/Kwh) |  | DB(1+2) | DB-1 Ops Hours | DB-2 Ops Hours | CT-1 Wetcomprssion Ops Hours | RO Operation Hours
[6 empty] | CT1 |  | CT2 |  | CT1 |  | CT2 | [43 empty] | mmscf/d | mmscf/d | WetC flow | HBTU KPPH | HBTU KPPH | LBTU KPPH | mbar | Hz | [7 empty] | mmscf/d
|  |  |  | Max | Min | hrs | min | hrs | min | hrs | min | hrs | min | hrs | min | [42 empty] | gpm
Week 35 | 2017-08-27 | 92.4 | 65.8% | 100 | 84 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3473 | 2932 | 2932 | 2861 | 2961 | 41 | 0 | 40 | 0 | 60 | 0 | 100 | -71 | 126 | 97.92% | 144.7083 | 82.38% | 100% | 86.52% | 8.036 | 136.18 | 1094.3425 | 25.247 | 946 | 23883.662 | 8730.5154 | 122.1667 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 990 | 976 | 995 | -14 | 8730.5154 | 41.4583 | 0 | 0 | 24 | 26.8 | 22.18 | 23.04 | 983.9 | 50.1 | 0.9342 | 95.1 | 86.4 |  | 12736 | 12746 | 10 | 0 | 0 | 0 | 24 | 6.5
| 2017-08-28 | 90 | 65% | 100 | 84 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3496 | 2965 | 2965 | 2893 | 2994 | 42 | 0 | 41 | 0 | 60 | 0 | 101 | -72 | 127 | 98.23% | 145.6667 | 82.75% | 100% | 87.41% | 8.025 | 140.49 | 1127.4323 | 25.583 | 945 | 24175.935 | 8746.4111 | 123.5417 | 0 | 0 | 0 | 0 | 18 | 1440 | 0 | 1000 | 991 | 1003 | -9 | 8746.4111 | 41.7917 | 0 | 0 | 23.81 | 27.19 | 22.59 | 23.19 | 984.8 | 50.16 | 0.9331 | 94.65 | 86.4 |  | 12769 | 12763 | -6 | 0 | 0 | 0 | 24 | 6.73
| 2017-08-29 | 88 | 70% | 95 | 81 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3525 | 3155 | 3155 | 3084 | 3190 | 41 | 0 | 41 | 0 | 60 | 0 | 106 | -71 | 141 | 94.27% | 146.875 | 87.49% | 100% | 93.66% | 8.022 | 138.92 | 1114.4162 | 28.068 | 934 | 26215.512 | 8861.8444 | 131.4583 | 0 | 0 | 0 | 0 | 18 | 720 | 0 | 1005 | 991 | 1194 | -14 | 8861.8444 | 49.75 | 1.143 | 1.143 | 24 | 27.6 | 23 | 23.02 | 986.46 | 50.18 | 0.9333 | 94.98 | 86.5 |  | 12929 | 12929 | 0 | 2.286 | 12 | 12 | 24 | 4.6
| 2017-08-30 | 82.9 | 82.1% | 88 | 79 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 3571 | 3161 | 3161 | 3086 | 3191 | 42 | 0 | 42 | 0 | 60 | 0 | 105 | -75 | 142 | 93.63% | 148.7917 | 86.42% | 100% | 93.75% | 8.01 | 133.29 | 1067.6529 | 28.009 | 935 | 26188.415 | 8832.1672 | 131.7083 | 0 | 0 | 0 | 0 | 18 | 720 | 0 | 1008 | 997 | 1186 | -11 | 8832.1672 | 49.4167 | 1.046 | 1.078 | 24 | 27.6 | 23 | 23.3 | 987 | 50.19 | 0.9343 | 95.3 | 86.7 |  | 12838 | 12854 | 16 | 2.124 | 12 | 12 | 24 | 5.17
| 2017-08-31 | 82.6 | 83.4% | 86 | 80 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 3575 | 3135 | 3135 | 3067 | 3170 | 42 | 0 | 41 | 0 | 60 | 0 | 103 | -68 | 141 | 93.68% | 148.9583 | 85.79% | 100% | 92.92% | 8.06 | 136.14 | 1097.2884 | 27.59 | 936 | 25824.24 | 8777.8052 | 130.625 | 0 | 0 | 0 | 0 | 18 | 810 | 0 | 1009 | 995 | 1166 | -14 | 8777.8052 | 48.5833 | 0.914 | 0.924 | 24 | 27.4 | 22.9 | 23.4 | 987 | 50.17 | 0.9331 | 95.3 | 86.7 |  | 12761 | 12812 | 51 | 1.838 | 10.5 | 10.5 | 24 | 8.43
| 2017-09-01 | 86.6 | 75.9% | 94 | 79 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 10.5 | 0 | 3530 | 2969 | 2969 | 2901 | 2998 | 42 | 0 | 41 | 0 | 60 | 0 | 97 | -68 | 127 | 98.36% | 147.0833 | 82.18% | 100% | 87.41% | 8.03 | 137.51 | 1104.2053 | 25.271 | 951 | 24032.721 | 8664.9177 | 123.7083 | 0 | 0 | 0 | 0 | 18 | 1440 | 0 | 1005 | 989 | 1004 | -16 | 8664.9177 | 41.8333 | 0 | 0 | 24 | 27 | 22.4 | 23.2 | 985.1 | 50.19 | 0.9332 | 95.2 | 86.6 |  | 12632 | 12690 | 58 | 0 | 0 | 0 | 24 | 6.42
| 2017-09-02 | 87.9 | 74.7% | 97 | 82 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3519 | 2963 | 2963 | 2892 | 2987 | 42 | 0 | 41 | 0 | 60 | 0 | 95 | -71 | 126 | 98.78% | 146.625 | 82.18% | 100% | 87.41% | 7.942 | 143.64 | 1140.7889 | 25.079 | 952 | 23875.208 | 8650.0681 | 123.4583 | 0 | 0 | 0 | 0 | 18 | 1440 | 0 | 999 | 987 | 1001 | -12 | 8650.0681 | 41.7083 | 0 | 0 | 24 | 26.8 | 22.3 | 23.2 | 985.2 | 50.18 | 0.9308 | 95.2 | 86.6 |  | 12606 | 12672 | 66 | 0 | 0 | 0 | 24 | 6.3
Week 36 | 2017-09-03 | 88.7 | 72.6% | 96 | 81 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3514 | 2956 | 2956 | 2886 | 2982 | 42 | 0 | 41 | 0 | 60 | 0 | 96 | -70 | 126 | 98.61% | 146.4167 | 82.13% | 100% | 88.11% | 7.97 | 134.11 | 1068.8567 | 25.171 | 952 | 23962.792 | 8673.4749 | 123.1667 | 0 | 0 | 0 | 0 | 17 | 1440 | 0 | 999 | 983 | 1000 | -16 | 8673.4749 | 41.6667 | 0 | 0 | 24 | 26.92 | 22.47 | 23.12 | 896.17 | 50.19 | 0.9343 | 95.16 | 86.52 |  | 12660 | 12755 | 95 | 0 | 0 | 0 | 24 | 5.57
| 2017-09-04 | 89.6 | 70% | 100 | 81 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3502 | 2964 | 2964 | 2897 | 2993 | 42 | 0 | 41 | 0 | 60 | 0 | 96 | -67 | 128 | 97.43% | 145.9167 | 82.72% | 100% | 87.41% | 7.98 | 136.89 | 1092.3822 | 25.333 | 952 | 24117.016 | 8701.8979 | 123.5 | 0 | 0 | 0 | 0 | 18 | 1440 | 0 | 1002 | 989 | 1002 | -13 | 8701.8979 | 41.75 | 0 | 0 | 24 | 27.07 | 22.59 | 23.27 | 987.21 | 50.2 | 0.9336 | 94.89 | 86.37 |  | 12696 | 12773 | 77 | 0 | 0 | 0 | 24 | 6.63
| 2017-09-05 | 89.3 | 72.7% | 100 | 79 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3506 | 2955 | 2955 | 2888 | 2988 | 42 | 0 | 41 | 0 | 60 | 0 | 100 | -67 | 127 | 98.03% | 146.0833 | 82.37% | 100% | 87.41% | 8 | 138.21 | 1105.68 | 25.321 | 949 | 24029.629 | 8703.3618 | 123.125 | 0 | 0 | 0 | 0 | 18 | 1440 | 0 | 1000 | 986 | 1002 | -14 | 8703.3618 | 41.75 | 0 | 0 | 24 | 27.09 | 22.63 | 23.28 | 987.4 | 50.19 | 0.9332 | 95.25 | 86.42 |  | 12732 | 12829 | 97 | 0 | 0 | 0 | 24 | 5.3
| 2017-09-06 | 90.13 | 68.15% | 99 | 84 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3497 | 2954 | 2954 | 2894 | 2995 | 42 | 0 | 41 | 0 | 60 | 0 | 101 | -60 | 128 | 97.49% | 145.7083 | 82.76% | 100% | 87.41% | 7.95 | 134.45 | 1068.8775 | 25.487 | 946.5 | 24123.4455 | 8705.0183 | 123.0833 | 0 | 0 | 0 | 0 | 18 | 1440 | 0 | 1005 | 986 | 1004 | -19 | 8705.0183 | 41.8333 | 0 | 0 | 24 | 27.16 | 22.16 | 23.15 | 987.7 | 50.22 | 0.9348 | 95.37 | 86.33 |  | 12709 | 12805 | 96 | 0 | 0 | 0 | 24 | 5.42
| 2017-09-07 | 87.29 | 65.42% | 98 | 78 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3524 | 2995 | 2995 | 2928 | 3025 | 42 | 0 | 42 | 0 | 60 | 0 | 97 | -67 | 128 | 98.47% | 146.8333 | 83.09% | 100% | 87.5% | 8.002 | 132.55 | 1060.6651 | 25.708 | 945 | 24294.06 | 8659.4006 | 124.7917 | 0 | 0 | 0 | 0 | 18 | 1440 | 0 | 1012 | 999 | 1014 | -13 | 8659.4006 | 42.25 | 0 | 0 | 24 | 27.33 | 22.92 | 22.85 | 988.9 | 50.14 | 0.9356 | 94.81 | 86.24 |  | 12688 | 12765 | 77 | 0 | 0 | 0 | 23.15 | 6.08
| 2017-09-08 | 91 | 63% | 100 | 80 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3494 | 2986 | 2986 | 2913 | 3012 | 42 | 0 | 41 | 0 | 60 | 0 | 99 | -73 | 128 | 98.05% | 145.5833 | 83.37% | 100% | 87.41% | 8 | 132.95 | 1063.6 | 25.611 | 944 | 24176.784 | 8664.7388 | 124.4167 | 0 | 0 | 0 | 0 | 18 | 1440 | 0 | 1010 | 992 | 1010 | -18 | 8664.7388 | 42.0833 | 0 | 0 | 23.54 | 27.31 | 22.89 | 22.48 | 989.33 | 50.19 | 0.9355 | 95.01 | 86.22 |  | 12716 | 12815 | 99 | 0 | 0 | 0 | 24 | 6.12
| 2017-09-09 | 92 | 62% | 102 | 82 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3473 | 2967 | 2967 | 2896 | 2993 | 41 | 0 | 41 | 0 | 60 | 0 | 97 | -71 | 127 | 98.2% | 144.7083 | 83.39% | 100% | 87.32% | 7.975 | 128.15 | 1021.9963 | 25.529 | 943 | 24073.847 | 8665.6917 | 123.625 | 0 | 0 | 0 | 0 | 18 | 1440 | 0 | 1003 | 986 | 1004 | -17 | 8665.6917 | 41.8333 | 0 | 0 | 24 | 27.2 | 22.83 | 22.37 | 987.4 | 50.15 | 0.937 | 95.17 | 86.31 |  | 12752 | 12860 | 108 | 0 | 0 | 0 | 24 | 6
Week 37 | 2017-09-10 | 91 | 64% | 101 | 82 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3488 | 2968 | 2968 | 2903 | 3000 | 42 | 0 | 41 | 0 | 60 | 0 | 97 | -65 | 127 | 98.43% | 145.3333 | 83.23% | 100% | 87.41% | 7.95 | 128.43 | 1021.0185 | 25.645 | 941 | 24131.945 | 8664.4724 | 123.6667 | 0 | 0 | 0 | 0 | 18 | 1440 | 0 | 1004 | 990 | 1006 | -14 | 8664.4724 | 41.9167 | 0 | 0 | 24 | 27.3 | 23 | 22.01 | 987.4 | 50.18 | 0.9371 | 94.93 | 86.31 |  | 12782 | 12855 | 73 | 0 | 0 | 0 | 24 | 6.35
| 2017-09-11 | 88 | 67.6% | 97 | 79 | 21 | 55 | 22 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 3517 | 2926 | 2926 | 2635 | 2728 | 42 | 105 | 41 | 73 | 60 | 108 | 93 | -291 | 129 | 88.11% | 146.5417 | 74.92% | 93.26% | 81.19% | 7.9 | 130.03 | 1027.237 | 23.381 | 941 | 22001.521 | 8739.5666 | 121.9167 | 23 | 20 | 20 | 21 | 18 | 1332 | 0 | 879 | 935 | 914 | 56 | 8739.5666 | 38.0833 | 0 | 0 | 24 | 24.5 | 21.9 | 21 | 990.67 | 50.07 | 0.9365 | 87.5 | 86.6 |  | 13271 | 13008 | -263 | 0 | 0 | 0 | 11.1 | 6.5
| 2017-09-12 | 91.3 | 63.9% | 100 | 82 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3485 | 2906 | 2906 | 2842 | 2942 | 40 | 0 | 41 | 0 | 60 | 0 | 100 | -64 | 125 | 98.07% | 145.2083 | 81.55% | 100% | 87.23% | 7.844 | 126.87 | 995.1683 | 25.299 | 941 | 23806.359 | 8726.7865 | 121.0833 | 0 | 0 | 0 | 0 | 18 | 1440 | 0 | 958 | 984 | 1000 | 26 | 8726.7865 | 41.6667 | 0 | 0 | 24 | 26.4 | 22.9 | 22.2 | 990.2 | 50.17 | 0.9378 | 90.9 | 86.5 |  | 12975 | 12901 | -74 | 0 | 0 | 0 | 15.28 | 2.55
| 2017-09-13 | 90.5 | 61.1% | 104 | 81 | 18 | 55 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3495 | 2654 | 2654 | 2593 | 2692 | 40 | 274 | 41 | 0 | 60 | 0 | 99 | -61 | 130 | 86.28% | 145.625 | 74.19% | 94.6% | 78.72% | 7.852 | 127.33 | 999.7952 | 22.971 | 942 | 21638.682 | 8730.6121 | 110.5833 | 18 | 31 | 0 | 0 | 22 | 1440 | 0 | 801 | 992 | 899 | 191 | 8730.6121 | 37.4583 | 0 | 0 | 24.4 | 22 | 23 | 22.1 | 989.9 | 50.18 | 0.9376 | 95.1 | 86.3 |  | 12785 | 12843 | 58 | 0 | 0 | 0 | 17.82 | 4
| 2017-09-14 | 87.5 | 56.8% | 97 | 77 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3521 | 3019 | 3019 | 2951 | 3049 | 42 | 0 | 42 | 0 | 60 | 0 | 98 | -68 | 130 | 97.72% | 146.7083 | 83.81% | 100% | 87.5% | 7.858 | 127.74 | 1003.7809 | 25.944 | 943 | 24465.192 | 8630.6245 | 125.7917 | 0 | 0 | 0 | 0 | 18 | 1440 | 0 | 1024 | 1005 | 1020 | -19 | 8630.6245 | 42.5 | 0 | 0 | 24 | 27.59 | 23.11 | 22.16 | 990.25 | 50.17 | 0.9376 | 95.83 | 86.32 |  | 12624 | 12740 | 116 | 0 | 0 | 0 | 24 | 7
| 2017-09-15 | 88.2 | 62% | 99 | 80 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3514 | 3002 | 3002 | 2929 | 3028 | 42 | 0 | 41 | 0 | 60 | 0 | 99 | -73 | 128 | 98.57% | 146.4167 | 83.35% | 100% | 87.41% | 7.866 | 127.31 | 1001.4205 | 25.831 | 943 | 24358.633 | 8658.2634 | 125.0833 | 0 | 0 | 0 | 0 | 18 | 1440 | 0 | 1014 | 998 | 1016 | -16 | 8658.2634 | 42.3333 | 0 | 0 | 24 | 27.5 | 23.04 | 22.21 | 989.63 | 50.18 | 0.9376 | 96.29 | 86.41 |  | 12729 | 12800 | 71 | 0 | 0 | 0 | 24 | 6.56
| 2017-09-16 | 89.7 | 60.8% | 98 | 78 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3500 | 2983 | 2983 | 2917 | 3017 | 42 | 0 | 41 | 0 | 60 | 0 | 100 | -66 | 128 | 98.21% | 145.8333 | 83.34% | 100% | 87.41% | 7.835 | 126.36 | 990.0306 | 25.761 | 944 | 24318.384 | 8676.1792 | 124.2917 | 0 | 0 | 0 | 0 | 18 | 1440 | 0 | 1012 | 993 | 1012 | -19 | 8676.1792 | 42.1667 | 0 | 0 | 24 | 27.42 | 23 | 22.13 | 988.96 | 50.18 | 0.9385 | 96.36 | 86.39 |  | 12753 | 12836 | 83 | 0 | 0 | 0 | 24 | 6.38
Week 38 | 2017-09-17 | 90.49 | 62.23% | 101 | 81 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3492 | 2971 | 2971 | 2903 | 3001 | 42 | 0 | 41 | 0 | 60 | 0 | 98 | -68 | 127 | 98.46% | 145.5 | 83.13% | 100% | 87.41% | 7.886 | 125.88 | 992.6897 | 25.611 | 944 | 24176.784 | 8670.1597 | 123.7917 | 0 | 0 | 0 | 0 | 18 | 1440 | 0 | 1005 | 988 | 1008 | -17 | 8670.1597 | 42 | 0 | 0 | 24 | 27.31 | 22.94 | 22.11 | 988.88 | 50.14 | 0.9379 | 96.58 | 86.41 |  | 12764 | 12870 | 106 | 0 | 0 | 0 | 24 | 6.8
| 2017-09-18 | 90.36 | 59.96% | 102 | 79 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 3498 | 3169 | 3169 | 3110 | 3216 | 42 | 0 | 41 | 0 | 60 | 0 | 106 | -59 | 144 | 93.06% | 145.75 | 88.91% | 100% | 93.71% | 7.874 | 128.42 | 1011.1791 | 27.972 | 944 | 26405.568 | 8815.6743 | 132.0417 | 0 | 0 | 0 | 0 | 18 | 720 | 0 | 1007 | 991 | 1218 | -16 | 8815.6743 | 50.75 | 1.204 | 1.179 | 24 | 27.25 | 22.98 | 22.08 | 987.6 | 50.14 | 0.937 | 96.37 | 86.32 |  | 12707 | 12837 | 130 | 2.383 | 12 | 12 | 24 | 5.47
| 2017-09-19 | 88.89 | 59.12% | 102 | 77 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 3509 | 3183 | 3183 | 3116 | 3223 | 42 | 0 | 42 | 0 | 60 | 0 | 107 | -67 | 143 | 93.91% | 146.2083 | 88.8% | 100% | 94.1% | 7.863 | 125.79 | 989.0868 | 27.969 | 946 | 26458.674 | 8808.6524 | 132.625 | 0 | 0 | 0 | 0 | 17 | 720 | 0 | 1014 | 995 | 1214 | -19 | 8808.6524 | 50.5833 | 1.168 | 1.158 | 24 | 27.39 | 23.06 | 22.18 | 986.3 | 50.18 | 0.9377 | 96.12 | 86.24 |  | 12687 | 12818 | 131 | 2.326 | 12 | 12 | 24 | 5.93
| 2017-09-20 | 87.2 | 62.6% | 100 | 77 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 3526 | 3174 | 3174 | 3104 | 3212 | 42 | 0 | 41 | 0 | 60 | 0 | 108 | -70 | 142 | 94.25% | 146.9167 | 88.03% | 100% | 93.71% | 7.87 | 124.97 | 983.5139 | 27.824 | 947 | 26349.328 | 8805.6836 | 132.25 | 0 | 0 | 0 | 0 | 18 | 720 | 0 | 1014 | 996 | 1202 | -18 | 8805.6836 | 50.0833 | 1.095 | 1.082 | 24 | 27.32 | 23.03 | 22.06 | 986 | 50.1 | 0.938 | 96.33 | 86.34 |  | 12668 | 12804 | 136 | 2.177 | 12 | 12 | 24 | 5.8
| 2017-09-21 | 87 | 63% | 99 | 76 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 3527 | 3182 | 3182 | 3113 | 3218 | 42 | 0 | 41 | 0 | 60 | 0 | 105 | -69 | 143 | 93.76% | 146.9583 | 88.26% | 100% | 94.06% | 7.89 | 126.25 | 996.1125 | 27.883 | 947 | 26405.201 | 8802.2208 | 132.5833 | 0 | 0 | 0 | 0 | 17 | 720 | 0 | 1012 | 995 | 1211 | -17 | 8802.2208 | 50.4583 | 1.152 | 1.124 | 24 | 27.27 | 23.02 | 22.16 | 986.1 | 50.17 | 0.9376 | 96.28 | 86.34 |  | 12644 | 12793 | 149 | 2.276 | 12 | 12 | 24 | 5.8
| 2017-09-22 | 87 | 61% | 100 | 77 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 3519 | 3187 | 3187 | 3120 | 3228 | 42 | 0 | 41 | 0 | 60 | 0 | 108 | -67 | 143 | 94.06% | 146.625 | 88.66% | 100% | 94.06% | 7.885 | 125.92 | 992.8792 | 27.951 | 947 | 26469.597 | 8802.0757 | 132.7917 | 0 | 0 | 0 | 0 | 17 | 720 | 0 | 1016 | 999 | 1213 | -17 | 8802.0757 | 50.5417 | 1.143 | 1.133 | 24 | 27.3 | 23.08 | 22.1 | 986.9 | 50.15 | 0.9378 | 96.26 | 86.31 |  | 12655 | 12795 | 140 | 2.276 | 12 | 12 | 24 | 7.6
| 2017-09-23 | 88 | 62.5% | 101 | 79 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3518 | 2981 | 2981 | 2915 | 3013 | 42 | 0 | 41 | 0 | 60 | 0 | 98 | -66 | 129 | 97.32% | 146.5833 | 82.86% | 100% | 87.41% | 7.88 | 125.75 | 990.91 | 25.688 | 947 | 24326.536 | 8685.2302 | 124.2083 | 0 | 0 | 0 | 0 | 18 | 1440 | 0 | 1009 | 993 | 1011 | -16 | 8685.2302 | 42.125 | 0 | 0 | 24 | 27.2 | 23 | 22 | 988.3 | 50.07 | 0.9377 | 96.4 | 86.3 |  | 12688 | 12815 | 127 | 0 | 0 | 0 | 24 | 6.72
Week 39 | 2017-09-24 | 88.2 | 68.8% | 100 | 79 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3514 | 2964 | 2964 | 2891 | 2990 | 42 | 0 | 41 | 0 | 60 | 0 | 99 | -73 | 126 | 98.88% | 146.4167 | 82.27% | 100% | 87.41% | 7.89 | 126.13 | 995.1657 | 25.588 | 946 | 24206.248 | 8717.196 | 123.5 | 0 | 0 | 0 | 0 | 18 | 1440 | 0 | 1002 | 984 | 1004 | -18 | 8717.196 | 41.8333 | 0 | 0 | 24 | 27.2 | 22.9 | 22.1 | 989.6 | 50.09 | 0.9377 | 97.1 | 86.4 |  | 12751 | 12884 | 133 | 0 | 0 | 0 | 24 | 6.45
| 2017-09-25 | 88.1 | 64.9% | 100 | 78 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3515 | 2978 | 2978 | 2914 | 3012 | 42 | 0 | 41 | 0 | 60 | 0 | 98 | -64 | 128 | 98.05% | 146.4583 | 82.9% | 100% | 87.41% | 7.9 | 126.25 | 997.375 | 25.763 | 946 | 24371.798 | 8705.9619 | 124.0833 | 0 | 0 | 0 | 0 | 18 | 1440 | 0 | 1010 | 991 | 1011 | -19 | 8705.9619 | 42.125 | 0 | 0 | 24 | 27.4 | 23.1 | 22.1 | 988.6 | 50.12 | 0.9375 | 96.8 | 86.3 |  | 12751 | 12888 | 137 | 0 | 0 | 0 | 24 | 6.43
| 2017-09-26 | 88.2 | 62.8% | 101 | 76 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 3512 | 3184 | 3184 | 3109 | 3215 | 42 | 0 | 41 | 0 | 60 | 0 | 106 | -75 | 142 | 94.34% | 146.3333 | 88.53% | 100% | 93.71% | 7.91 | 129.76 | 1026.4016 | 28.025 | 946 | 26511.65 | 8857.5271 | 132.6667 | 0 | 0 | 0 | 0 | 18 | 720 | 0 | 1009 | 990 | 1216 | -19 | 8857.5271 | 50.6667 | 1.164 | 1.164 | 24 | 27.32 | 22.96 | 22.32 | 988.67 | 50.08 | 0.9365 | 96.72 | 86.27 |  | 12724 | 12859 | 135 | 2.328 | 12 | 12 | 24 | 6.6
| 2017-09-27 | 88.3 | 62.4% | 101 | 76 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3516 | 2981 | 2981 | 2914 | 3016 | 42 | 0 | 41 | 0 | 60 | 0 | 102 | -67 | 128 | 98.18% | 146.5 | 82.88% | 100% | 87.41% | 7.925 | 129.08 | 1022.959 | 25.751 | 946 | 24360.446 | 8710.8459 | 124.2083 | 0 | 0 | 0 | 0 | 18 | 1440 | 0 | 1009 | 992 | 1015 | -17 | 8710.8459 | 42.2917 | 0 | 0 | 24 | 27.32 | 22.87 | 22.39 | 989.25 | 50.1 | 0.9367 | 96.67 | 86.24 |  | 12710 | 12810 | 100 | 0 | 0 | 0 | 24 | 6.75
| 2017-09-28 | 86.9 | 62% | 102 | 74 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 3527 | 3190 | 3190 | 3124 | 3231 | 42 | 0 | 41 | 0 | 60 | 0 | 107 | -66 | 143 | 94.14% | 146.9583 | 88.57% | 100% | 93.71% | 7.935 | 129.03 | 1023.853 | 28.174 | 945 | 26624.43 | 8850.2827 | 132.9167 | 0 | 0 | 0 | 0 | 18 | 720 | 0 | 1016 | 997 | 1218 | -19 | 8850.2827 | 50.75 | 1.156 | 1.154 | 24 | 27.48 | 23.09 | 22.31 | 988.71 | 50.11 | 0.9366 | 96.46 | 86.23 |  | 12729 | 12848 | 119 | 2.31 | 12 | 12 | 24 | 6.5
| 2017-09-29 | 87.18 | 57% | 100 | 74 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 3524 | 3203 | 3203 | 3137 | 3243 | 43 | 0 | 42 | 0 | 60 | 0 | 106 | -66 | 143 | 94.49% | 146.8333 | 89.02% | 100% | 94.14% | 7.925 | 126.57 | 1003.0672 | 28.19 | 939.007 | 26470.6065 | 8757.9451 | 133.4583 | 0 | 0 | 0 | 0 | 17 | 720 | 0 | 1023 | 1007 | 1213 | -16 | 8757.9451 | 50.5417 | 1.084 | 1.082 | 24 | 27.64 | 23.27 | 22.19 | 987.96 | 50.15 | 0.9374 | 95.94 | 86.09 |  | 12696 | 12787 | 91 | 2.166 | 12 | 12 | 24 | 6.33
| 2017-09-30 | 85.38 | 58.83% | 100 | 72 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 3543 | 3107 | 3107 | 3043 | 3141 | 43 | 0 | 42 | 0 | 60 | 0 | 98 | -64 | 143 | 91.52% | 147.625 | 85.89% | 100% | 90.72% | 7.92 | 128.62 | 1018.6704 | 26.941 | 945 | 25459.245 | 8701.2538 | 129.4583 | 0 | 0 | 0 | 0 | 17 | 1140 | 0 | 1025 | 1010 | 1106 | -15 | 8701.2538 | 46.0833 | 0.463 | 0.463 | 24 | 27.61 | 23.21 | 22.12 | 990 | 50.12 | 0.9368 | 95.81 | 86.1 |  | 12655 | 12721 | 66 | 0.926 | 5 | 5 | 24 | 5.95
| Monthly | 88.664 | 64.26% | 99.7 | 78.6667 | 712 | 50 | 718 | 46 | 0 | 0 | 0 | 0 | 51.5 | 0 | 105319 | 90621 | 90621 | 88550.83 | 91388 | 41.9 | 379 | 41.1667 | 73 | 60 | 108 | 2837.17 | -2243 | 132.2 | 96.11% | 146.2764 | 84.08% | 99.6% | 88.77% | 237.507 | 129.6983 | 30809.366 | 782.672 | 945.4836 | 740002.33 | 8704.7371 | 125.8625 | 41 | 51 | 20 | 21 | 558 | 37422 | 0 | 30872 | 30688 | 32995 | -184 | 8704.7371 | 1374.7917 | 11.185 | 11.139 | 23.9981 | 26.9984 | 22.841 | 22.4632 | 985.0577 | 50.1539 | 0.93613 | 95.3755 | 86.3884 | #DIV/0! | 12745.6774 | 12824.6129 | 78.9355 | 19.168 | 101 | 101 | 691.35 | 182.31
| Totals | Avg.F | % Avg. | M Avg | m Avg | hrs | min | hrs | min | hrs | min | hrs | min | Avg Int Avi | Avg Ext Avi | MWhr Total | MWhr Total | MWhr Total | MWhr Total | MWhr Total | MW Avg | Total min | Avg MW | Total min | Avg MW | Total min | MWhr | Total MW | Av Max D/Gen | Av. DailyLF | Avg. | Avg. |  | Avg. | Total | Avg. |  | Total | Avg. |  | Avg. | [7 empty] | Total |  |  |  |  | Avg.
| Weeks data | Site Avg. Amb. Temp F | Site Avg. Relative humidity % | Max: Site Maximum/Minumum Temperature; CT1 hrs: CT-1 Base Load Hours; CT2 hrs: CT-2 Base Load Hours; CT1 hrs: CT-1 stand by hours / min; CT2 hrs: CT-2 standby hours / min; CT2 hrs: Plant ambient Corrected maximum Load hours/min | Average Corrected Plant Capacity | Ambient Corrected Declared Avail'y (MWH) | Av Plant WAPDA Dispatch | Net Plant Export (MWH) | Gross Generation | CT1 Av Cap (MW) | CT1 Unavail minutes | CT2 Av Cap (MW) | CT2 Unavail minutes | ST Unavail minutes | ST Average Cap (MW) | Plant Aux Load including Colony Load MWH | Differenece (+/-) MW | Maximum Daily Generation | Daily Load Factor | Avg. Corrected Plant | Plant Capacity Facto | Plant Availability Factor | Equivalent Plant Availability | LBtu gas flow mmscf | 1 LBtu gas (Average Btu/scf) | LBTU MMBTU | PL gas flow (mscf/week) | 1 PL gas (Average Btu/scf) | HBTU MMBTU | Plant Net Heat Rate (Btu/Kwh) | [11 empty] | -17.5
| Week 35 | 87.2 | 73.84% | 94.2857 | 81.2857 | 168 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 34.5 | 0 | 3527 | 3040 | 3040 | 2969.1429 | 3070.1429 | 41.7143 | No outage | 41 | No outage | 420 | no data | no data | -496 | 132.8571 | 96.41% | 146.9583 | 84.17% | 100% | 89.87% | 56.125 | 138.0243 | 7746.613 | 184.847 | 942.7143 | 174257.9076 | 8751.9613
| Week 36 | 89.7171 | 67.7% | 99.2857 | 80.7143 | 168 | -2 | 168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3501.4286 | 2968.1429 | 2968.1429 | 20302 | 20988 | 41.8571 | No outage | 288 | no data | 420 | no data | 686 | -475 | 127.4286 | 98.04% | 145.8929 | 82.83% | 100% | 87.51% | 55.877 | 133.9014 | 7482.0101 | 178.16 | 947.3571 | 168781.1486 | 8681.9406 | [5 empty] | 0.27381
| Week 37 | 89.4571 | 62.31% | 99.4286 | 79.8571 | 160 | 110 | 166 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 3502.8571 | 2922.5714 | 2922.5714 | 19770 | 20456 | 41.4286 | 379 | 288 | no data | 420 | no data | 686 | -688 | 128.1429 | 95.06% | 145.9524 | 80.63% | 98.27% | 85.27% | 55.105 | 127.7243 | 7038.2468 | 149.071 | 941.8333 | 140400.0368 | 8689.5007 | [5 empty] | 0.26672
| Week 38 | 88.42 | 61.49% | 100.7143 | 78 | 168 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 3512.7143 | 3121 | 3121 | 21381 | 22111 | 42 | No outage | 288 | no data | 420 | no data | 730 | -466 | 138.7143 | 94.97% | 146.3631 | 86.95% | 100% | 92.06% | 55.148 | 126.14 | 6956.3687 | 190.898 | 946 | 180589.508 | 8769.9567
| Week 39 | 87.4657 | 0.6239 | 100.5714 | 75.5714 | 168 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 3521.5714 | 3086.7143 | 3086.7143 | 21132 | 21848 | 42.2857 | #REF! | #REF! | no data | #REF! | no data | 716 | -475 | 136.1429 | 95.66% | 146.7321 | 85.72% | 100% | 90.64% | 55.405 | 127.92 | 7087.4076 | 188.432 | 944.7153 | 178014.5899 | 8757.2875
| Date | Plant Status Whether Normal Operation or Tripping (State full detail for trippings/return to normal).
| 2017-09-01 | Plant load restricted to 119~123 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-09-02 | Plant load restricted to 119~122 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-09-03 | Plant load restricted to 118~122 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-09-04 | Plant load restricted to 118~123 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-09-05 | Plant load restricted to 118~123 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-09-06 | Plant load restricted to 118~123 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-09-07 | Plant load restricted to 119~124 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-09-08 | Plant load restricted to 119~124 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-09-09 | Plant load restricted to 119~123 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-09-10 | Plant load restricted to 119~123 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-09-11 | Plant tripped at 1026hrs due to WAPDA supply failure. After restoration of WAPDA supply at 1042hrs, CT-2 synch @ 1139hrs, CT-1 synch @ 1211hrs and STG synch @ 1214hrs.
| 2017-09-12 | Plant load restricted to 115~120 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-09-13 | Gas turbine CT-1 de-synch @ 0619 hrs for Inspection of wet compression system spray nozzles & synch @ 1053 hrs.
| 2017-09-14 | Plant load restricted to 121~126 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-09-15 | Plant load restricted to 120~123 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-09-16 | Plant load restricted to 119~124 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-09-17 | Plant load restricted to 119~123 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-09-18 | Plant load increased from 121 to 136 MW by taking DBs into service at 1100 hrs to achieve maximum export. At 2300 hrs, plant load reduced from 139 to 123 MW by taking duct burners out of service to keep within contractual plant heat rate.
| 2017-09-19 | Plant load increased from 121 to 135 MW by taking DBs into service at 1100 hrs to achieve maximum export. At 2300 hrs, plant load reduced from 138 to 123 MW by taking duct burners out of service to keep within contractual plant heat rate.
| 2017-09-20 | Plant load increased from 122 to 136 MW by taking DBs into service at 1100 hrs to achieve maximum export. At 2300 hrs, plant load reduced from 136 to 124 MW by taking duct burners out of service to keep within contractual plant heat rate.
| 2017-09-21 | Plant load increased from 121 to 136 MW by taking DBs into service at 1100 hrs to achieve maximum export. At 2300 hrs, plant load reduced from 138 to 125 MW by taking duct burners out of service to keep within contractual plant heat rate.
| 2017-09-22 | Plant load increased from 122 to 136 MW by taking DBs into service at 1100 hrs to achieve maximum export. At 2300 hrs, plant load reduced from 138 to 124 MW by taking duct burners out of service to keep within contractual plant heat rate.
| 2017-09-23 | Plant load restricted to 119~124 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-09-24 | Plant load restricted to 118~122 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-09-25 | Plant load restricted to 119~124 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-09-26 | Plant load increased from 122 to 137 MW by taking DBs into service at 1100 hrs to achieve maximum export. At 2300 hrs, plant load reduced from 138 to 122 MW by taking duct burners out of service to keep within contractual plant heat rate.
| 2017-09-27 | Plant load restricted to 119~124 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-09-28 | Plant load increased from 123 to 137 MW by taking DBs into service at 1100 hrs to achieve maximum export. At 2300 hrs, plant load reduced from 139 to 124 MW by taking duct burners out of service to keep within contractual plant heat rate.
| 2017-09-29 | Plant load increased from 123 to 138 MW by taking DBs into service at 1100 hrs to achieve maximum export. At 2300 hrs, plant load reduced from 140 to 125 MW by taking duct burners out of service to keep within contractual plant heat rate.
| 2017-09-30 | Plant load increased from 122 to 135 MW by taking DBs into service at 1800 hrs to achieve maximum export. At 2300 hrs, plant load reduced from 139 to 126 MW by taking duct burners out of service to keep within contractual plant heat rate.

## Oct
Monthly Operational Returns Kabirwala
2017-10-01
| Date | Site Avg. Ambient Temp.F | Site Avg. Relative Humidty % | Site Ambient Temp |  | Base load hours |  |  |  | Standby hours |  |  |  | Plant ambient corrected Max Load |  | Corrected Plant Capacity | Ambient Corrected Daclared Avail'y (MWH) | Plant WAPDA Dispatch (MWH) | Net Plant Export (MWH) | Gross Generation | CT1 Average Cap (MW) | CT1 Unavail minutes | CT2 Average Cap (MW) | CT2 Unavail minutes | ST Average Cap (MW) | ST Unavail minutes | Plant Aux Load including Colony Load MWH | Differenece (+/-) MW | Maximum Daily Generation | Daily Load Factor | Avg. Corrected Plant Capacity | Plant Capacity Factor | Plant Availability Factor | Equivalent Plant Availability | LBtu gas flow (mmscf/day) | 1 LBtu gas (Average Btu/scf) | LBTU MMBTU | 1 HBtu gas flow (mmscf/day) | 1 HBtu gas (Average Btu/scf) | HBTU MMBTU | HHV Net Heat Rate (Btu/Kwh) | Avg. declared availability | CT1 Derated MW | CT1 derated mintutes | CT-2 derated MW | CT-2 derated mintutes | ST derated MW | ST derated mintutes | WAPDA Backfeed (MWH) | CT-1 Gross Generation (MWH) | CT-2 Gross Generation (MWH) | STG Gross Generation (MWH) | CT-1 & CT-2 MWH difference | Base load Heat Rate | STG load | DB1 | DB2 | CT1 | CT1 Gas flow | CT2 Gas flow |  | Pamb | Freq. Hz | LBTU Gas Specific gravity | CT-1 compressor efficiency(%) | CT-2 compressor efficiency(%) |  | CT-1 Heat Rate (Btu/Kwh) | CT-2 Heat Rate (Btu/Kwh) |  | DB(1+2) | DB-1 Ops Hours | DB-2 Ops Hours | CT-1 Wetcomprssion Ops Hours | RO Operation Hours
[6 empty] | CT1 |  | CT2 |  | CT1 |  | CT2 | [43 empty] | mmscf/d | mmscf/d | WetC flow | HBTU KPPH | HBTU KPPH | LBTU KPPH | mbar | Hz | [7 empty] | mmscf/d
|  |  |  | Max | Min | hrs | min | hrs | min | hrs | min | hrs | min | hrs | min | [42 empty] | gpm
Week 40 | 2017-10-01 | 86.13 | 55.49% | 99 | 72 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3535 | 3038 | 3038 | 2972 | 3070 | 43 | 0 | 42 | 0 | 60 | 0 | 98 | -66 | 132 | 96.91% | 147.2917 | 84.07% | 100% | 88.28% | 7.93 | 127.55 | 1011.4715 | 26.045 | 946 | 24638.57 | 8630.5658 | 126.5833 | 0 | 0 | 0 | 0 | 17 | 1440 | 0 | 1027 | 1013 | 1030 | -14 | 8630.5658 | 42.9167 | 0 | 0 | 24 | 27.59 | 23.21 | 22.21 | 989.2 | 50.14 | 0.937 | 95.56 | 86.06 |  | 12638 | 12692 | 54 | 0 | 0 | 0 | 24 | 6.15
| 2017-10-02 | 86 | 58% | 100 | 74 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3542 | 3031 | 3031 | 2962 | 3057 | 43 | 0 | 42 | 0 | 60 | 0 | 95 | -69 | 130 | 97.98% | 147.5833 | 83.63% | 100% | 88.28% | 7.935 | 126.66 | 1005.0471 | 25.931 | 947 | 24556.657 | 8629.8798 | 126.2917 | 0 | 0 | 0 | 0 | 17 | 1440 | 0 | 1023 | 1008 | 1026 | -15 | 8629.8798 | 42.75 | 0 | 0 | 24 | 27.54 | 23.21 | 22.05 | 989.25 | 50.11 | 0.9374 | 95.8 | 86.14 |  | 12652 | 12729 | 77 | 0 | 0 | 0 | 24 | 6
| 2017-10-03 | 86 | 61% | 98 | 76 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3534 | 3016 | 3016 | 2948 | 3047 | 43 | 0 | 42 | 0 | 60 | 0 | 99 | -68 | 129 | 98.42% | 147.25 | 83.42% | 100% | 88.28% | 7.92 | 126.38 | 1000.9296 | 25.898 | 943.75 | 24441.2375 | 8630.3145 | 125.6667 | 0 | 0 | 0 | 0 | 17 | 1440 | 0 | 1018 | 1006 | 1023 | -12 | 8630.3145 | 42.625 | 0 | 0 | 24 | 27.55 | 23.14 | 22.22 | 990.08 | 50.11 | 0.9374 | 95.74 | 86.11 |  | 12712 | 12742 | 30 | 0 | 0 | 0 | 24 | 6.7
| 2017-10-04 | 86 | 57% | 99 | 75 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3535 | 3045 | 3045 | 2982 | 3077 | 43 | 0 | 42 | 0 | 60 | 0 | 95 | -63 | 131 | 97.87% | 147.2917 | 84.36% | 100% | 88.28% | 7.916 | 128.42 | 1016.5727 | 26.171 | 945.889 | 24754.861 | 8642.3319 | 126.875 | 0 | 0 | 0 | 0 | 17 | 1440 | 0 | 1029 | 1017 | 1031 | -12 | 8642.3319 | 42.9583 | 0 | 0 | 24 | 27.72 | 23.33 | 22.17 | 991.5 | 50.13 | 0.9368 | 95.16 | 85.96 |  | 12661 | 12684 | 23 | 0 | 0 | 0 | 24 | 6.22
| 2017-10-05 | 85 | 56.5% | 98 | 73 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3545 | 3041 | 3041 | 2975 | 3073 | 43 | 0 | 42 | 0 | 60 | 0 | 98 | -66 | 131 | 97.74% | 147.7083 | 83.92% | 100% | 88.28% | 7.918 | 127.88 | 1012.5538 | 25.978 | 950 | 24679.1 | 8635.85 | 126.7083 | 0 | 0 | 0 | 0 | 17 | 1440 | 0 | 1027 | 1015 | 1031 | -12 | 8635.85 | 42.9583 | 0 | 0 | 24 | 27.5 | 23.1 | 22.2 | 992.29 | 50.11 | 0.9368 | 95.4 | 86.1 |  | 12599 | 12621 | 22 | 0 | 0 | 0 | 24 | 6.6
| 2017-10-06 | 85.4 | 56.3% | 99 | 74 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3549 | 3035 | 3035 | 2972 | 3070 | 43 | 0 | 42 | 0 | 60 | 0 | 98 | -63 | 131 | 97.65% | 147.875 | 83.74% | 100% | 88.28% | 7.922 | 129.75 | 1027.8795 | 25.999 | 947 | 24621.053 | 8630.1926 | 126.4583 | 0 | 0 | 0 | 0 | 17 | 1440 | 0 | 1025 | 1014 | 1031 | -11 | 8630.1926 | 42.9583 | 0 | 0 | 24 | 27.6 | 23.2 | 22.1 | 993 | 50.08 | 0.9366 | 95.4 | 86.1 |  | 12672 | 12673 | 1 | 0 | 0 | 0 | 24 | 6.2
| 2017-10-07 | 85.4 | 58.7% | 99 | 74 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3544 | 3022 | 3022 | 2959 | 3057 | 43 | 0 | 42 | 0 | 60 | 0 | 98 | -63 | 130 | 97.98% | 147.6667 | 83.49% | 100% | 88.28% | 7.925 | 127.71 | 1012.1017 | 25.971 | 945 | 24542.595 | 8636.2612 | 125.9167 | 0 | 0 | 0 | 0 | 17 | 1440 | 0 | 1022 | 1008 | 1027 | -14 | 8636.2612 | 42.7917 | 0 | 0 | 24 | 27.6 | 23.1 | 22.1 | 991.75 | 50.09 | 0.9369 | 95.4 | 86.1 |  | 12700 | 12698 | -2 | 0 | 0 | 0 | 24 | 6.22
Week 41 | 2017-10-08 | 85.1 | 58% | 99 | 71 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3545 | 3023 | 3023 | 2959 | 3058 | 42 | 0 | 42 | 0 | 60 | 0 | 99 | -64 | 131 | 97.26% | 147.7083 | 83.47% | 100% | 88.19% | 7.91 | 127.7 | 1010.107 | 25.941 | 946 | 24540.186 | 8634.7729 | 125.9583 | 0 | 0 | 0 | 0 | 17 | 1440 | 0 | 1019 | 1012 | 1027 | -7 | 8634.7729 | 42.7917 | 0 | 0 | 24 | 27.52 | 23.05 | 22.04 | 990.38 | 50.11 | 0.937 | 95.24 | 86.13 |  | 12674 | 12649 | -25 | 0 | 0 | 0 | 24 | 6.47
| 2017-10-09 | 84.2 | 61.9% | 99 | 74 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 3559 | 3217 | 3217 | 3143 | 3247 | 42 | 0 | 42 | 0 | 60 | 0 | 104 | -74 | 145 | 93.3% | 148.2917 | 88.31% | 100% | 94.1% | 7.905 | 127.55 | 1008.2827 | 28.141 | 947 | 26649.527 | 8799.8122 | 134.0417 | 0 | 0 | 0 | 0 | 17 | 720 | 0 | 1011 | 1005 | 1231 | -6 | 8799.8122 | 51.2917 | 1.179 | 1.179 | 22.8 | 27.34 | 23.05 | 22.09 | 990.63 | 50.1 | 0.9379 | 94.76 | 86.22 |  | 12728 | 12689 | -39 | 2.358 | 12 | 12 | 22.75 | 6.25
| 2017-10-10 | 84.7 | 62.3% | 99 | 75 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 3550 | 3216 | 3216 | 3139 | 3247 | 42 | 0 | 42 | 0 | 60 | 0 | 108 | -77 | 145 | 93.3% | 147.9167 | 88.42% | 100% | 94.1% | 7.901 | 126.62 | 1000.4246 | 28.141 | 946 | 26621.386 | 8799.5574 | 134 | 0 | 0 | 0 | 0 | 17 | 720 | 0 | 1009 | 1004 | 1234 | -5 | 8799.5574 | 51.4167 | 1.215 | 1.223 | 24 | 27.33 | 22.95 | 22.03 | 990.46 | 50.11 | 0.9375 | 95.14 | 86.24 |  | 12725 | 12692 | -33 | 2.438 | 12 | 12 | 24 | 6.05
| 2017-10-11 | 84.67 | 63.55% | 95 | 73 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 3549 | 3207 | 3207 | 3132 | 3237 | 42 | 0 | 42 | 0 | 60 | 0 | 105 | -75 | 143 | 94.32% | 147.875 | 88.25% | 100% | 94.1% | 7.93 | 133.19 | 1056.1967 | 27.994 | 946.5774 | 26498.4877 | 8797.792 | 133.625 | 0 | 0 | 0 | 0 | 17 | 720 | 0 | 1008 | 1001 | 1228 | -7 | 8797.792 | 51.1667 | 1.187 | 1.192 | 24 | 27.29 | 22.88 | 22.27 | 990.8 | 50.11 | 0.935 | 95.44 | 86.23 |  | 12721 | 12690 | -31 | 2.379 | 12 | 12 | 24 | 6.47
| 2017-10-12 | 84.46 | 63.93% | 95 | 74 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 3554 | 3192 | 3192 | 3121 | 3226 | 42 | 0 | 42 | 0 | 60 | 0 | 105 | -71 | 143 | 94% | 148.0833 | 87.82% | 100% | 94.1% | 7.911 | 131.11 | 1037.2112 | 27.849 | 948.592 | 26417.3386 | 8796.7157 | 133 | 0 | 0 | 0 | 0 | 17 | 720 | 0 | 1007 | 1001 | 1218 | -6 | 8796.7157 | 50.75 | 1.139 | 1.143 | 24 | 27.19 | 22.8 | 22.18 | 990.75 | 50.11 | 0.9357 | 95.48 | 86.18 |  | 12686 | 12637 | -49 | 2.282 | 12 | 12 | 24 | 5.97
| 2017-10-13 | 84.01 | 58.77% | 95 | 74 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 3559 | 3217 | 3217 | 3147 | 3253 | 42 | 0 | 42 | 0 | 60 | 0 | 106 | -70 | 145 | 93.48% | 148.2917 | 88.42% | 100% | 94.1% | 7.9 | 127.57 | 1007.803 | 28.021 | 949 | 26591.929 | 8770.1722 | 134.0417 | 0 | 0 | 0 | 0 | 17 | 720 | 0 | 1015 | 1010 | 1228 | -5 | 8770.1722 | 51.1667 | 1.154 | 1.147 | 24 | 27.34 | 22.94 | 22.21 | 988.17 | 50.15 | 0.937 | 95.11 | 86.09 |  | 12657 | 12608 | -49 | 2.301 | 12 | 12 | 24 | 6.63
| 2017-10-14 | 83 | 60% | 96 | 73 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 3566 | 3214 | 3214 | 3142 | 3247 | 42 | 0 | 42 | 0 | 60 | 0 | 105 | -72 | 144 | 93.95% | 148.5833 | 88.11% | 100% | 94.1% | 7.93 | 128.87 | 1021.9391 | 27.956 | 949 | 26530.244 | 8768.9953 | 133.9167 | 0 | 0 | 0 | 0 | 17 | 720 | 0 | 1014 | 1008 | 1225 | -6 | 8768.9953 | 51.0417 | 1.137 | 1.137 | 24 | 27.3 | 22.9 | 22.2 | 988.1 | 50.06 | 0.9364 | 95.1 | 86.15 |  | 12668 | 12633 | -35 | 2.274 | 12 | 12 | 24 | 6.3
Week 42 | 2017-10-15 | 82 | 62% | 94 | 71 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3579 | 3025 | 3025 | 2962 | 3057 | 42 | 0 | 42 | 0 | 60 | 0 | 95 | -63 | 130 | 97.98% | 149.125 | 82.76% | 100% | 87.5% | 7.925 | 128.53 | 1018.6002 | 25.762 | 950 | 24473.9 | 8606.516 | 126.0417 | 0 | 0 | 0 | 0 | 18 | 1440 | 0 | 1016 | 1012 | 1029 | -4 | 8606.516 | 42.875 | 0 | 0 | 24 | 27.3 | 22.9 | 22.1 | 988.4 | 50.11 | 0.9368 | 95.25 | 86.14 |  | 12639 | 12569 | -70 | 0 | 0 | 0 | 24 | 6.4
| 2017-10-16 | 81.9 | 64.6% | 95 | 71 | 0 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 3576 | 44 | 44 | 44 | 46 | 42 | 1419 | 42 | 1376 | 60 | 1402 | 17 | 0 | 46 | 4.167% | 149 | 1.23% | 2.821% | 1.267% | 0 | 0 | 0 | 0.405 | 950 | 384.75 | 8744.3182 | 1.8333 | 19 | 16 | 25 | 59 | 38 | 38 | 5 | 11 | 20 | 15 | 9 | 8744.3182 | 0.625 | 0 | 0 | 0 | 21.4 | 16.7 | 4.4 | 990.4 | 50.1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2017-10-17 | 80.8 | 64.7% | 95 | 69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3583 | 0 | 0 | 0 | 0 | 42 | 1440 | 42 | 1440 | 60 | 1440 | 11 | 0 | 0 | no data | 149.2917 | no data | 0% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 990.58 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2017-10-18 | 81.4 | 60.6% | 97.7 | 67.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3578 | 0 | 0 | 0 | 0 | 42 | 1440 | 42 | 1440 | 60 | 1440 | 11 | 0 | 0 | no data | 149.0833 | no data | 0% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 992.2 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2017-10-19 | 80.4 | 57.33% | 96.5 | 68.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3590 | 0 | 0 | 0 | 0 | 42 | 1440 | 42 | 1440 | 60 | 1440 | 0 | 0 | 0 | no data | 149.5833 | no data | 0% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 991.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2017-10-20 | 81.6 | 58.8% | 93 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3579 | 0 | 0 | 0 | 0 | 42 | 1440 | 42 | 1440 | 60 | 1440 | 12 | 0 | 0 | no data | 149.125 | no data | 0% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 992.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2017-10-21 | 80.8 | 61% | 94 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3585 | 0 | 0 | 0 | 0 | 42 | 1440 | 42 | 1440 | 60 | 1440 | 7 | 0 | 0 | no data | 149.375 | no data | 0% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 991.13 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Week 43 | 2017-10-22 | 79.2 | 56.1% | 94 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3604 | 0 | 0 | 0 | 0 | 42 | 1440 | 42 | 1440 | 60 | 1440 | 9 | 0 | 0 | no data | 150.1667 | no data | 0% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 988.38 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2017-10-23 | 76.86 | 67.99% | 89 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3628 | 0 | 0 | 0 | 0 | 42 | 1440 | 42 | 1440 | 60 | 1440 | 10 | 0 | 0 | no data | 151.1667 | no data | 0% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 992.33 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2017-10-24 | 77.66 | 65.47% | 91 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3614 | 0 | 0 | 0 | 0 | 42 | 1440 | 42 | 1440 | 60 | 1440 | 10 | 0 | 0 | no data | 150.5833 | no data | 0% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 996.21 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2017-10-25 | 77.96 | 59.29% | 92 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3616 | 0 | 0 | 0 | 0 | 42 | 1440 | 42 | 1440 | 60 | 1440 | 13 | 0 | 0 | no data | 150.6667 | no data | 0% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 996.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2017-10-26 | 76.6 | 53.7% | 89 | 65 | 6 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3628 | 534 | 534 | 535 | 565 | 44 | 885 | 44 | 1440 | 60 | 1029 | 40 | 1 | 77 | 30.57% | 151.1667 | 14.75% | 23.03% | 15.85% | 0 | 0 | 0 | 5.075 | 948.412 | 4813.1909 | 8996.6185 | 22.25 | 18 | 165 | 0 | 0 | 30 | 411 | 10 | 366 | 0 | 199 | -366 | 8996.6185 | 8.2917 | 0.792 | 0 | 24 | 25.4 | 0 | 0 | 992.1 | 50.1 | 0 | 94.1 | 0 |  | 12389 | 0 | 0 | 0.792 | 6.75 | 0 | 5.25 | 10
| 2017-10-27 | 76 | 60% | 90 | 63 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3633 | 1766.5 | 1766.5 | 1744 | 1823 | 45 | 0 | 45 | 1440 | 60 | 0 | 79 | -22.5 | 78 | 97.38% | 151.375 | 48% | 70% | 50% | 0 | 0 | 0 | 16.196 | 945 | 15305.22 | 8775.9289 | 73.6042 | 0 | 0 | 0 | 0 | 30 | 1440 | 0 | 1088 | 0 | 735 | -1088 | 8775.9289 | 30.625 | 2.564 | 0 | 24 | 28.7 | 0 | 0 | 996.6 | 50.12 | 0 | 93.76 | 0 |  | 12433 | 0 | -12433 | 2.564 | 24 | 0 | 24 | 5.4
| 2017-10-28 | 77 | 62% | 88 | 67 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3629 | 1726 | 1726 | 1698 | 1776 | 45 | 0 | 45 | 1440 | 60 | 0 | 78 | -28 | 76 | 97.37% | 151.2083 | 46.79% | 70% | 49.33% | 0 | 0 | 0 | 15.7354 | 944 | 14854.227 | 8748.0725 | 71.9167 | 0 | 0 | 0 | 0 | 31 | 1440 | 0 | 1073 | 0 | 698 | -1073 | 8748.0725 | 29.0833 | 2.219 | 0 | 24 | 28.6 | 0 | 0 | 996.7 | 50.1 | 0 | 93.62 | 0 |  | 12519 | 0 | -12519 | 2.219 | 24 | 0 | 24 | 5.6
Week 44 | 2017-10-29 | 76.2 | 61.1% | 89 | 65 | 18 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3627 | 1187 | 1187 | 1171 | 1228 | 45 | 389 | 45 | 1440 | 60 | 469 | 63 | -16 | 75 | 68.22% | 151.125 | 32.29% | 48.87% | 32.88% | 0 | 0 | 0 | 10.865 | 943 | 10245.695 | 8749.526 | 49.4583 | 34 | 16 | 0 | 0 | 35 | 971 | 6 | 820 | 0 | 408 | -820 | 8749.526 | 17 | 0.899 | 0 | 24 | 21.9 | 0 | 0 | 998.7 | 50.09 | 0 | 93.1 | 0 |  | 12538 | 0 | -12538 | 0.899 | 10.34 | 0 | 18.23 | 7.18
| 2017-10-30 | 74.7 | 68.9% | 86 | 66 | 5 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3643 | 399 | 399 | 373 | 392 | 45 | 1020 | 45 | 1440 | 60 | 1108 | 35 | -26 | 65 | 25.13% | 151.7917 | 10.24% | 17.97% | 10.96% | 0 | 0 | 0 | 3.641 | 945 | 3440.745 | 9224.5174 | 16.625 | 24 | 78 | 0 | 0 | 40 | 332 | 16 | 284 | 0 | 108 | -284 | 9224.5174 | 4.5 | 0 | 0 | 24 | 26.7 | 0 | 0 | 988.88 | 50.14 | 0 | 94.3 | 0 |  | 12514 | 0 | -12514 | 0 | 0 | 0 | 5.1 | 3.27
| 2017-10-31 | 76.1 | 65.5% | 87 | 66 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3633 | 1512 | 1512 | 1489 | 1559 | 45 | 0 | 45 | 1440 | 60 | 0 | 70 | -23 | 66 | 98.42% | 151.375 | 40.99% | 70% | 43.33% | 0 | 0 | 0 | 13.715 | 947 | 12988.105 | 8722.7032 | 63 | 0 | 0 | 0 | 0 | 40 | 1440 | 0 | 1075 | 0 | 484 | -1075 | 8722.7032 | 20.1667 | 0 | 0 | 24 | 28.5 | 0 | 0 | 996.5 | 50.08 | 0 | 94 | 0 |  | 12471 | 0 | -12471 | 0 | 0 | 0 | 24 | 5
| 2017-11-01 | [25 empty] | 0 | 0 |  | no data | no data | no data | #DIV/0! | no data |  |  | 0 |  |  | 0 | no data | 0 | [10 empty] | 0 | no data | 0 | [14 empty] | 0 | 0
| 2017-11-02 | [25 empty] | 0 | 0 |  | no data | no data | no data | #DIV/0! | no data |  |  | 0 |  |  | 0 | no data | 0 | [10 empty] | 0 | no data | 0 | [14 empty] | 0 | 0
| 2017-11-03 | [25 empty] | 0 | 0 |  | no data | no data | no data | #DIV/0! | no data |  |  | 0 |  |  | 0 | no data | 0 | [10 empty] | 0 | no data | 0 | [14 empty] | 0 | 0
| 2017-11-04 | [25 empty] | 0 | 0 |  | no data | no data | no data | #DIV/0! | no data |  |  | 0 |  |  | 0 | no data | 0 | [10 empty] | 0 | no data | [15 empty] | 0 | 0
| Monthly | 81.5242 | 0.60662 | 94.5226 | 70.4194 | 462 | 32 | 360 | 5 | 0 | 0 | 0 | 0 | 12 | 0 | 110991 | 53707.5 | 53707.5 | 52668.77 | 54412 | 42.7742 | 16673 | 42.5484 | 22976 | 60 | 16968 | 1836.23 | -1138.5 | 81.3871 | 84.7% | 149.1815 | 67.11% | 58.15% | 70.99% | 118.778 | 62.1126 | 15247.1206 | 467.4304 | 671.9103 | 442589.0048 | 8692.7438 | 72.1875 | 95 | 275 | 25 | 59 | 500 | 23352 | 93 | 19987 | 15154 | 19266 | -4833 | 8692.7438 | 802.75 | 13.485 | 7.021 | 16.2194 | 19.1261 | 11.6923 | 10.8571 | 991.8158 | 35.56 | 0.4533 | 64.2858 | 41.6758 | 0 | 8548.2581 | 6129.2258 | -2419.0323 | 20.506 | 137.09 | 72 | 459.33 | 131.08
| Totals | Avg.F | % Avg. | M Avg | m Avg | hrs | min | hrs | min | hrs | min | hrs | min | Avg Int Avi | Avg Ext Avi | MWhr Total | MWhr Total | MWhr Total | MWhr Total | MWhr Total | MW Avg | Total min | Avg MW | Total min | Avg MW | Total min | MWhr | Total MW | Av Max D/Gen | Av. DailyLF | Avg. | Avg. |  | Avg. | Total | Avg. |  | Total | Avg. |  | Avg. | [7 empty] | Total |  |  |  |  | Avg.
| Weeks data | Site Avg. Amb. Temp F | Site Avg. Relative humidity % | Max: Site Maximum/Minumum Temperature; CT1 hrs: CT-1 Base Load Hours; CT2 hrs: CT-2 Base Load Hours; CT1 hrs: CT-1 stand by hours / min; CT2 hrs: CT-2 standby hours / min; CT2 hrs: Plant ambient Corrected maximum Load hours/min | Average Corrected Plant Capacity | Ambient Corrected Declared Avail'y (MWH) | Av Plant WAPDA Dispatch | Net Plant Export (MWH) | Gross Generation | CT1 Av Cap (MW) | CT1 Unavail minutes | CT2 Av Cap (MW) | CT2 Unavail minutes | ST Unavail minutes | ST Average Cap (MW) | Plant Aux Load including Colony Load MWH | Differenece (+/-) MW | Maximum Daily Generation | Daily Load Factor | Avg. Corrected Plant | Plant Capacity Facto | Plant Availability Factor | Equivalent Plant Availability | LBtu gas flow mmscf | 1 LBtu gas (Average Btu/scf) | LBTU MMBTU | PL gas flow (mscf/week) | 1 PL gas (Average Btu/scf) | HBTU MMBTU | Plant Net Heat Rate (Btu/Kwh) | [11 empty] | -91.5
| Week 40 | 85.7043 | 57.57% | 98.8571 | 74 | 168 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3540.5714 | 3032.5714 | 3032.5714 | 2967.1429 | 3064.4286 | 43 | No outage | 42 | No outage | 420 | no data | no data | -458 | 130.5714 | 97.79% | 147.5238 | 83.8% | 100% | 88.28% | 55.466 | 127.7643 | 7086.5739 | 181.993 | 946.377 | 172233.9894 | 8633.628
| Week 41 | 84.3057 | 61.21% | 96.8571 | 73.4286 | 168 | -2 | 168 | 0 | 0 | 0 | 0 | -60 | 72 | 0 | 3554.5714 | 3183.7143 | 3183.7143 | 21783 | 22515 | 42 | No outage | 294 | no data | 420 | no data | 732 | -503 | 142.2857 | 94.23% | 148.1071 | 87.54% | 100% | 93.25% | 55.387 | 128.9443 | 7141.8372 | 194.043 | 947.4528 | 183846.5781 | 8766.8311 | [5 empty] | 0.27381
| Week 42 | 81.2714 | 61.29% | 95.0286 | 69.8571 | 24 | 5 | 24 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 3581.4286 | 438.4286 | 438.4286 | 3006 | 3103 | 42 | 8619 | 294 | no data | 420 | no data | 153 | -63 | 25.1429 | 51.07% | 149.2262 | 42% | 14.69% | 44.38% | 7.925 | 18.3614 | 145.5143 | 26.167 | 316.6667 | 8286.2167 | 8675.4171 | [5 empty] | 0.26672
| Week 43 | 77.3257 | 60.65% | 90.4286 | 66.4286 | 54 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3621.7143 | no data | no data | no data | no data | 43.1429 | 6645 | 302 | 1440 | 420 | 969.8571 | 239 | no data | no data | 75.11% | 150.9048 | 36.51% | no data | 38.39% | no data | no data | #VALUE! | no data | no data | #VALUE! | 8840.2066
| Week 44 | 75.6667 | 0.65167 | 87.3333 | 65.6667 | 47 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3634.3333 | 1032.6667 | 1032.6667 | 3033 | 3179 | 45 | 5594 | 305 | 1440 | #REF! | 525.6667 | 168 | -65 | 68.6667 | 63.92% | 151.4306 | 27.84% | no data | 29.06% | no data | no data | #VALUE! | 28.221 | 945 | 26668.845 | 8898.9155
| Date | Plant Status Whether Normal Operation or Tripping (State full detail for trippings/return to normal).
| 2017-10-01 | Plant load restricted to 120~128 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-10-02 | Plant load restricted to 121~126 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-10-03 | Plant load restricted to 120~125 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-10-04 | Plant load restricted to 121~127 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-10-05 | Plant load restricted to 121~127 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-10-06 | Plant load restricted to 121~127 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-10-07 | Plant load restricted to 121~126 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-10-08 | Plant load restricted to 120~127 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-10-09 | Plant load increased from 124 to 138 MW by taking DBs into service at 1100 hrs to achieve maximum export. At 2300 hrs, plant load reduced from 140 to 124 MW by taking duct burners out of service to keep within contractual plant heat rate.
| 2017-10-10 | Plant load increased from 123 to 139 MW by taking DBs into service at 1100 hrs to achieve maximum export. At 2300 hrs, plant load reduced from 140 to 124 MW by taking duct burners out of service to keep within contractual plant heat rate.
| 2017-10-11 | Plant load increased from 123 to 137 MW by taking DBs into service at 1100 hrs to achieve maximum export. At 2300 hrs, plant load reduced from 138 to 123 MW by taking duct burners out of service to keep within contractual plant heat rate.
| 2017-10-12 | Plant load increased from 121 to 135 MW by taking DBs into service at 1100 hrs to achieve maximum export. At 2300 hrs, plant load reduced from 139 to 124 MW by taking duct burners out of service to keep within contractual plant heat rate.
| 2017-10-13 | Plant load increased from 122 to 137 MW by taking DBs into service at 1100 hrs to achieve maximum export. At 2300 hrs, plant load reduced from 140 to 125 MW by taking duct burners out of service to keep within contractual plant heat rate.
| 2017-10-14 | Plant load increased from 122 to 137 MW by taking DBs into service at 1100 hrs to achieve maximum export. At 2300 hrs, plant load reduced from 139 to 125 MW by taking duct burners out of service to keep within contractual plant heat rate.
| 2017-10-15 | Plant load restricted to 121~126 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-10-16 | CT-1 de-synch @ 0021hrs, STG de-synch @ 0038hrs and CT-2 de-synch @ 0104hrs to avail scheduled outage of complex for 2017.
| 2017-10-17 | FKPCL complex is shutdown for "Scheduled Outage of 2017"
| 2017-10-18 | FKPCL complex is shutdown for "Scheduled Outage of 2017"
| 2017-10-19 | FKPCL complex is shutdown for "Scheduled Outage of 2017"
| 2017-10-20 | FKPCL complex is shutdown for "Scheduled Outage of 2017"
| 2017-10-21 | FKPCL complex is shutdown for "Scheduled Outage of 2017"
| 2017-10-22 | FKPCL complex is shutdown for "Scheduled Outage of 2017"
| 2017-10-23 | FKPCL complex is shutdown for "Scheduled Outage of 2017"
| 2017-10-24 | FKPCL complex is shutdown for "Scheduled Outage of 2017"
| 2017-10-25 | FKPCL complex is shutdown for "Scheduled Outage of 2017"
| 2017-10-26 | CT-1 synch @ 1445hrs and STG synch @ 1709hrs after completion of scheduled outage activities and are commercially available from time of synchronization. Gas turbine CT-2 is still shutdown for scheduled outage activities for 2017.
| 2017-10-27 | Plant load remained 71~75 MW from 0000~2400 hrs. CT-2 is shutdown for schudled outage activties of 2017.
| 2017-10-28 | Plant load remained 69~72 MW from 0000~2400 hrs. CT-2 is shutdown for schudled outage activties of 2017.
| 2017-10-29 | STG de-synch @ 1611hrs & CT-1 de-synch @ 1631hrs to attend ST governor valve problem while Gas turbine CT-2 is already in shutdown condition for approved scheduled outage activities of 2017.
| 2017-10-30 | CT-1 synch @ 1700 hrs & STG synch @ 1828 hrsto attending ST governor valve problem while Gas turbine CT-2 is already in shutdown condition for approved scheduled outage activities of 2017.
| 2017-10-31 | Plant load remained 61~63 MW from 0000~2400 hrs. CT-2 is shutdown for scheduled outage activities of 2017.
Note on AB21: ops.e: EDG+Wapda import
Note on AB25: ops.e: EDG + Wapda Import

## Nov
Monthly Operational Returns Kabirwala
2017-11-01
| Date | Site Avg. Ambient Temp.F | Site Avg. Relative Humidty % | Site Ambient Temp |  | Base load hours |  |  |  | Standby hours |  |  |  | Plant ambient corrected Max Load |  | Corrected Plant Capacity | Ambient Corrected Daclared Avail'y (MWH) | Plant WAPDA Dispatch (MWH) | Net Plant Export (MWH) | Gross Generation | CT1 Average Cap (MW) | CT1 Unavail minutes | CT2 Average Cap (MW) | CT2 Unavail minutes | ST Average Cap (MW) | ST Unavail minutes | Plant Aux Load including Colony Load MWH | Differenece (+/-) MW | Maximum Daily Generation | Daily Load Factor | Avg. Corrected Plant Capacity | Plant Capacity Factor | Plant Availability Factor | Equivalent Plant Availability | LBtu gas flow (mmscf/day) | 1 LBtu gas (Average Btu/scf) | LBTU MMBTU | 1 HBtu gas flow (mmscf/day) | 1 HBtu gas (Average Btu/scf) | HBTU MMBTU | HHV Net Heat Rate (Btu/Kwh) | Avg. declared availability | CT1 Derated MW | CT1 derated mintutes | CT-2 derated MW | CT-2 derated mintutes | ST derated MW | ST derated mintutes | WAPDA Backfeed (MWH) | CT-1 Gross Generation (MWH) | CT-2 Gross Generation (MWH) | STG Gross Generation (MWH) | CT-1 & CT-2 MWH difference | Base load Heat Rate | STG load | DB1 | DB2 | CT1 | CT1 Gas flow | CT2 Gas flow |  | Pamb | Freq. Hz | LBTU Gas Specific gravity | CT-1 compressor efficiency(%) | CT-2 compressor efficiency(%) |  | CT-1 Heat Rate (Btu/Kwh) | CT-2 Heat Rate (Btu/Kwh) |  | DB(1+2) | DB-1 Ops Hours | DB-2 Ops Hours | CT-1 Wetcomprssion Ops Hours | RO Operation Hours
[6 empty] | CT1 |  | CT2 |  | CT1 |  | CT2 | [43 empty] | mmscf/d | mmscf/d | WetC flow | HBTU KPPH | HBTU KPPH | LBTU KPPH | mbar | Hz | [7 empty] | mmscf/d
|  |  |  | Max | Min | hrs | min | hrs | min | hrs | min | hrs | min | hrs | min | [42 empty] | gpm
Week 45 | 2017-10-29 | 76.2 | 61.1% | 89 | 65 | 18 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3627 | 1187 | 1187 | 1171 | 1228 | 45 | 389 | 45 | 1440 | 60 | 469 | 63 | -16 | 75 | 68.22% | 151.125 | 32.29% | 48.87% | 32.88% | 0 | 0 | 0 | 10.865 | 943 | 10245.695 | 8749.526 | 49.4583 | 34 | 16 | 0 | 0 | 35 | 971 | 6 | 820 | 0 | 408 | -820 | 8749.526 | 17 | 0.899 | 0 | 24 | 21.9 | 0 | 0 | 998.7 | 50.09 | 0 | 93.1 | 0 |  | 12538 | 0 | -12538 | 0.899 | 10.34 | 0 | 18.23 | 7.18
| 2017-10-30 | 74.7 | 68.9% | 86 | 66 | 5 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3643 | 399 | 399 | 373 | 392 | 45 | 1020 | 45 | 1440 | 60 | 1108 | 35 | -26 | 65 | 25.13% | 151.7917 | 10.24% | 17.97% | 10.96% | 0 | 0 | 0 | 3.641 | 945 | 3440.745 | 9224.5174 | 16.625 | 24 | 78 | 0 | 0 | 40 | 332 | 16 | 284 | 0 | 108 | -284 | 9224.5174 | 4.5 | 0 | 0 | 24 | 26.7 | 0 | 0 | 988.88 | 50.14 | 0 | 94.3 | 0 |  | 12514 | 0 | -12514 | 0 | 0 | 0 | 5.1 | 3.27
| 2017-10-31 | 76.1 | 65.5% | 87 | 66 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3633 | 1512 | 1512 | 1489 | 1559 | 45 | 0 | 45 | 1440 | 60 | 0 | 70 | -23 | 66 | 98.42% | 151.375 | 40.99% | 70% | 43.33% | 0 | 0 | 0 | 13.715 | 947 | 12988.105 | 8722.7032 | 63 | 0 | 0 | 0 | 0 | 40 | 1440 | 0 | 1075 | 0 | 484 | -1075 | 8722.7032 | 20.1667 | 0 | 0 | 24 | 28.5 | 0 | 0 | 996.5 | 50.08 | 0 | 94 | 0 |  | 12471 | 0 | -12471 | 0 | 0 | 0 | 24 | 5
| 2017-11-01 | 72.5 | 76.2% | 81 | 66 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3670 | 1500 | 1500 | 1475 | 1545 | 45 | 0 | 45 | 1440 | 60 | 0 | 70 | -25 | 65 | 99.04% | 152.9167 | 40.19% | 70% | 43.33% | 0 | 0 | 0 | 13.8113 | 944.193 | 13040.5328 | 8841.0392 | 62.5 | 0 | 0 | 0 | 0 | 40 | 1440 | 0 | 1062 | 0 | 483 | -1062 | 8841.0392 | 20.125 | 0 | 0 | 24 | 28.48 | 0 | 0 | 998.04 | 50.06 | 0 | 93.66 | 0 |  | 21613 | 0 | -21613 | 0 | 0 | 0 | 24 | 0
| 2017-11-02 | 71.2 | 82.4% | 79 | 65 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3678 | 1488 | 1488 | 1467 | 1536 | 44 | 0 | 45 | 1440 | 60 | 0 | 69 | -21 | 66 | 96.97% | 153.25 | 39.89% | 69.8% | 42.95% | 0 | 0 | 0 | 13.732 | 943 | 12949.276 | 8827.0457 | 62 | 0 | 0 | 0 | 0 | 40 | 1440 | 0 | 1053 | 0 | 483 | -1053 | 8827.0457 | 20.125 | 0 | 0 | 24 | 28.44 | 0 | 0 | 999.71 | 50.07 | 0 | 93.5 | 0 | 0 | 21690 | 0 | -21690 | 0 | 0 | 0 | 24 | 6.12
| 2017-11-03 | 68.2 | 89.6% | 72 | 66 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3710 | 1490 | 1490 | 821 | 856 | 44 | 592 | 45 | 1440 | 60 | 658 | 36 | -669 | 65 | 54.87% | 154.5833 | 22.13% | 39.26% | 24.68% | 0 | 0 | 0 | 9.652 | 941 | 9082.532 | 11062.7674 | 62.0833 | 0 | 0 | 0 | 0 | 40 | 782 | 1 | 597 | 0 | 259 | -597 | 11062.7674 | 10.7917 | 0 | 0 | 24 | 28.23 | 0 | 0 | 987.83 | 49.95 | 0 | 93.42 | 0 | 0 | 21672 | 0 | -21672 | 0 | 0 | 0 | 24 | 0
| 2017-11-04 | 70.8 | 84.2% | 77 | 68 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3688 | 1490 | 1490 | 1464 | 1530 | 44 | 0 | 45 | 1440 | 60 | 0 | 66 | -26 | 64 | 99.61% | 153.6667 | 39.7% | 69.8% | 42.95% | 0 | 0 | 0 | 13.841 | 935 | 12941.335 | 8839.7097 | 62.0833 | 0 | 0 | 0 | 0 | 40 | 1440 | 0 | 1046 | 0 | 484 | -1046 | 8839.7097 | 20.1667 | 0 | 0 | 24 | 28.53 | 0 | 0 | 1000.2 | 50.06 | 0 | 93.17 | 0 |  | 12821 | 0 | -12821 | 0 | 0 | 0 | 24 | 6.72
Week 46 | 2017-11-05 | 68.15 | 87.21% | 75 | 65 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3704 | 1495 | 1495 | 1471 | 1536 | 44 | 0 | 45 | 1440 | 60 | 0 | 65 | -24 | 65 | 98.46% | 154.3333 | 39.71% | 69.8% | 42.95% | 0 | 0 | 0 | 13.834 | 938 | 12976.292 | 8821.4086 | 62.2917 | 0 | 0 | 0 | 0 | 40 | 1440 | 0 | 1051 | 0 | 485 | -1051 | 8821.4086 | 20.2083 | 0 | 0 | 24 | 28.46 | 0 | 0 | 1000.5 | 50.07 | 0 | 92.99 | 0 |  | 12730 | 0 | -12730 | 0 | 0 | 0 | 24 | 6.75
| 2017-11-06 | 68.51 | 85.41% | 76 | 65 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3701 | 1496 | 1496 | 1473 | 1537 | 44 | 0 | 45 | 1440 | 60 | 0 | 64 | -23 | 65 | 98.53% | 154.2083 | 39.8% | 69.8% | 42.95% | 0 | 0 | 0 | 13.915 | 934 | 12996.61 | 8823.2247 | 62.3333 | 0 | 0 | 0 | 0 | 40 | 1440 | 0 | 1052 | 0 | 485 | -1052 | 8823.2247 | 20.2083 | 0 | 0 | 24 | 28.79 | 0 | 0 | 999.46 | 50.08 | 0 | 93.04 | 0 |  | 12858 | 0 | -12858 | 0 | 0 | 0 | 24 | 5.75
| 2017-11-07 | 69 | 78% | 79 | 64 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3689 | 1499 | 1499 | 1474 | 1539 | 44 | 0 | 45 | 1440 | 60 | 0 | 65 | -25 | 65 | 98.65% | 153.7083 | 39.96% | 69.8% | 42.95% | 0 | 0 | 0 | 13.981 | 934 | 13058.254 | 8859.0597 | 62.4583 | 0 | 0 | 0 | 0 | 40 | 1440 | 0 | 1056 | 0 | 483 | -1056 | 8859.0597 | 20.125 | 0 | 0 | 24 | 28.7 | 0 | 0 | 998.5 | 50.1 | 0 | 92.89 | 0 |  | 12768 | 0 | -12768 | 0 | 0 | 0 | 24 | 6.4
| 2017-11-08 | 68 | 83% | 74 | 63 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3698 | 1502 | 1502 | 1471 | 1536 | 44 | 0 | 45 | 1440 | 60 | 0 | 65 | -31 | 65 | 98.46% | 154.0833 | 39.78% | 69.8% | 42.95% | 0 | 0 | 0 | 14.089 | 916 | 12905.524 | 8773.2998 | 62.5833 | 0 | 0 | 0 | 0 | 40 | 1440 | 0 | 1055 | 0 | 481 | -1055 | 8773.2998 | 20.0417 | 0 | 0 | 24 | 29.4 | 0 | 0 | 998.5 | 50.15 | 0 | 92.84 | 0 |  | 13085 | 0 | -13085 | 0 | 0 | 0 | 24 | 9.7
| 2017-11-09 | 64 | 86% | 71 | 59 | 24 | 0 | 7 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 3718 | 2055 | 2055 | 2040 | 2120 | 44 | 0 | 45 | 894 | 60 | 0 | 80 | -15 | 137 | 64.48% | 154.9167 | 54.87% | 81.25% | 58.69% | 2.381 | 139.6 | 332.3876 | 19.041 | 926 | 17631.966 | 8806.0557 | 85.625 | 0 | 0 | 20 | 116 | 32 | 1440 | 0 | 1067 | 391 | 662 | -676 | 8806.0557 | 27.5833 | 0 | 0 | 24 | 28.8 | 9.2 | 8 | 998.1 | 50.14 | 0.9318 | 92.4 | 86.5 |  | 12709 | 11896 | -813 | 0 | 0 | 0 | 24 | 8.1
| 2017-11-10 | 61.9 | 89.6% | 66 | 58 | 24 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 2446 | 2446 | 2409 | 2491 | 44 | 0 | 47 | 618 | 60 | 0 | 82 | -37 | 137 | 75.76% | 155 | 64.76% | 86.64% | 68.3% | 4.028 | 140.81 | 567.1827 | 21.422 | 945 | 20243.79 | 8638.843 | 101.9167 | 0 | 0 | 24 | 42 | 27 | 1440 | 0 | 1068 | 627 | 796 | -441 | 8638.843 | 33.1667 | 0 | 0 | 24 | 28.7 | 23.6 | 22.7 | 999.25 | 50.1 | 0.9313 | 92.2 | 85.6 |  | 12642 | 12226 | -416 | 0 | 0 | 0 | 24 | 8.76
| 2017-11-11 | 63.1 | 91.5% | 68 | 61 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 3193 | 3193 | 3140 | 3234 | 44 | 0 | 46 | 0 | 60 | 0 | 94 | -53 | 136 | 99.08% | 155 | 84.41% | 100% | 89.33% | 7.577 | 133.36 | 1010.4687 | 27.598 | 948 | 26162.904 | 8653.9404 | 133.0417 | 0 | 0 | 0 | 0 | 16 | 1440 | 0 | 1061 | 1113 | 1060 | 52 | 8653.9404 | 44.1667 | 0 | 0 | 24 | 28.4 | 24.1 | 23.7 | 1000 | 50.07 | 0.9336 | 92.4 | 85.3 |  | 12610 | 11976 | -634 | 0 | 0 | 0 | 24 | 6.65
Week 47 | 2017-11-12 | 62.1 | 87.2% | 69 | 57 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3718 | 3209 | 3209 | 3150 | 3244 | 45 | 0 | 46 | 0 | 60 | 0 | 94 | -59 | 137 | 98.66% | 154.9167 | 84.72% | 100% | 89.4% | 7.636 | 138.51 | 1057.6624 | 27.689 | 946 | 26193.794 | 8651.256 | 133.7083 | 0 | 0 | 0 | 0 | 16 | 1440 | 0 | 1069 | 1111 | 1064 | 42 | 8651.256 | 44.3333 | 0 | 0 | 24 | 28.8 | 24.3 | 23.6 | 997.8 | 50.1 | 0.9316 | 92.2 | 84.8 |  | 12642 | 12072 | -570 | 0 | 0 | 0 | 24 | 6.33
| 2017-11-13 | 64.1 | 78.7% | 75 | 55 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3705 | 3182 | 3150 | 3102 | 3193 | 43 | 0 | 45 | 0 | 60 | 0 | 91 | -48 | 136 | 97.82% | 154.375 | 83.72% | 100% | 89.19% | 7.753 | 134.29 | 1041.1504 | 27.298 | 946 | 25823.908 | 8660.5604 | 132.5833 | 0 | 0 | 0 | 0 | 16 | 1440 | 0 | 1039 | 1096 | 1058 | 57 | 8660.5604 | 44.0833 | 0 | 0 | 24 | 28.16 | 24.09 | 23.59 | 995.29 | 50.09 | 0.9336 | 89.79 | 84.35 |  | 12740 | 12130 | -610 | 0 | 0 | 0 | 18.42 | 6.57
| 2017-11-14 | 65 | 80.6% | 70 | 60 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3714 | 3177 | 3177 | 3111 | 3205 | 44 | 0 | 45 | 0 | 60 | 0 | 94 | -66 | 136 | 98.19% | 154.75 | 83.76% | 100% | 89.26% | 7.755 | 133.27 | 1033.5089 | 27.475 | 944 | 25936.4 | 8669.2089 | 132.375 | 0 | 0 | 0 | 0 | 16 | 1440 | 0 | 1055 | 1090 | 1060 | 35 | 8669.2089 | 44.1667 | 0 | 0 | 24 | 28.53 | 24.09 | 23.56 | 994.5 | 50.13 | 0.9335 | 91.8 | 84.4 |  | 12713 | 12184 | -529 | 0 | 0 | 0 | 24 | 6.37
| 2017-11-15 | 62.2 | 83.9% | 71 | 68 | 19 | 9 | 18 | 49 | 3 | 35 | 3 | 31 | 0 | 0 | 3718 | 3268 | 2645 | 2554 | 2633 | 44 | 0 | 44 | 0 | 60 | 0 | 83 | -91 | 136 | 80.67% | 154.9167 | 68.69% | 100% | 89.6% | 6.458 | 141.1 | 911.2238 | 23.105 | 946 | 21857.33 | 8914.8605 | 136.1667 | 20 | 76 | 20 | 100 | 16 | 1165 | 4 | 879 | 907 | 847 | 28 | 8914.8605 | 35.2917 | 0 | 0 | 24 | 23.91 | 20.23 | 19.7 | 999.13 | 50.1 | 0.9306 | 91.96 | 84.6 |  | 12631 | 12076 | -555 | 0 | 0 | 0 | 18.43 | 7.18
| 2017-11-16 | 64.1 | 74% | 74 | 74 | 17 | 40 | 13 | 2 | 4 | 53 | 4 | 53 | 0 | 0 | 3710 | 3110 | 2121 | 2084 | 2152 | 44 | 0 | 45 | 295 | 60 | 0 | 74 | -37 | 138 | 64.98% | 154.5833 | 56.17% | 93.81% | 80.81% | 4.323 | 152.89 | 660.9435 | 19.213 | 948 | 18213.924 | 9057.0381 | 129.5833 | 17 | 87 | 20 | 70 | 23 | 1088 | 6 | 816 | 656 | 680 | -160 | 9057.0381 | 28.3333 | 0 | 0 | 24 | 22.33 | 14.47 | 13.59 | 1001.3 | 50.1 | 0.9281 | 90.65 | 86.23 |  | 12717 | 11801 | -916 | 0 | 0 | 0 | 15.25 | 7.73
| 2017-11-17 | 65.37 | 66.36% | 77 | 56 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3701 | 3335 | 3221 | 3174 | 3269 | 45 | 0 | 48 | 0 | 60 | 0 | 95 | -47 | 139 | 97.99% | 154.2083 | 85.76% | 100% | 90.2% | 7.85 | 139.2 | 1092.72 | 27.347 | 944 | 25815.568 | 8477.7215 | 138.9583 | 0 | 0 | 0 | 0 | 15 | 1440 | 0 | 1049 | 1150 | 1070 | 101 | 8477.7215 | 44.5833 | 0 | 0 | 24 | 28.51 | 24.85 | 23.76 | 1001.3 | 50.1 | 0.9324 | 89.92 | 85.62 |  | 12780 | 11876 | -904 | 0 | 0 | 0 | 19.5 | 6.98
| 2017-11-18 | 64.62 | 58.16% | 76 | 55 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3703 | 3275 | 3275 | 3204 | 3297 | 44 | 0 | 48 | 0 | 60 | 0 | 93 | -71 | 139 | 98.83% | 154.2917 | 86.52% | 100% | 90.13% | 7.845 | 138.39 | 1085.6695 | 27.512 | 947 | 26053.864 | 8470.5161 | 136.4583 | 0 | 0 | 0 | 0 | 15 | 1440 | 0 | 1061 | 1161 | 1075 | 100 | 8470.5161 | 44.7917 | 0 | 0 | 24 | 28.59 | 24.91 | 23.83 | 1001.8 | 50.15 | 0.9318 | 89.86 | 85.36 |  | 12658 | 11807 | -851 | 0 | 0 | 0 | 19.67 | 4.98
Week 48 | 2017-11-19 | 65.9 | 53% | 79 | 56 | 19 | 33 | 19 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 3695 | 3336 | 3120 | 3072 | 3162 | 43 | 0 | 46 | 0 | 60 | 0 | 90 | -48 | 139 | 94.78% | 153.9583 | 83.14% | 100% | 86.37% | 7.84 | 135.76 | 1064.3584 | 26.354 | 950 | 25036.3 | 8496.3081 | 139 | 7 | 367 | 6 | 367 | 17 | 1440 | 0 | 1011 | 1113 | 1038 | 102 | 8496.3081 | 43.25 | 0 | 0 | 24 | 21.58 | 23.98 | 23.85 | 1001.75 | 50.1 | 0.9326 | 87.6 | 85.22 |  | 12834 | 11928 | -906 | 0 | 0 | 0 | 13.4 | 6.48
| 2017-11-20 | 65 | 54% | 80 | 52 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3693 | 3238 | 3238 | 3171 | 3264 | 43 | 0 | 48 | 0 | 60 | 0 | 93 | -67 | 138 | 98.55% | 153.875 | 85.87% | 100% | 90.07% | 7.85 | 137.01 | 1075.5285 | 27.321 | 944 | 25791.024 | 8472.5804 | 134.9167 | 0 | 0 | 0 | 0 | 15 | 1440 | 0 | 1042 | 1150 | 1072 | 108 | 8472.5804 | 44.6667 | 0 | 0 | 24 | 28.3 | 24.9 | 23.98 | 1002 | 50.07 | 0.9322 | 87.82 | 84.91 |  | 12771 | 11931 | -840 | 0 | 0 | 0 | 14 | 2.3
| 2017-11-21 | 66 | 51% | 80 | 52 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3693 | 3226 | 3226 | 3158 | 3255 | 43 | 0 | 48 | 0 | 60 | 0 | 97 | -68 | 139 | 97.57% | 153.875 | 85.51% | 100% | 90.07% | 7.9 | 137.11 | 1083.169 | 26.908 | 948 | 25508.784 | 8420.5044 | 134.4167 | 0 | 0 | 0 | 0 | 15 | 1440 | 0 | 1033 | 1150 | 1072 | 117 | 8420.5044 | 44.6667 | 0 | 0 | 24 | 28 | 24.73 | 24.45 | 1000.5 | 50.07 | 0.9324 | 87.42 | 84.87 |  | 12741 | 11885 | -856 | 0 | 0 | 0 | 12.1 | 3.3
| 2017-11-22 | 65.3 | 49.9% | 81 | 52 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3692 | 3221 | 3221 | 3159 | 3252 | 43 | 0 | 48 | 0 | 60 | 0 | 93 | -62 | 138 | 98.19% | 153.8333 | 85.56% | 100% | 90.07% | 8.01 | 134.29 | 1075.6629 | 27.021 | 945 | 25534.845 | 8423.7125 | 134.2083 | 0 | 0 | 0 | 0 | 15 | 1440 | 0 | 1033 | 1147 | 1072 | 114 | 8423.7125 | 44.6667 | 0 | 0 | 24 | 28 | 24.9 | 24.2 | 999.7 | 50.08 | 0.9333 | 87.2 | 84.6 |  | 12775 | 11974 | -801 | 0 | 0 | 0 | 11.45 | 6.52
| 2017-11-23 | 65.3 | 51.1% | 83 | 52 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 3685 | 3395 | 3395 | 3332 | 3430 | 43 | 0 | 48 | 0 | 60 | 0 | 98 | -63 | 153 | 93.41% | 153.5417 | 90.42% | 100% | 94.48% | 7.9 | 134.42 | 1061.918 | 29.213 | 948 | 27693.924 | 8630.2047 | 141.4583 | 0 | 0 | 0 | 0 | 10 | 1200 | 0 | 1032 | 1141 | 1257 | 109 | 8630.2047 | 52.375 | 1.069 | 1.051 | 24 | 27.9 | 24.6 | 24.7 | 998.04 | 50.04 | 0.9331 | 86.9 | 84.4 |  | 12727 | 11965 | 0 | 2.12 | 20 | 20 | 11.27 | 6.55
| 2017-11-24 | 63.67 | 54.58% | 80 | 53 | 6 | 1 | 6 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 3702 | 3606 | 3606 | 859 | 884 | 43 | 1079 | 48 | 1075 | 60 | 1076 | 39 | -2747 | 151 | 24.39% | 154.25 | 23.2% | 25.24% | 24.52% | 1.751 | 132.45 | 231.9199 | 8.213 | 944 | 7753.072 | 9295.6833 | 150.25 | 20 | 16 | 24 | 22 | 2 | 364 | 14 | 247 | 284 | 353 | 37 | 9295.6833 | 14.7083 | 0.421 | 0.421 | 0 | 6.95 | 6.52 | 6.037 | 999.79 | 50.09 | 0.9333 | 83.4 | 84.38 |  | 12849 | 11969 | -880 | 0.842 | 5.7 | 5.7 | 0 | 0
| 2017-11-25 | 61.5 | 57.8% | 78 | 52 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3696 | 3636 | 3636 | 0 | 0 | 43 | 1440 | 48 | 1440 | 60 | 1440 | 15 | -3636 | 0 | no data | 154 | no data | 0% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 151.5 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999.7 | 50.06 | -- | -- | -- | -- | -- | -- | #VALUE! | 0 | 0 | 0 | 0 | 0
Week 49 | 2017-11-26 | 65 | 59% | 80 | 56 | 4 | 3 | 4 | 10 | 19 | 9 | 17 | 24 | 1 | 52 | 3694 | 3635 | 3596 | 656 | 682 | 44 | 1150 | 48 | 1044 | 60 | 1163 | 35 | -2940 | 156 | 18.22% | 153.9167 | 17.76% | 22.11% | 19.17% | 2.066 | 141.69 | 292.7315 | 6.82 | 944 | 6438.08 | 10260.3834 | 151.4583 | 24 | 48 | 18 | 146 | 16 | 165 | 9 | 193 | 276 | 213 | 83 | 10260.3834 | 8.875 | 0.192 | 0.187 | 26 | 5.55 | 6.65 | 6.05 | 1001.04 | 50.09 | 0.9303 | 88.57 | 86 |  | 12640 | 12074 | -566 | 0.379 | 2.43 | 2.55 | 1.53 | 3.75
| 2017-11-27 | 64.8 | 61.8% | 80 | 53 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 11 | 6 | 3693 | 3560 | 3403 | 3374 | 3474 | 45 | 0 | 48 | 0 | 60 | 0 | 100 | -29 | 157 | 92.2% | 153.875 | 91.36% | 100% | 94.73% | 8.285 | 136.69 | 1132.4767 | 29.715 | 943 | 28021.245 | 8640.7 | 148.3333 | 0 | 0 | 0 | 0 | 15 | 774 | 0 | 1083 | 1151 | 1240 | 68 | 8640.7 | 51.6667 | 1.069 | 1.059 | 26 | 28.69 | 24.77 | 24.85 | 998.71 | 50.09 | 0.9324 | 91.16 | 85.74 |  | 12453 | 11910 | -543 | 2.128 | 11.25 | 11.17 | 15.5 | 4.63
| 2017-11-28 | 66.1 | 56.6% | 82 | 55 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3690 | 3662 | 3662 | 3593 | 3703 | 45 | 0 | 47 | 0 | 62 | 0 | 110 | -69 | 157 | 98.27% | 153.75 | 97.37% | 100% | 100% | 8.376 | 134.51 | 1126.6558 | 31.915 | 946 | 30191.59 | 8716.4614 | 152.5833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1081 | 1138 | 1484 | 57 | 8716.4614 | 61.8333 | 2.291 | 2.288 | 26 | 28.64 | 24.97 | 24.36 | 995.1 | 50.07 | 0.9331 | 91.49 | 85.38 |  | 12456 | 12072 | -384 | 4.579 | 24 | 24 | 15.8 | 4.25
| 2017-11-29 | 66.95 | 55.47% | 81 | 56 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3687 | 3674 | 3674 | 3620 | 3729 | 46 | 0 | 48 | 0 | 62 | 0 | 109 | -54 | 161 | 96.51% | 153.625 | 98.18% | 100% | 100% | 8.425 | 133.98 | 1128.7815 | 32.059 | 951 | 30488.109 | 8733.9477 | 153.0833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1098 | 1139 | 1492 | 41 | 8733.9477 | 62.1667 | 2.32 | 2.32 | 27.25 | 28.85 | 25.17 | 24.39 | 997.4 | 50.01 | 0.9334 | 93.18 | 85.21 |  | 12356 | 12130 | -226 | 4.64 | 24 | 24 | 19.35 | 6.35
| 2017-11-30 | 66.58 | 54.37% | 80 | 58 | 15 | 22 | 19 | 34 | 0 | 0 | 0 | 0 | 4 | 30 | 3690 | 3241 | 3241 | 2515 | 2591 | 45 | 453 | 48 | 248 | 62 | 249 | 80 | -726 | 154 | 70.1% | 153.75 | 68.16% | 78.62% | 70.05% | 7.717 | 132.58 | 1023.1199 | 22.65 | 947 | 21449.55 | 8935.4552 | 135.0417 | 18 | 70 | 21 | 17 | 19 | 921 | 4 | 721 | 933 | 937 | 212 | 8935.4552 | 39.0417 | 0.427 | 1.177 | 28 | 19.3 | 20.23 | 21.89 | 998.25 | 50.07 | 0.9351 | 95.11 | 84.88 |  | 12322 | 12073 | -249 | 1.604 | 6.55 | 18.73 | 10.9 | 9.65
| 2017-12-01 | [25 empty] | 0 | 0 |  | no data | no data | no data | #DIV/0! | no data |  |  | 0 |  |  | 0 | no data | 0 | [10 empty] | 0 | no data | 0 | [14 empty] | 0 | 0
| 2017-12-02 | [25 empty] | 0 | 0 |  | no data | no data | no data | #DIV/0! | no data |  |  | 0 |  |  | 0 | no data | 0 | [10 empty] | 0 | no data | [15 empty] | 0 | 0
| Monthly | 65.8317 | 70.69% | 76.4667 | 59.0667 | 633 | 48 | 413 | 23 | 50 | 37 | 48 | 48 | 8 | 28 | 110975 | 83640 | 81470 | 69724.27 | 71879 | 44 | 4714 | 46.4 | 17134 | 60.2 | 4586 | 2207.73 | -11877 | 117.8 | 86.32% | 154.1319 | 64.87% | 80.52% | 69.66% | 139.726 | 96.0637 | 19089.2395 | 622.7443 | 911.1731 | 587790.3268 | 8703.9931 | 116.1667 | 106 | 664 | 153 | 880 | 636 | 33819 | 53 | 27710 | 19924 | 24245 | -7786 | 8703.9931 | 1010.2083 | 7.789 | 8.503 | 22.8417 | 25.184 | 14.842 | 14.4929 | 998.773 | 50.082 | 0.67516 | 90.9841 | 61.6672 | 0 | 13620.7931 | 8688.1034 | -4932.6897 | 16.292 | 93.93 | 106.15 | 528.57 | 164.87
| Totals | Avg.F | % Avg. | M Avg | m Avg | hrs | min | hrs | min | hrs | min | hrs | min | Avg Int Avi | Avg Ext Avi | MWhr Total | MWhr Total | MWhr Total | MWhr Total | MWhr Total | MW Avg | Total min | Avg MW | Total min | Avg MW | Total min | MWhr | Total MW | Av Max D/Gen | Av. DailyLF | Avg. | Avg. |  | Avg. | Total | Avg. |  | Total | Avg. |  | Avg. | [7 empty] | Total |  |  |  |  | Avg. | [20 empty] | 164.87
| Weeks data | Site Avg. Amb. Temp F | Site Avg. Relative humidity % | Max: Site Maximum/Minumum Temperature; CT1 hrs: CT-1 Base Load Hours; CT2 hrs: CT-2 Base Load Hours; CT1 hrs: CT-1 stand by hours / min; CT2 hrs: CT-2 standby hours / min; CT2 hrs: Plant ambient Corrected maximum Load hours/min | Average Corrected Plant Capacity | Ambient Corrected Declared Avail'y (MWH) | Av Plant WAPDA Dispatch | Net Plant Export (MWH) | Gross Generation | CT1 Av Cap (MW) | CT1 Unavail minutes | CT2 Av Cap (MW) | CT2 Unavail minutes | ST Unavail minutes | ST Average Cap (MW) | Plant Aux Load including Colony Load MWH | Differenece (+/-) MW | Maximum Daily Generation | Daily Load Factor | Avg. Corrected Plant | Plant Capacity Facto | Plant Availability Factor | Equivalent Plant Availability | LBtu gas flow mmscf | 1 LBtu gas (Average Btu/scf) | LBTU MMBTU | PL gas flow (mscf/week) | 1 PL gas (Average Btu/scf) | HBTU MMBTU | Plant Net Heat Rate (Btu/Kwh) | [11 empty] | 112
| Week 40 | 72.8143 | 75.41% | 81.5714 | 66 | 143 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3664.1429 | 1295.1429 | 1295.1429 | 1180 | 1235.1429 | 44.5714 | 2001 | 45 | 10080 | 420 | 319.2857 | 409 | -806 | 66.5714 | 77.47% | 152.6726 | 32.2% | 55.1% | 34.44% | no data | no data | #VALUE! | 79.2573 | 942.599 | 74707.8517 | 9181.0441
| Week 41 | 66.0943 | 85.82% | 72.7143 | 62.1429 | 168 | 0 | 44 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 3707.1429 | 1955.1429 | 1955.1429 | 13478 | 13993 | 44 | No outage | 318 | 1038.8571 | 420 | no data | 515 | -208 | 95.7143 | 90.49% | 154.4643 | 51.9% | 78.16% | 55.45% | no data | no data | #VALUE! | 123.88 | 934.4286 | 115757.0114 | 8767.976 | [5 empty] | 0.27381
| Week 42 | 63.9271 | 75.56% | 73.1429 | 60.7143 | 156 | 49 | 151 | 51 | 8 | 28 | 8 | 24 | 0 | 0 | 3709.8571 | 3222.2857 | 2971.1429 | 20379 | 20993 | 44.1429 | No outage | 321 | no data | 420 | no data | 624 | -419 | 137.2857 | 91.02% | 154.5774 | 78.48% | 99.12% | 88.37% | 49.62 | 139.6643 | 6930.1419 | 152.127 | 945.6667 | 143861.433 | 8700.1659 | [5 empty] | 0.26672
| Week 43 | 64.6671 | 53.05% | 80.1429 | 52.7143 | 121 | 34 | 121 | 38 | 24 | 0 | 24 | 0 | 4 | 0 | 3693.7143 | 3379.7143 | 3348.8571 | 16751 | 17247 | 43 | 2519 | 334 | no data | 420 | no data | 525 | -6691 | 122.5714 | 84.48% | 153.9048 | 75.62% | 75.03% | 79.26% | 41.251 | 115.8629 | 4779.4587 | 145.03 | 811.2857 | 117660.7671 | 8623.1656
| Week 44 | 65.886 | 0.57448 | 80.6 | 55.6 | 91 | 25 | 95 | 44 | 19 | 9 | 17 | 24 | 65 | 28 | 3690.8 | 3554.4 | 3515.2 | 13758 | 14179 | 45 | 3669 | 336 | 258.4 | #REF! | 282.4 | 434 | -3818 | 157 | 75.06% | 153.7833 | 74.57% | #DIV/0! | 76.79% | 34.869 | 135.89 | 4738.3484 | 123.159 | 946.2 | 116533.0458 | 9057.3895
| Date | Plant Status Whether Normal Operation or Tripping (State full detail for trippings/return to normal).
| 2017-11-01 | Plant load remained 61~62 MW from 0000~2400 hrs. CT-2 is shutdown for scheduled outage activities of 2017.
| 2017-11-02 | Plant load remained 60~63 MW from 0000~2400 hrs. CT-2 is shutdown for scheduled outage activities of 2017.
| 2017-11-03 | Complex tripped @ 0245 hrs due to "Wapda Supply Failure". After restoration of reliable Wapda Supply, CT-1 synch @ 1237 hrs & STG synch @ 1343 hrs.
| 2017-11-04 | Plant load remained 60~62 MW from 0000~2400 hrs. CT-2 is shutdown for scheduled outage activities of 2017.
| 2017-11-05 | Plant load remained 60~62 MW from 0000~2400 hrs. CT-2 is shutdown for scheduled outage activities of 2017.
| 2017-11-06 | Plant load remained 61~62 MW from 0000~2400 hrs. CT-2 is shutdown for scheduled outage activities of 2017.
| 2017-11-07 | Plant load remained 60~62 MW from 0000~2400 hrs. CT-2 is shutdown for scheduled outage activities of 2017.
| 2017-11-08 | Plant load remained 60~62 MW from 0000~2400 hrs. CT-2 is shutdown for scheduled outage activities of 2017.
| 2017-11-09 | Gas turbine CT-2 synch @ 1046hrs and de-synch @ 1142hrs due to hot gas leakage. CT-2 again synch @ 1508hrs and de-synch @ 2318hrs for balancing purpose during scheduled outage period and CT2 is still not commercially available.
| 2017-11-10 | Gas turbine CT-2 synch @ 1018 hrs after balancing during scheduled outage.
| 2017-11-11 | Plant load restricted to 129~132 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-11-12 | Plant load restricted to 129~133 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-11-13 | Plant load remained 128 MW from 0000~0537 hrs at "Wapda Demand" & 128~133 MW from 0537~2400 hrs to remain within contractual heat rate.
| 2017-11-14 | Plant load restricted to 128~132 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-11-15 | CT-1 de-sync @ 0246 hrs, STG de-sync @ 0248 hrs, CT-2 de-sync @ 0250 at Wapda demand of 0 MW. CT-1 sync @ 0621 hrs, CT-2 sync @ 0621 hrs & STG synch @ 0723 hrs after receiving Wapda despatch of full load demand.
| 2017-11-16 | CT-1 de-synch @0037hrs, STG de-synch @0040hrs & CT-2 de-synch @0040hrs at Wapda demand of 0 MW.CT-1 synch @ 0530 hrs, STG synch @ 0632 hrs & CT-2 synch @ 1028 hrs after receiving Wapda demand of maximum load.WAPDA despatch of 128 MW received @2206hrs.
| 2017-11-17 | WAPDA despatch of 128MW followed from 0000~0432 hrs. From 0432~2400 plant load restricted to 131~135 MW hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-11-18 | Plant load restricted to 131~135 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-11-19 | Plant load remained 120 MW from 0041~0101 hrs & 110 MW from 0101~0535 MW on Wapda Demand.
| 2017-11-20 | Plant load restricted to 131~134 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-11-21 | Plant load restricted to 128~135 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-11-22 | Plant load restricted to 130~134 MW from 0000~2400 hrs as both duct burners kept off to remain within contractual heat rate.
| 2017-11-23 | Plant load increased from 132 to 149 MW by taking DBs into service at 1100 hrs.
| 2017-11-24 | CT-1 de-synch @ 0601 hrs, STG de-synch @ 0604 hrs & CT-2 de-synch @ 0605 hrs due to suspension of HBTU gas by SNGPL.
| 2017-11-25 | Plant remained shutdown due to suspension of HBTU gas by M/S SNGPL.
| 2017-11-26 | After restoration of HBTU gas supply by M/S SNGPL, CT-2 synch @ 1724 hrs, CT-1 synch @ 1909 hrs & STG synch @ 1923 hrs. Wapda load despatch of 128 MW received @ 2222 hrs.
| 2017-11-27 | Plant load remained 128~131 MW from 00:00 to 05:53 hrs at Wapda demand. Plant load increased from 133 to 148 MW @ 1254 hrs by taking duct burners into service to achieve ambient corrected export.
| 2017-11-28 | Normal operation. Plant remained at base load throughout the day.
| 2017-11-29 | Normal operation. “Annual Dependable Capacity (ADC) Test” for the year 2017 carried out successfully.
| 2017-11-30 | CT-1 desynch @0445hrs & synch @0745hrs after replacement of inlet air filters. CT-1 de-synch @ 1927 hrs, STG de-synch @ 1951 hrs & CT-2 de-synch @ 1952 hrs due to suspension of HBTU gas by SNGPL.
Note on Y24: ops.e: Offline washing

## Dec
Monthly Operational Returns Kabirwala
2017-12-01
| Date | Site Avg. Ambient Temp.F | Site Avg. Relative Humidty % | Site Ambient Temp |  | Base load hours |  |  |  | Standby hours |  |  |  | Plant ambient corrected Max Load |  | Corrected Plant Capacity | Ambient Corrected Daclared Avail'y (MWH) | Plant WAPDA Dispatch (MWH) | Net Plant Export (MWH) | Gross Generation | CT1 Average Cap (MW) | CT1 Unavail minutes | CT2 Average Cap (MW) | CT2 Unavail minutes | ST Average Cap (MW) | ST Unavail minutes | Plant Aux Load including Colony Load MWH | Differenece (+/-) MW | Maximum Daily Generation | Daily Load Factor | Avg. Corrected Plant Capacity | Plant Capacity Factor | Plant Availability Factor | Equivalent Plant Availability | LBtu gas flow (mmscf/day) | 1 LBtu gas (Average Btu/scf) | LBTU MMBTU | 1 HBtu gas flow (mmscf/day) | 1 HBtu gas (Average Btu/scf) | HBTU MMBTU | HHV Net Heat Rate (Btu/Kwh) | Avg. declared availability | CT1 Derated MW | CT1 derated mintutes | CT-2 derated MW | CT-2 derated mintutes | ST derated MW | ST derated mintutes | WAPDA Backfeed (MWH) | CT-1 Gross Generation (MWH) | CT-2 Gross Generation (MWH) | STG Gross Generation (MWH) | CT-1 & CT-2 MWH difference | Base load Heat Rate | STG load | DB1 | DB2 | CT1 | CT1 Gas flow | CT2 Gas flow |  | Pamb | Freq. Hz | LBTU Gas Specific gravity | CT-1 compressor efficiency(%) | CT-2 compressor efficiency(%) | CT-1 Heat Rate (Btu/Kwh) | CT-2 Heat Rate (Btu/Kwh) |  | DB(1+2) | DB-1 Ops Hours | DB-2 Ops Hours | CT-1 Wetcomprssion Ops Hours | RO Operation Hours
[6 empty] | CT1 |  | CT2 |  | CT1 |  | CT2 | [43 empty] | mmscf/d | mmscf/d | WetC flow | HBTU KPPH | HBTU KPPH | LBTU KPPH | mbar | Hz | [6 empty] | mmscf/d
|  |  |  | Max | Min | hrs | min | hrs | min | hrs | min | hrs | min | hrs | min | [42 empty] | gpm
Week 49 | 2017-11-26 | 65 | 59% | 80 | 56 | 4 | 3 | 4 | 10 | 19 | 9 | 17 | 24 | 1 | 52 | 3694 | 3635 | 3596 | 656 | 682 | 44 | 0 | 48 | 0 | 60 | 0 | 35 | -2940 | 156 | 18.22% | 153.9167 | 17.76% | 100% | 97.07% | 2.066 | 141.69 | 292.7315 | 6.54 | 944 | 6173.76 | 9857.4566 | 151.4583 | 24 | 48 | 18 | 146 | 16 | 165 | 9 | 193 | 276 | 213 | 83 | 9857.4566 | 8.875 | 0.192 | 0.187 | 26 | 5.55 | 6.65 | 6.05 | 1001.04 | 50.09 | 0.9303 | 88.57 | 86 | 12640 | 12074 | -566 | 0.379 | 2.43 | 2.55 | 1.53 | 3.75
| 2017-11-27 | 64.8 | 61.8% | 80 | 53 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 11 | 6 | 3693 | 3560 | 3403 | 3374 | 3474 | 45 | 0 | 48 | 0 | 60 | 0 | 100 | -29 | 157 | 92.2% | 153.875 | 91.36% | 100% | 94.73% | 8.285 | 136.69 | 1132.4767 | 29.527 | 943 | 27843.961 | 8588.1558 | 148.3333 | 0 | 0 | 0 | 0 | 15 | 774 | 0 | 1083 | 1151 | 1240 | 68 | 8588.1558 | 51.6667 | 1.069 | 1.059 | 26 | 28.69 | 24.77 | 24.85 | 998.71 | 50.09 | 0.9324 | 91.16 | 85.74 | 12453 | 11910 | -543 | 2.128 | 11.25 | 11.17 | 15.5 | 4.63
| 2017-11-28 | 66.1 | 56.6% | 82 | 55 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3690 | 3662 | 3662 | 3593 | 3703 | 45 | 0 | 47 | 0 | 62 | 0 | 110 | -69 | 157 | 98.27% | 153.75 | 97.37% | 100% | 100% | 8.09 | 134.51 | 1088.1859 | 31.915 | 946 | 30191.59 | 8705.7545 | 152.5833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1081 | 1138 | 1484 | 57 | 8705.7545 | 61.8333 | 2.291 | 2.288 | 26 | 28.64 | 24.97 | 24.36 | 995.1 | 50.07 | 0.9331 | 91.49 | 85.38 | 12456 | 12072 | -384 | 4.579 | 24 | 24 | 15.8 | 4.25
| 2017-11-29 | 66.95 | 55.47% | 81 | 56 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3687 | 3674 | 3674 | 3620 | 3729 | 46 | 0 | 48 | 0 | 62 | 0 | 109 | -54 | 161 | 96.51% | 153.625 | 98.18% | 100% | 100% | 8.425 | 133.98 | 1128.7815 | 32.059 | 951 | 30488.109 | 8733.9477 | 153.0833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1098 | 1139 | 1492 | 41 | 8733.9477 | 62.1667 | 2.32 | 2.32 | 27.25 | 28.85 | 25.17 | 24.39 | 997.4 | 50.01 | 0.9334 | 93.18 | 85.21 | 12356 | 12130 | -226 | 4.64 | 24 | 24 | 19.35 | 6.35
| 2017-11-30 | 66.58 | 54.37% | 80 | 58 | 15 | 22 | 19 | 34 | 0 | 0 | 0 | 0 | 4 | 30 | 3690 | 3241 | 3241 | 2515 | 2591 | 45 | 453 | 48 | 248 | 62 | 249 | 80 | -726 | 154 | 70.1% | 153.75 | 68.16% | 78.62% | 70.05% | 7.3 | 132.58 | 967.834 | 21.94 | 947 | 20777.18 | 8646.1288 | 135.0417 | 18 | 70 | 21 | 17 | 19 | 921 | 4 | 721 | 933 | 937 | 212 | 8646.1288 | 39.0417 | 0.427 | 1.177 | 28 | 19.3 | 20.23 | 21.89 | 998.25 | 50.07 | 0.9351 | 95.11 | 84.88 | 12322 | 12073 | -249 | 1.604 | 6.55 | 18.73 | 10.9 | 9.65
| 2017-12-01 | 64 | 62% | 82 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3701 | 3669 | 3669 | 0 | 0 | 45 | 1440 | 48 | 1440 | 60 | 1440 | 14 | -3669 | 0 | no data | 154.2083 | no data | 0% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 152.875 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 996.9 | 50.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2017-12-02 | 63.8 | 58.1% | 82 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3702 | 3669 | 3669 | 0 | 0 | 45 | 1440 | 48 | 1440 | 60 | 1440 | 12 | -3669 | 0 | no data | 154.25 | no data | 0% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 152.875 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 996.8 | 50.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Week 50 | 2017-12-03 | 62 | 62% | 76 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3707 | 3669 | 3669 | 0 | 0 | 45 | 1440 | 48 | 1440 | 60 | 1440 | 12 | -3669 | 0 | no data | 154.4583 | no data | 0% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 152.875 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 998.4 | 50.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2017-12-04 | 62 | 56.2% | 77 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3706 | 3671 | 3671 | 0 | 0 | 45 | 1440 | 48 | 1440 | 60 | 1440 | 14 | -3671 | 0 | no data | 154.4167 | no data | 0% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 152.9583 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 998 | 50.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2017-12-05 | 60.1 | 38.4% | 77 | 52 | 0 | 0 | 3 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 3710 | 2971 | 2971 | 341 | 359 | 45 | 1440 | 51 | 1048 | 60 | 1195 | 28 | -2630 | 73 | 20.49% | 154.5833 | 9.191% | 15.44% | 9.354% | 2.643 | 143.64 | 379.6405 | 2.987 | 954 | 2849.598 | 9469.9077 | 123.7917 | 0 | 0 | 25 | 165 | 39 | 245 | 10 | 0 | 273 | 86 | 273 | 9469.9077 | 3.5833 | 0 | 0.074 | 0 | 0 | 21.8 | 34.2 | 999 | 50.07 | 0.9334 | 0 | 84.97 | 0 | 13607 | 13607 | 0.074 | 0 | 3.78 | 0 | 0
| 2017-12-06 | 58.4 | 44% | 75 | 46 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3712 | 1747 | 1747 | 1719 | 1785 | 45 | 1440 | 50 | 0 | 60 | 0 | 66 | -28 | 75 | 99.17% | 154.6667 | 46.31% | 70.97% | 47.74% | 11.59 | 139.01 | 1611.1259 | 13.994 | 952 | 13322.288 | 8687.2681 | 72.7917 | 0 | 0 | 0 | 0 | 36 | 1440 | 0 | 0 | 1208 | 577 | 1208 | 8687.2681 | 24.0417 | 0 | 0.764 | 0 | 0 | 24.5 | 33.5 | 999.3 | 50.05 | 0.9364 | 0 | 85.2 | 0 | 11760 | 11760 | 0.764 | 0 | 24 | 0 | 0
| 2017-12-07 | 60.91 | 45.36% | 79 | 45 | 0 | 0 | 21 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 3704 | 1932 | 1932 | 1549 | 1607 | 45 | 1440 | 50 | 125 | 60 | 129 | 60 | -383 | 75 | 89.28% | 154.3333 | 41.82% | 64.7% | 42.2% | 10.55 | 136.54 | 1440.497 | 13.749 | 956 | 13144.044 | 9415.4558 | 80.5 | 0 | 0 | 19 | 21 | 38 | 1311 | 2 | 0 | 1083 | 524 | 1083 | 9415.4558 | 21.8333 | 0 | 0.707 | 0 | 0 | 21.87 | 29.78 | 999.08 | 50.05 | 0.937 | 0 | 85.18 | 0 | 11746 | 11746 | 0.707 | 0 | 21.57 | 0 | 2
| 2017-12-08 | 62 | 50.8% | 82 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3704 | 3670 | 3670 | 0 | 0 | 45 | 1440 | 50 | 1440 | 60 | 1440 | 16 | -3670 | 0 | no data | 154.3333 | no data | 0% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 152.9167 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999.2 | 50.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2017-12-09 | 60.6 | 54.8% | 77 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3708 | 3671 | 3671 | 0 | 0 | 45 | 1440 | 50 | 1440 | 60 | 1440 | 12 | -3671 | 0 | no data | 154.5 | no data | 0% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 152.9583 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 996.7 | 50.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Week 51 | 2017-12-10 | 59 | 63.3% | 67 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 3685 | 3685 | 0 | 0 | 45 | 1440 | 50 | 1440 | 60 | 1440 | 11 | -3685 | 0 | no data | 155 | no data | 0% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 153.5417 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 998.6 | 50.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2017-12-11 | 56.7 | 81.8% | 59 | 55 | 0 | 0 | 12 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 2466 | 2466 | 907 | 947 | 45 | 1440 | 50 | 604 | 60 | 712 | 45 | -1559 | 75 | 52.61% | 155 | 24.38% | 38.3% | 25.76% | 6.36 | 144.22 | 917.2392 | 7.865 | 955.87 | 7517.9176 | 9300.0626 | 102.75 | 0 | 0 | 22 | 114 | 35 | 728 | 5 | 0 | 641 | 306 | 641 | 9300.0626 | 12.75 | 0 | 0.602 | 0 | 0 | 13.54 | 17.97 | 996.3 | 50.03 | 0.9331 | 0 | 85.45 | 0 | 11914 | 11914 | 0.602 | 0 | 12.02 | 0 | 4.67
| 2017-12-12 | 52.2 | 85.8% | 57 | 47 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 1753 | 1753 | 1725 | 1790 | 45 | 1440 | 49 | 0 | 60 | 0 | 65 | -28 | 76 | 98.14% | 155 | 46.37% | 70.78% | 48.05% | 11.2 | 137.07 | 1535.184 | 14.174 | 949 | 13451.126 | 8687.7159 | 73.0417 | 0 | 0 | 0 | 0 | 35 | 1440 | 0 | 0 | 1186 | 604 | 1186 | 8687.7159 | 25.1667 | 0 | 1.084 | 0 | 0 | 23.97 | 32.17 | 997.3 | 49.98 | 0.9363 | 0 | 85.23 | 0 | 11753 | 11753 | 1.084 | 0 | 24 | 0 | 4.37
| 2017-12-13 | 52 | 86% | 55 | 48 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 1760 | 1760 | 1729 | 1795 | 46 | 1440 | 49 | 0 | 60 | 0 | 66 | -31 | 76 | 98.41% | 155 | 46.48% | 70.32% | 47.74% | 11.17 | 135.68 | 1515.5456 | 14.198 | 951 | 13502.298 | 8685.8552 | 73.3333 | 0 | 0 | 0 | 0 | 35 | 1440 | 0 | 0 | 1188 | 607 | 1188 | 8685.8552 | 25.2917 | 0 | 1.122 | 0 | 0 | 23.95 | 32.72 | 1000.7 | 50.03 | 0.9372 | 0 | 85.11 | 0 | 11773 | 11773 | 1.122 | 0 | 24 | 0 | 2.3
| 2017-12-14 | 54 | 80% | 60 | 48 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 1760 | 1760 | 1732 | 1798 | 46 | 1440 | 49 | 0 | 60 | 0 | 66 | -28 | 76 | 98.57% | 155 | 46.56% | 70.32% | 47.1% | 11.3 | 137.45 | 1553.185 | 14.165 | 953 | 13499.245 | 8690.7794 | 73.3333 | 0 | 0 | 0 | 0 | 36 | 1440 | 0 | 0 | 1180 | 618 | 1180 | 8690.7794 | 25.75 | 0 | 1.185 | 0 | 0 | 23.8 | 32.76 | 1003 | 49.99 | 0.9362 | 0 | 85.23 | 0 | 11778 | 11778 | 1.185 | 0 | 24 | 0 | 5.75
| 2017-12-15 | 53.14 | 74.51% | 67 | 43 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 1742 | 1742 | 1721 | 1787 | 46 | 1440 | 50 | 0 | 60 | 0 | 66 | -21 | 76 | 97.97% | 155 | 46.26% | 70.51% | 48.08% | 11.29 | 134.29 | 1516.1341 | 14.089 | 952 | 13412.728 | 8674.5277 | 72.5833 | 0 | 0 | 0 | 0 | 35 | 1440 | 0 | 0 | 1188 | 599 | 1188 | 8674.5277 | 24.9583 | 0 | 0.992 | 0 | 0 | 23.92 | 32.77 | 1004.42 | 50.03 | 0.9375 | 0 | 84.88 | 0 | 11755 | 11755 | 0.992 | 0 | 24 | 0 | 0
| 2017-12-16 | 57 | 53.8% | 71 | 46 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3717 | 1740 | 1740 | 1715 | 1780 | 46 | 1440 | 50 | 0 | 60 | 0 | 65 | -25 | 76 | 97.59% | 154.875 | 46.14% | 70.51% | 47.44% | 11.295 | 136.65 | 1543.4618 | 14.068 | 947 | 13322.396 | 8668.1386 | 72.5 | 0 | 0 | 0 | 0 | 36 | 1440 | 0 | 0 | 1194 | 586 | 1194 | 8668.1386 | 24.4167 | 0 | 0.878 | 0 | 0 | 24.2 | 32.5 | 1005 | 50.08 | 0.9367 | 0 | 84.9 | 0 | 11788 | 11788 | 0.878 | 0 | 24 | 0 | 6.13
Week 52 | 2017-12-17 | 59.9 | 47.7% | 74 | 48 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3711 | 1733 | 1733 | 1704 | 1768 | 46 | 1440 | 50 | 0 | 60 | 0 | 64 | -29 | 75 | 98.22% | 154.625 | 45.92% | 70.51% | 47.44% | 11.37 | 137.92 | 1568.1504 | 13.925 | 949 | 13214.825 | 8675.455 | 72.2083 | 0 | 0 | 0 | 0 | 36 | 1440 | 0 | 0 | 1186 | 582 | 1186 | 8675.455 | 24.25 | 0 | 0.829 | 0 | 0 | 24 | 32.6 | 1005.5 | 50.03 | 0.9364 | 0 | 85 | 0 | 11787 | 11787 | 0.829 | 0 | 24 | 0 | 0
| 2017-12-18 | 61.8 | 50.5% | 77 | 51 | 0 | 0 | 14 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 3706 | 2535 | 2535 | 1042 | 1081 | 46 | 1440 | 50 | 544 | 60 | 549 | 47 | -1493 | 74 | 60.87% | 154.4167 | 28.12% | 43.74% | 29.27% | 7.125 | 135.28 | 963.87 | 8.622 | 943 | 8130.546 | 8727.8464 | 105.625 | 0 | 0 | 20 | 22 | 36 | 891 | 8 | 0 | 728 | 353 | 728 | 8727.8464 | 14.7083 | 0 | 0.446 | 0 | 0 | 24.19 | 32.44 | 1004.3 | 50.04 | 0.9373 | 0 | 84.92 | 0 | 11854 | 11854 | 0.446 | 0 | 24 | 0 | 0
| 2017-12-19 | 62.7 | 56.3% | 73 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3708 | 3684 | 3684 | 0 | 0 | 46 | 1440 | 50 | 1440 | 60 | 1440 | 12 | -3684 | 0 | no data | 154.5 | no data | 0% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 153.5 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1003.3 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2
| 2017-12-20 | 63 | 74% | 76 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3713 | 3684 | 3684 | 0 | 0 | 46 | 1440 | 50 | 1440 | 60 | 1440 | 12 | -3684 | 0 | no data | 154.7083 | no data | 0% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 153.5 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1002.7 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2017-12-21 | 62.2 | 72.2% | 82 | 50 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 3701 | 3684 | 3684 | 105 | 114 | 45 | 1440 | 48 | 1275 | 60 | 1380 | 18 | -3579 | 65 | 7.308% | 154.2083 | 2.837% | 5.229% | 3.086% | 0.998 | 143.9 | 143.6122 | 0.861 | 948 | 816.228 | 9141.3352 | 153.5 | 0 | 0 | 20 | 116 | 40 | 60 | 9 | 0 | 98 | 16 | 98 | 9141.3352 | 0.66667 | 0 | 0 | 0 | 0 | 2.54 | 2.92 | 1003.9 | 50.01 | 0.9341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2017-12-22 | 64.3 | 60.6% | 81 | 56 | 20 | 56 | 24 | 0 | 0 | 0 | 0 | 0 | 13 | 27 | 3702 | 3268 | 3268 | 3202 | 3303 | 46 | 128 | 49 | 0 | 60 | 0 | 101 | -66 | 154 | 89.37% | 154.25 | 86.49% | 97.36% | 90.09% | 11.13 | 136.7 | 1521.471 | 27.895 | 944 | 26332.88 | 8699.0478 | 136.1667 | 30 | 56 | 0 | 0 | 23 | 633 | 0 | 972 | 1183 | 1148 | 211 | 8699.0478 | 47.8333 | 0.907 | 0.903 | 28 | 26.14 | 24.66 | 31.6 | 1002.4 | 50.1 | 0.9367 | 91.74 | 85.76 | 12499 | 11975 | -524 | 1.81 | 13.6667 | 13.5833 | 14.03 | 9.52
| 2017-12-23 | 62.1 | 68% | 76 | 52 | 0 | 47 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 3707 | 1802 | 1802 | 1768 | 1837 | 46 | 1374 | 49 | 0 | 60 | 0 | 69 | -34 | 150 | 51.03% | 154.4583 | 47.69% | 71.68% | 49.69% | 11.14 | 135.27 | 1506.9078 | 14.597 | 952 | 13896.344 | 8712.2465 | 75.0833 | 17 | 19 | 0 | 0 | 35 | 1393 | 0 | 46 | 1167 | 624 | 1121 | 8712.2465 | 26 | 0.03 | 0.947 | 28 | 1.3 | 23.88 | 31.73 | 998 | 50.04 | 0.9369 | 94.93 | 85.29 | 12368 | 11879 | -489 | 0.977 | 0.87 | 24 | 0.75 | 0
Week 53 | 2017-12-24 | 62 | 67% | 76 | 53 | 4 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3709 | 2063 | 2063 | 2018 | 2093 | 45 | 1142 | 48 | 0 | 60 | 0 | 75 | -45 | 150 | 58.14% | 154.5417 | 54.41% | 76.67% | 57.33% | 10.88 | 135.87 | 1478.2656 | 16.897 | 962 | 16254.914 | 8787.5023 | 85.9583 | 25 | 34 | 0 | 0 | 29 | 1440 | 0 | 208 | 1153 | 732 | 945 | 8787.5023 | 30.5 | 0.328 | 1.198 | 28 | 5.79 | 23.79 | 31.81 | 997.63 | 50.06 | 0.9368 | 92.4 | 84.96 | 12649 | 11947 | -702 | 1.526 | 4.55 | 24 | 3.53 | 5.25 | 0.45
| 2017-12-25 | 61.6 | 65.6% | 74 | 50 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 3698 | 3586 | 3586 | 3497 | 3605 | 45 | 0 | 48 | 0 | 60 | 0 | 108 | -89 | 158 | 95.07% | 154.0833 | 94.56% | 100% | 98.09% | 10.877 | 136.33 | 1482.8614 | 31.428 | 920 | 28913.76 | 8692.1994 | 149.4167 | 0 | 0 | 0 | 0 | 5 | 840 | 0 | 1085 | 1157 | 1363 | 72 | 8692.1994 | 56.7917 | 1.691 | 1.965 | 28 | 29.29 | 25.4 | 31.6 | 1000.3 | 50.08 | 0.9368 | 91.11 | 84.67 | 12694 | 12516 | -178 | 3.656 | 24 | 24 | 15.5 | 6.8 | 19.45
| 2017-12-26 | 62 | 67% | 74 | 53 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 19 | 57 | 3708 | 3646 | 3562 | 3503 | 3610 | 45 | 0 | 48 | 0 | 60 | 0 | 107 | -59 | 157 | 95.81% | 154.5 | 94.47% | 100% | 98.68% | 10.938 | 133.62 | 1461.5356 | 30.171 | 960 | 28964.16 | 8685.6111 | 151.9167 | 0 | 0 | 0 | 0 | 12 | 243 | 0 | 1090 | 1144 | 1376 | 54 | 8685.6111 | 57.3333 | 1.688 | 1.688 | 28 | 28.37 | 23.34 | 31.9 | 999.6 | 50.08 | 0.9377 | 91.27 | 84.55 | 12235 | 11884 | -351 | 3.376 | 24 | 24 | 16.2 | 7 | 4.55
| 2017-12-27 | 61 | 73% | 71 | 55 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 20 | 22 | 3715 | 3642 | 3562 | 3498 | 3602 | 45 | 0 | 47 | 0 | 60 | 0 | 104 | -64 | 155 | 96.83% | 154.7917 | 94.16% | 100% | 98.61% | 10.856 | 137.02 | 1487.4891 | 29.798 | 971 | 28933.858 | 8696.7831 | 151.75 | 0 | 0 | 0 | 0 | 14 | 218 | 0 | 1090 | 1134 | 1378 | 44 | 8696.7831 | 57.4167 | 1.764 | 1.749 | 28 | 28.05 | 22.81 | 32.08 | 998.6 | 50.03 | 0.9366 | 92.12 | 84.43 | 12106 | 11787 | -319 | 3.513 | 24 | 24 | 17.68 | 4.35
| 2017-12-28 | 60.8 | 70% | 72 | 53 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 21 | 19 | 3715 | 3618 | 3552 | 3489 | 3596 | 45 | 0 | 47 | 0 | 60 | 0 | 107 | -63 | 155 | 96.67% | 154.7917 | 93.92% | 100% | 99.04% | 10.9 | 136.45 | 1487.305 | 29.671 | 976 | 28958.896 | 8726.3402 | 150.75 | 0 | 0 | 0 | 0 | 13 | 161 | 0 | 1082 | 1131 | 1383 | 49 | 8726.3402 | 57.625 | 1.691 | 1.669 | 28 | 27.76 | 22.65 | 32.29 | 1000.08 | 50.02 | 0.9369 | 91.43 | 84.15 | 12710 | 12461 | -249 | 3.36 | 24 | 24 | 14.6 | 3.9
| 2017-12-29 | 59.3 | 62% | 77 | 48 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3713 | 3615 | 3615 | 3541 | 3650 | 44 | 0 | 48 | 0 | 60 | 0 | 109 | -74 | 156 | 97.49% | 154.7083 | 95.37% | 100% | 100% | 10.91 | 137.58 | 1500.9978 | 30.358 | 966 | 29325.828 | 8705.6836 | 150.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1062 | 1155 | 1433 | 93 | 8705.6836 | 59.7083 | 1.935 | 1.937 | 28 | 27.77 | 23.38 | 32.54 | 1000.7 | 50.06 | 0.9364 | 87.76 | 83.99 | 13108 | 12513 | -595 | 3.872 | 24 | 24 | 8.9 | 5.6
| 2017-12-30 | 58.7 | 58.1% | 77 | 47 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3714 | 3609 | 3609 | 3535 | 3641 | 44 | 0 | 48 | 0 | 60 | 0 | 106 | -74 | 158 | 96.02% | 154.75 | 95.18% | 100% | 100% | 10.905 | 138.98 | 1515.5769 | 30.399 | 962 | 29243.838 | 8701.3904 | 150.375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1053 | 1161 | 1427 | 108 | 8701.3904 | 59.4583 | 1.926 | 1.926 | 28 | 27.63 | 23.66 | 32.5 | 1000 | 50.04 | 0.9358 | 92.12 | 84.03 | 12434 | 12069 | -365 | 3.852 | 24 | 24 | 5.9 | 6.45
| 2017-12-31 | 58 | 61.9% | 73 | 48 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3714 | 3617 | 3617 | 3536 | 3644 | 44 | 0 | 48 | 0 | 60 | 0 | 108 | -81 | 157 | 96.71% | 154.75 | 95.21% | 100% | 100% | 11.004 | 137.44 | 1512.3898 | 30.052 | 968 | 29090.336 | 8654.617 | 150.7083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1061 | 1158 | 1425 | 97 | 8654.617 | 59.375 | 1.901 | 1.891 | 28 | 27.54 | 23.23 | 32.67 | 999.5 | 50.07 | 0.9364 | 87.31 | 84.1 | 12205 | 11742 | -463 | 3.792 | 24 | 24 | 8.28 | 5.47
| Monthly | 59.9113 | 62.93% | 73.4194 | 49.8065 | 194 | 7 | 648 | 7 | 0 | 0 | 0 | 0 | 35 | 52 | 115025 | 91361 | 91131 | 47673.08 | 49192 | 45.2258 | 32884 | 48.9677 | 16556 | 60 | 16925 | 1667.92 | -43555 | 78.7742 | 81.44% | 154.6035 | 58.27% | 51.84% | 60.67% | 216.431 | 97.6423 | 29642.4456 | 403.963 | 677.1248 | 386098.0536 | 8720.6553 | 122.797 | 72 | 109 | 106 | 438 | 568 | 18243 | 149 | 8749 | 22696 | 17747 | 13947 | 8720.6553 | 739.4583 | 13.861 | 24.556 | 9.0323 | 7.4077 | 15.7768 | 21.5177 | 1000.1681 | 50.0468 | 0.66447 | 29.4255 | 57.4839 | 4032.5161 | 8138.3226 | 4105.8065 | 38.417 | 187.0867 | 458.9533 | 105.37 | 80.76
| Totals | Avg.F | % Avg. | M Avg | m Avg | hrs | min | hrs | min | hrs | min | hrs | min | Avg Int Avi | Avg Ext Avi | MWhr Total | MWhr Total | MWhr Total | MWhr Total | MWhr Total | MW Avg | Total min | Avg MW | Total min | Avg MW | Total min | MWhr | Total MW | Av Max D/Gen | Av. DailyLF | Avg. | Avg. |  | Avg. | Total | Avg. |  | Total | Avg. |  | Avg. | [7 empty] | Total |  |  |  |  | Avg. | [19 empty] | 78.49
| Weeks data | Site Avg. Amb. Temp F | Site Avg. Relative humidity % | Max: Site Maximum/Minumum Temperature; CT1 hrs: CT-1 Base Load Hours; CT2 hrs: CT-2 Base Load Hours; CT1 hrs: CT-1 stand by hours / min; CT2 hrs: CT-2 standby hours / min; CT2 hrs: Plant ambient Corrected maximum Load hours/min | Average Corrected Plant Capacity | Ambient Corrected Declared Avail'y (MWH) | Av Plant WAPDA Dispatch | Net Plant Export (MWH) | Gross Generation | CT1 Av Cap (MW) | CT1 Unavail minutes | CT2 Av Cap (MW) | CT2 Unavail minutes | ST Unavail minutes | ST Average Cap (MW) | Plant Aux Load including Colony Load MWH | Differenece (+/-) MW | Maximum Daily Generation | Daily Load Factor | Avg. Corrected Plant | Plant Capacity Facto | Plant Availability Factor | Equivalent Plant Availability | LBtu gas flow mmscf | 1 LBtu gas (Average Btu/scf) | LBTU MMBTU | PL gas flow (mscf/week) | 1 PL gas (Average Btu/scf) | HBTU MMBTU | Plant Net Heat Rate (Btu/Kwh) | [11 empty] | 206.5
| Week 49 | 65.3186 | 58.19% | 81 | 55 | 91 | 25 | 95 | 44 | 19 | 9 | 17 | 24 | 65 | 28 | 3693.8571 | 3587.1429 | 3559.1429 | 1965.4286 | 2025.5714 | 45 | 3333 | 47.8571 | 3128 | 426 | no data | no data | -11156 | 112.1429 | 75.06% | 153.9107 | 74.57% | 68.37% | 92.37% | 34.166 | 97.0643 | 3316.2984 | 121.981 | 675.8571 | 82441.7301 | 8906.2887 | [7 empty] | 33
| Week 50 | 60.8586 | 50.22% | 77.5714 | 46.7143 | 0 | 0 | 49 | 102 | 0 | 0 | 0 | 0 | 0 | 36 | 3707.2857 | 3047.2857 | 3047.2857 | no data | no data | 45 | 10080 | 347 | 990.4286 | 420 | 1012 | 208 | -17722 | no data | 69.65% | 154.4702 | 32.44% | no data | 33.1% | no data | no data | #VALUE! | no data | no data | #VALUE! | 9190.8772 | [5 empty] | 0.27381 |  | 0.55
| Week 51 | 54.8629 | 75.03% | 62.2857 | 48.4286 | 0 | 0 | 132 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 3719.5714 | 2129.4286 | 2129.4286 | no data | no data | 45.5714 | 10080 | 347 | 292 | 420 | 307.4286 | 384 | -5377 | no data | 90.55% | 154.9821 | 42.7% | no data | 44.03% | no data | no data | #VALUE! | no data | no data | #VALUE! | 8784.5132 | [5 empty] | 0.26672 |  | 10.55
| Week 52 | 62.2857 | 61.33% | 77 | 52 | 21 | 43 | 87 | 23 | 0 | 0 | 0 | 0 | 14 | 14 | 3706.8571 | 2912.8571 | 2912.8571 | 7821 | 8103 | 45.8571 | 8702 | 346 | no data | 420 | no data | 323 | -12569 | 74 | 61.36% | 154.4524 | 42.21% | 41.22% | 43.91% | 41.763 | 98.4386 | 4111.0901 | 65.9 | 676.5714 | 44586.0571 | 8791.1862
| Week 53 | 60.425 | 0.65575 | 74.25 | 50.875 | 172 | 24 | 192 | 0 | 0 | 0 | 0 | 0 | 143 | 38 | 3710.75 | 3424.5 | 3395.75 | 26617 | 27441 | 44.625 | 8404 | 344 | no data | #REF! | no data | 824 | -549 | 155.75 | 91.59% | 154.6146 | 89.66% | 97.08% | 93.97% | 87.27 | 136.6612 | 11926.4273 | 228.774 | 960.625 | 219766.0237 | 8706.2659
| Date | Plant Status Whether Normal Operation or Tripping (State full detail for trippings/return to normal).
| 2017-12-01 | Plant remained shutdown due to suspension of HBTU gas by M/S SNGPL.
| 2017-12-02 | Plant remained shutdown due to suspension of HBTU gas by M/S SNGPL.
| 2017-12-03 | Plant remained shutdown due to suspension of HBTU gas by M/S SNGPL.
| 2017-12-04 | Plant remained shutdown due to suspension of HBTU gas by M/S SNGPL.
| 2017-12-05 | CT-2 synch@ 1728 hrs & and STG synch @ 1955 hrs after restoration of partial RLNG quota by SNGPL.
| 2017-12-06 | Plant load remained restricted to 70~73 MW due to curtailment of HBTU gas by M/S SNGPL.
| 2017-12-07 | STG de-synch @ 2151 hrs & CT-2 de-synch @ 2155 hrs due to suspension of HBTU gas by SNGPL.
| 2017-12-08 | Plant remained shutdown due to suspension of HBTU gas by M/S SNGPL.
| 2017-12-09 | Plant remained shutdown due to suspension of HBTU gas by M/S SNGPL.
| 2017-12-10 | Plant remained shutdown due to suspension of HBTU gas by M/S SNGPL.
| 2017-12-11 | After restoration of partial RLNG quota by SNGPL, CT-2 synch @ 1004hrs and STG synch @ 1152hrs.
| 2017-12-12 | Plant load remained restricted to 70~73 MW due to curtailment of HBTU gas by M/S SNGPL.
| 2017-12-13 | Plant load remained restricted to 71~73 MW due to curtailment of HBTU gas by M/S SNGPL.
| 2017-12-14 | Plant load remained restricted to 71~73 MW due to curtailment of HBTU gas by M/S SNGPL.
| 2017-12-15 | Plant load remained restricted to 70~73 MW due to curtailment of HBTU gas by M/S SNGPL.
| 2017-12-16 | Plant load remained restricted to 70~72 MW due to curtailment of HBTU gas by M/S SNGPL.
| 2017-12-17 | Plant load remained restricted to 70~72 MW due to curtailment of HBTU gas by M/S SNGPL.
| 2017-12-18 | STG de-synch @ 1451 hrs & CT-2 de-synch @ 1456 hrs due to suspension of HBTU gas by SNGPL.
| 2017-12-19 | Plant remained shutdown due to suspension of HBTU gas by M/S SNGPL.
| 2017-12-20 | Plant remained shutdown due to suspension of HBTU gas by M/S SNGPL.
| 2017-12-21 | After restoration of partial RLNG quota by SNGPL, CT-2 synch @ 2115 hrs and STG synch @ 2300 hrs.
| 2017-12-22 | CT-1 synch @0208 hrs after restoration of partial RLNG quota by SNGPL. Plant load increased to base load after increase in HBTU gas quota form 25 to 30mmscfd by SNGPL.
| 2017-12-23 | CT-1 desynch @0106 hrs due to curtailment of RLNG by SNGPL. Plant load remained restricted to 69~71 MW from 0106hrs~2400hrs due to curtailment of HBTU gas by M/S SNGPL.
| 2017-12-24 | Plant load remained restricted to 69~71 MW from 0000~1902hrs due to curtailment of HBTU gas by M/S SNGPL. CT-1 synch @1902 hrs after increase in HBTU (RLNG) gas quota from 13 to 30 mmscfd by SNGPL.
| 2017-12-25 | Plant load remained restricted to 141~145 MW from 0000~1400hrs due to curtailment of HBTU gas by M/S SNGPL.
| 2017-12-26 | Normal operation. WAPDA load demand of 135 MW received from 0124 hrs to 0518 hrs.
| 2017-12-27 | Normal operation. WAPDA load demand of 132MW received from 0123hrs to 0455hrs.
| 2017-12-28 | Normal operation. WAPDA load demand of 132 MW received from 0145 hrs to 0426 hrs.
| 2017-12-29 | Normal operation.Plant remained at maximum load from 0000 to 2400 hrs.
| 2017-12-30 | Normal operation.Plant remained at maximum load from 0000 to 2400 hrs.
| 2017-12-31 | Normal operation.Plant remained at maximum load from 0000 to 2400 hrs.