## Jan
Monthly Operational Returns Kabirwala
2018-01-01
| Date | Site Avg. Ambient Temp.F | Site Avg. Relative Humidty % | Site Avg. Ambient Wetbulb Temp.F | Site Ambient Temp |  | Base load hours |  |  |  | Standby hours |  |  |  | Plant ambient corrected Max Load |  | Corrected Plant Capacity | Ambient Corrected Daclared Avail'y (MWH) | Plant WAPDA Dispatch (MWH) | Net Plant Export (MWH) | Gross Generation | CT1 Average Cap (MW) | CT1 Unavail minutes | CT2 Average Cap (MW) | CT2 Unavail minutes | ST Average Cap (MW) | ST Unavail minutes | Plant Aux Load including Colony Load MWH | Differenece (+/-) MW | Maximum Daily Generation | Daily Load Factor | Avg. Corrected Plant Capacity | Plant Capacity Factor | Plant Availability Factor | Equivalent Plant Availability | LBtu gas flow (mmscf/day) | 1 LBtu gas (Average Btu/scf) | LBTU MMBTU | 1 HBtu gas flow (mmscf/day) | 1 HBtu gas (Average Btu/scf) | HBTU MMBTU | HHV Net Heat Rate (Btu/Kwh) | Avg. declared availability | CT1 Derated MW | CT1 derated mintutes | CT-2 derated MW | CT-2 derated mintutes | ST derated MW | ST derated mintutes | WAPDA Backfeed (MWH) | CT-1 Gross Generation (MWH) | CT-2 Gross Generation (MWH) | STG Gross Generation (MWH) | CT-1 & CT-2 MWH difference | Base load Heat Rate | STG load | DB1 | DB2 | CT1 | CT1 Gas flow | CT2 Gas flow |  | Pamb | Freq. Hz | LBTU Gas Specific gravity | CT-1 compressor efficiency(%) | CT-2 compressor efficiency(%) |  | CT-1 Heat Rate (Btu/Kwh) | CT-2 Heat Rate (Btu/Kwh) |  | DB(1+2) | DB-1 Ops Hours | DB-2 Ops Hours | CT-1 Wetcomprssion Ops Hours | RO Operation Hours | CT1 T/G Brg |  | CT2 T/G Brg
[7 empty] | CT1 |  | CT2 |  | CT1 |  | CT2 | [43 empty] | mmscf/d | mmscf/d | WetC flow | HBTU KPPH | HBTU KPPH | LBTU KPPH | mbar | Hz | [7 empty] | mmscf/d |  |  |  |  | Supply air pressure | Seal air pressure | Supply air pressure | Seal air pressure
[5 empty] | Max | Min | hrs | min | hrs | min | hrs | min | hrs | min | hrs | min | [42 empty] | gpm | [17 empty] | Psi | "WC | Psi | "WC
Week 1 | 2018-01-01 | 57.8 | 65.4% | 48.38 | 72 | 47 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3716 | 3660 | 3660 | 3585 | 3692 | 45 | 0 | 48 | 0 | 60 | 0 | 107 | -75 | 157 | 97.98% | 154.8333 | 96.47% | 100% | 100% | 11.021 | 138.08 | 1521.7797 | 30.292 | 978 | 29625.576 | 8688.2443 | 152.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1080 | 1151 | 1461 | 71 | 8688.2443 | 60.875 | 2.051 | 2.051 | 28 | 27.57 | 22.83 | 32.52 | 997.4 | 50.05 | 0.9363 | 89.61 | 83.99 | -5.62 | 12005 | 11649 | -356 | 4.102 | 24 | 24 | 13.72 | 1.07 | 2.2 | 3.5 | 2.25 | 0.7
| 2018-01-02 | 58.1 | 64.4% | 48.58 | 71 | 47 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3715 | 3663 | 3663 | 3590 | 3698 | 45 | 0 | 48 | 0 | 60 | 0 | 108 | -73 | 156 | 98.77% | 154.7917 | 96.64% | 100% | 100% | 11.055 | 136.8 | 1512.324 | 30.429 | 981 | 29850.849 | 8736.2599 | 152.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1089 | 1140 | 1469 | 51 | 8736.2599 | 61.2083 | 2.114 | 2.114 | 28 | 27.68 | 22.72 | 31.99 | 997.4 | 49.97 | 0.9366 | 90.76 | 83.83 | -6.93 | 11945 | 11673 | -272 | 4.228 | 24 | 24 | 16.6 | 5.73 | 2.1 | 3.5 | 2.25 | 0.7
| 2018-01-03 | 57.3 | 67.51% | 48.75 | 70 | 48 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3719 | 3667 | 3667 | 3598 | 3706 | 45 | 0 | 48 | 0 | 61 | 0 | 108 | -69 | 157 | 98.35% | 154.9583 | 96.75% | 100% | 100% | 11.075 | 137.72 | 1525.249 | 30.338 | 978.904 | 29697.9896 | 8677.9429 | 152.7917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1095 | 1141 | 1470 | 46 | 8677.9429 | 61.25 | 2.044 | 2.044 | 27.5 | 27.81 | 22.64 | 32.39 | 997.8 | 49.98 | 0.9363 | 91.09 | 83.77 | -7.32 | 11939 | 11656 | -283 | 4.088 | 24 | 24 | 17.48 | 7.17 | 2.1 | 3.7 | 2.25 | 0.7
| 2018-01-04 | 50.75 | 80.17% | 45.75 | 60 | 42 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3720 | 3694 | 3694 | 3611 | 3718 | 46 | 0 | 47 | 0 | 62 | 0 | 107 | -83 | 157 | 98.67% | 155 | 97.07% | 100% | 100% | 11.1 | 138.69 | 1539.459 | 30.518 | 979 | 29877.122 | 8700.244 | 153.9167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1094 | 1138 | 1486 | 44 | 8700.244 | 61.9167 | 2.171 | 2.171 | 27.5 | 27.86 | 22.73 | 32.15 | 997.4 | 50.03 | 0.9359 | 88.94 | 83.45 | -5.49 | 11978 | 11700 | -278 | 4.342 | 24 | 24 | 13.07 | 6.8 | 2.1 | 3.5 | 2.25 | 0.7
| 2018-01-05 | 52.95 | 72.74% | 46.17 | 64 | 43 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3720 | 3711 | 3711 | 3630 | 3740 | 45 | 0 | 48 | 0 | 63 | 0 | 110 | -81 | 158 | 98.63% | 155 | 97.58% | 100% | 100% | 11.06 | 138.48 | 1531.5888 | 30.977 | 981 | 30388.437 | 8793.3955 | 154.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1078 | 1146 | 1516 | 68 | 8793.3955 | 63.1667 | 2.324 | 2.324 | 27.4 | 27.67 | 22.95 | 32.22 | 998 | 50.06 | 0.9359 | 88.08 | 83.41 | -4.67 | 12070 | 11724 | -346 | 4.648 | 24 | 24 | 11.25 | 5.72 | 2.1 | 3.5 | 2.25 | 0.6
| 2018-01-06 | 56 | 64% | 46.96 | 67 | 48 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3720 | 3689 | 3689 | 3602 | 3710 | 45 | 0 | 47 | 0 | 62 | 0 | 108 | -87 | 157 | 98.46% | 155 | 96.83% | 100% | 100% | 11.065 | 139.83 | 1547.219 | 30.865 | 977 | 30155.105 | 8801.3115 | 153.7083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1074 | 1138 | 1498 | 64 | 8801.3115 | 62.4167 | 2.234 | 2.234 | 27.5 | 27.8 | 22.95 | 31.9 | 997.8 | 50.01 | 0.9357 | 89.02 | 83.51 | -5.51 | 12142 | 11778 | -364 | 4.468 | 24 | 24 | 13 | 7.1 | 2.2 | 3.5 | 2.25 | 0.7
| 2018-01-07 | 57 | 64% | 47.96 | 67 | 47 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3720 | 3675 | 3675 | 3588 | 3697 | 45 | 0 | 47 | 0 | 62 | 0 | 109 | -87 | 156 | 98.74% | 155 | 96.45% | 100% | 100% | 11.015 | 137.87 | 1518.6381 | 30.422 | 979 | 29783.138 | 8724.0179 | 153.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1079 | 1137 | 1481 | 58 | 8724.0179 | 61.7083 | 2.118 | 2.116 | 28 | 27.6 | 22.68 | 31.9 | 998 | 50.07 | 0.9368 | 89.91 | 83.48 | -6.43 | 12033 | 11701 | -332 | 4.234 | 24 | 24 | 14.8 | 3.3 | 2.1 | 3.25 | 2.25 | 0.8
Week 2 | 2018-01-08 | 57 | 69% | 50.29 | 69 | 47 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3719 | 3667 | 3667 | 3585 | 3692 | 45 | 0 | 47 | 0 | 62 | 0 | 107 | -82 | 155 | 99.25% | 154.9583 | 96.4% | 100% | 100% | 11.07 | 138.8 | 1536.516 | 30.58 | 980 | 29968.4 | 8787.9821 | 152.7917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1084 | 1127 | 1481 | 43 | 8787.9821 | 61.7083 | 2.168 | 2.156 | 28 | 27.78 | 22.65 | 32.11 | 999.1 | 50.03 | 0.9366 | 90.42 | 83.47 | -6.95 | 12041 | 11771 | -270 | 4.324 | 24 | 24 | 16.1 | 3.2 | 2.1 | 3.7 | 2.2 | 0.5
| 2018-01-09 | 57.6 | 71.3% | 50.42 | 71.6 | 48.6 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3719 | 3652 | 3652 | 3557 | 3666 | 46 | 0 | 47 | 0 | 60 | 0 | 109 | -95 | 156 | 97.92% | 154.9583 | 95.64% | 100% | 100% | 11.06 | 134.96 | 1492.6576 | 30.409 | 974 | 29618.366 | 8746.4222 | 152.1667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1100 | 1123 | 1443 | 23 | 8746.4222 | 60.125 | 1.975 | 1.966 | 28 | 28.25 | 22.81 | 31.77 | 1000 | 50.09 | 0.9374 | 92.3 | 83.4 | -8.9 | 12443 | 12213 | -230 | 3.941 | 24 | 24 | 15.65 | 5.6 | 2.1 | 3.6 | 2.2 | 0.4
| 2018-01-10 | 57 | 69% | 48.4 | 77 | 42 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 20 | 12 | 3718 | 3640 | 3559 | 3493 | 3601 | 45 | 0 | 46 | 0 | 60 | 0 | 108 | -66 | 156 | 96.18% | 154.9167 | 93.95% | 100% | 98.64% | 11.14 | 137.14 | 1527.7396 | 29.722 | 971.008 | 28860.2998 | 8699.6964 | 151.6667 | 0 | 0 | 0 | 0 | 13 | 228 | 0 | 1081 | 1119 | 1401 | 38 | 8699.6964 | 58.375 | 1.815 | 1.804 | 28 | 27.99 | 22.72 | 32.28 | 1001 | 50.03 | 0.9364 | 89.67 | 83.18 | -6.49 | 12655 | 12386 | -269 | 3.619 | 24 | 24 | 13.6 | 7.23 | 2.1 | 3 | 2.23 | 0.6
| 2018-01-11 | 61 | 63.8% | 51 | 74 | 48 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 19 | 7 | 3707 | 3644 | 3532 | 3470 | 3575 | 45 | 0 | 47 | 0 | 60 | 0 | 105 | -62 | 155 | 96.1% | 154.4583 | 93.61% | 100% | 98.26% | 11.07 | 135.56 | 1500.6492 | 29.668 | 972 | 28837.296 | 8742.9237 | 151.8333 | 0 | 0 | 0 | 0 | 13 | 293 | 0 | 1069 | 1118 | 1388 | 49 | 8742.9237 | 57.8333 | 1.693 | 1.672 | 27.4 | 27.67 | 22.68 | 31.94 | 998.67 | 50.07 | 0.9375 | 90.09 | 83.52 | -6.57 | 12609 | 12319 | -290 | 3.365 | 24 | 24 | 15.38 | 7.03 | 2.12 | 3.4 | 2.25 | 0.6
| 2018-01-12 | 62.5 | 64.1% | 52.5 | 75 | 54 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 19 | 24 | 3707 | 3643 | 3535 | 3465 | 3571 | 45 | 0 | 48 | 0 | 60 | 0 | 106 | -70 | 157 | 94.77% | 154.4583 | 93.47% | 100% | 98.25% | 11.025 | 136.71 | 1507.2278 | 29.415 | 977 | 28738.455 | 8728.9128 | 151.7917 | 0 | 0 | 0 | 0 | 14 | 276 | 0 | 1077 | 1105 | 1389 | 28 | 8728.9128 | 57.875 | 1.792 | 1.781 | 27.98 | 27.7 | 22.21 | 31.93 | 996.63 | 50.01 | 0.9368 | 91.87 | 83.43 | -8.44 | 12088 | 11845 | -243 | 3.573 | 24 | 24 | 19.52 | 5.33 | 2.15 | 3.5 | 2.25 | 0.6
| 2018-01-13 | 60.3 | 64.3% | 50.6 | 75 | 50 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3710 | 3635 | 3635 | 3552 | 3661 | 45 | 0 | 46 | 0 | 60 | 0 | 109 | -83 | 156 | 97.78% | 154.5833 | 95.74% | 100% | 100% | 11.05 | 135.55 | 1497.8275 | 29.971 | 987 | 29581.377 | 8749.776 | 151.4583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1087 | 1116 | 1458 | 29 | 8749.776 | 60.75 | 2.074 | 2.074 | 27.6 | 27.65 | 22.27 | 31.88 | 997.3 | 50.07 | 0.9372 | 91.92 | 83.4 | -8.52 | 11962 | 11747 | -215 | 4.148 | 24 | 24 | 20.07 | 5.47 | 2.2 | 3.4 | 2.25 | 0.7
| 2018-01-14 | 60.9 | 60.7% | 50.3 | 75 | 51 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3709 | 3649 | 3649 | 3566 | 3675 | 46 | 0 | 47 | 0 | 60 | 0 | 109 | -83 | 157 | 97.53% | 154.5417 | 96.14% | 100% | 100% | 11.07 | 136.21 | 1507.8447 | 30.088 | 987 | 29696.856 | 8750.6171 | 152.0417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1102 | 1115 | 1458 | 13 | 8750.6171 | 60.75 | 2.038 | 2.038 | 28 | 27.95 | 22.27 | 31.9 | 997.17 | 50.09 | 0.937 | 93.15 | 83.38 | -9.77 | 11924 | 11736 | -188 | 4.076 | 24 | 24 | 23 | 7.17 | 2.25 | 3.7 | 2.24 | 0.7
Week 3 | 2018-01-15 | 60.66 | 62.34% | 50.37 | 75 | 49 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3709 | 3650 | 3650 | 3566 | 3675 | 45 | 0 | 47 | 0 | 61 | 0 | 109 | -84 | 157 | 97.53% | 154.5417 | 96.14% | 100% | 100% | 11.03 | 135.04 | 1489.4912 | 30.211 | 985 | 29757.835 | 8762.5704 | 152.0833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1085 | 1119 | 1471 | 34 | 8762.5704 | 61.2917 | 2.126 | 2.126 | 28 | 27.75 | 22.41 | 31.73 | 998.1 | 50.1 | 0.9373 | 91.59 | 83.45 | -8.14 | 12017 | 11758 | -259 | 4.252 | 24 | 24 | 19.38 | 7.3 | 2.2 | 4.1 | 2.25 | 0.75
| 2018-01-16 | 60.06 | 63.55% | 50.29 | 72 | 49 | 24 | 0 | 6 | 37 | 0 | 0 | 0 | 0 | 6 | 34 | 3713 | 2350 | 2350 | 2308 | 2393 | 45 | 0 | 47 | 978 | 61 | 0 | 85 | -42 | 156 | 63.92% | 154.7083 | 62.16% | 79.14% | 64.36% | 3.27 | 141.62 | 463.0974 | 20.618 | 986 | 20329.348 | 9008.8585 | 97.9167 | 0 | 0 | 23 | 65 | 29.7 | 1045.8 | 0 | 1092 | 352 | 949 | -740 | 9008.8585 | 39.5417 | 2.389 | 0.602 | 28 | 27.79 | 7.31 | 9.74 | 993.58 | 50.12 | 0.9347 | 91.99 | 86.34 | -5.65 | 11960 | 11486 | -474 | 2.991 | 24 | 7 | 20.88 | 6.9 | 2.2 | 4.2 | 2.25 | 3.3
| 2018-01-17 | 58.88 | 64.82% | 49.88 | 70 | 50 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3718 | 3676 | 3676 | 3602 | 3713 | 45 | 0 | 50 | 0 | 60 | 0 | 111 | -74 | 157 | 98.54% | 154.9167 | 96.88% | 100% | 100% | 11.015 | 135.09 | 1488.0164 | 30.398 | 978 | 29729.244 | 8666.6464 | 153.1667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1084 | 1187 | 1442 | 103 | 8666.6464 | 60.0833 | 1.947 | 1.947 | 28 | 27.83 | 23.34 | 31.72 | 993.9 | 50.1 | 0.9375 | 91.5 | 86.13 | -5.37 | 12074 | 11424 | -650 | 3.894 | 24 | 24 | 19.12 | 10.38 | 2.2 | 4.2 | 2.25 | 3.3
| 2018-01-18 | 59 | 62% | 50 | 73 | 49 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3712 | 3677 | 3677 | 3609 | 3718 | 45 | 0 | 49 | 0 | 60 | 0 | 109 | -68 | 158 | 98.05% | 154.6667 | 97.23% | 100% | 100% | 11.013 | 136.46 | 1502.834 | 30.689 | 971.45 | 29812.8291 | 8677.1025 | 153.2083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1092 | 1191 | 1435 | 99 | 8677.1025 | 59.7917 | 1.922 | 1.922 | 27.6 | 28.27 | 23.6 | 31.51 | 998 | 50.1 | 0.9368 | 91.69 | 86.12 | -5.57 | 12178 | 11489 | -689 | 3.844 | 24 | 24 | 19.9 | 7.4 | 2.2 | 4.2 | 2.25 | 3.2
| 2018-01-19 | 60 | 59% | 49 | 72 | 47 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 22 | 23 | 3712 | 3683 | 3649 | 3586 | 3695 | 44 | 0 | 49 | 0 | 60 | 0 | 109 | -63 | 157 | 98.06% | 154.6667 | 96.61% | 100% | 99.43% | 11.002 | 134.11 | 1475.4782 | 30.531 | 969 | 29584.539 | 8661.466 | 153.4583 | 0 | 0 | 0 | 0 | 13 | 97 | 0 | 1064 | 1194 | 1437 | 130 | 8661.466 | 59.875 | 1.922 | 1.914 | 27 | 27.8 | 23.7 | 31.56 | 998.4 | 50.07 | 0.9375 | 88.86 | 85.99 | -2.87 | 12293 | 11523 | -770 | 3.836 | 24 | 24 | 13.5 | 3.9 | 2.2 | 4.2 | 1.8 | 1.5
| 2018-01-20 | 62.9 | 55.5% | 50.4 | 75 | 52 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 18 | 52 | 3704 | 3666 | 3559 | 3505 | 3610 | 44 | 0 | 49 | 0 | 60 | 0 | 105 | -54 | 157 | 95.81% | 154.3333 | 94.63% | 100% | 98.32% | 11.007 | 136.8 | 1505.7576 | 29.509 | 974 | 28741.766 | 8629.8213 | 152.75 | 0 | 0 | 0 | 0 | 12 | 308 | 0 | 1051 | 1182 | 1377 | 131 | 8629.8213 | 57.375 | 1.613 | 1.585 | 27 | 27.3 | 23.3 | 31.4 | 996.5 | 50.03 | 0.9368 | 89.2 | 86 | -3.2 | 12198 | 11455 | -743 | 3.198 | 24 | 24 | 14 | 2.8 | 2.2 | 4.1 | 1.8 | 1.4
| 2018-01-21 | 61.2 | 57.6% | 49.4 | 76 | 50 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 3704 | 3656 | 3620 | 3552 | 3659 | 44 | 0 | 49 | 0 | 60 | 0 | 107 | -68 | 157 | 97.11% | 154.3333 | 95.9% | 100% | 99.3% | 11.004 | 136.54 | 1502.4862 | 29.966 | 977 | 29276.782 | 8665.3345 | 152.3333 | 0 | 0 | 0 | 0 | 14 | 110 | 0 | 1056 | 1180 | 1423 | 124 | 8665.3345 | 59.2917 | 1.954 | 1.945 | 27 | 27.3 | 23.3 | 31.3 | 994.2 | 50.08 | 0.9367 | 88.6 | 85.9 | -2.7 | 12178 | 11469 | -709 | 3.899 | 24 | 24 | 12.9 | 5.9 | 2.1 | 3.2 | 1.8 | 1.4
Week 4 | 2018-01-22 | 59.4 | 59.6% | 48.6 | 72 | 48 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3714 | 3667 | 3667 | 3585 | 3694 | 44 | 0 | 49 | 0 | 61 | 0 | 109 | -82 | 157 | 98.04% | 154.75 | 96.53% | 100% | 100% | 11.007 | 134.54 | 1480.8818 | 30.499 | 977 | 29797.523 | 8724.7991 | 152.7917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1049 | 1180 | 1465 | 131 | 8724.7991 | 61.0417 | 2.156 | 2.156 | 27 | 27.3 | 23.3 | 31.2 | 993 | 50.02 | 0.9374 | 88 | 85.9 | -2.1 | 12229 | 11498 | -731 | 4.312 | 24 | 24 | 10.93 | 4.48 | 2.2 | 3.6 | 1.8 | 2.2
| 2018-01-23 | 57.3 | 67.4% | 49.1 | 68 | 49 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3720 | 3675 | 3675 | 3598 | 3707 | 44 | 0 | 49 | 0 | 61 | 0 | 109 | -77 | 157 | 98.38% | 155 | 96.72% | 100% | 100% | 11.01 | 135.54 | 1492.2954 | 30.439 | 978 | 29769.342 | 8688.6152 | 153.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1065 | 1176 | 1466 | 111 | 8688.6152 | 61.0833 | 2.084 | 2.084 | 27 | 27.6 | 23.2 | 31.3 | 992 | 50.06 | 0.9368 | 89.8 | 85.8 | -4 | 12170 | 11454 | -716 | 4.168 | 24 | 24 | 14.7 | 6.16 | 2.2 | 3.5 | 1.85 | 2.3
| 2018-01-24 | 51.6 | 85% | 48.3 | 59 | 45 | 24 | 0 | 21 | 28 | 0 | 0 | 0 | 0 | 21 | 6 | 3720 | 3501 | 3501 | 3437 | 3543 | 44 | 0 | 49 | 104 | 61 | 0 | 106 | -64 | 158 | 93.43% | 155 | 92.39% | 97.7% | 94.75% | 9.7 | 138.39 | 1342.383 | 29.342 | 978 | 28696.476 | 8739.8484 | 145.875 | 0 | 0 | 24 | 48 | 31 | 174 | 0 | 1064 | 1080 | 1399 | 16 | 8739.8484 | 58.2917 | 2.16 | 1.863 | 27 | 27.48 | 29.6 | 28.95 | 994.71 | 50.06 | 0.9356 | 88.03 | 85.47 | -2.56 | 12155 | 11509 | -646 | 4.023 | 24 | 21.88 | 10.42 | 6.13 | 2.2 | 3.8 | 1.8 | 2.25 | 4
| 2018-01-25 | 49.9 | 89% | 47.3 | 57 | 45 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3720 | 3703 | 3703 | 3618 | 3725 | 44 | 0 | 49 | 0 | 63 | 0 | 107 | -85 | 156 | 99.49% | 155 | 97.26% | 100% | 100% | 10.815 | 135.31 | 1463.3776 | 30.694 | 978 | 30018.732 | 8701.5228 | 154.2917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1048 | 1176 | 1501 | 128 | 8701.5228 | 62.5417 | 2.259 | 2.259 | 27 | 27.21 | 23.46 | 30.86 | 995.21 | 50.01 | 0.9367 | 86.45 | 84.95 | -1.5 | 12199 | 11521 | -678 | 4.518 | 24 | 24 | 7.47 | 7.8 | 2.2 | 3.8 | 1.8 | 1.7 | 4.1
| 2018-01-26 | 50.2 | 86.5% | 46.9 | 60 | 44 | 21 | 26 | 24 | 0 | 0 | 0 | 0 | 0 | 21 | 10 | 3720 | 3468 | 3468 | 3450 | 3556 | 44 | 120 | 49 | 0 | 63 | 0 | 106 | -18 | 157 | 94.37% | 155 | 92.74% | 97.65% | 94.97% | 10.785 | 137.25 | 1480.2413 | 29.554 | 975 | 28815.15 | 8781.2728 | 144.5 | 0 | 0 | 22 | 34 | 31 | 170 | 0 | 968 | 1170 | 1418 | 202 | 8781.2728 | 59.0833 | 1.981 | 2.297 | 27 | 25.27 | 23.48 | 30.97 | 995.63 | 50.05 | 0.936 | 88.78 | 84.68 | -4.1 | 12157 | 11603 | -554 | 4.278 | 21.52 | 24 | 8.98 | 0 | 2.15 | 3.7 | 1.7 | 1 | 3
| 2018-01-27 | 48.99 | 88.58% | 46.54 | 55 | 46 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3720 | 3687 | 3687 | 3600 | 3709 | 44 | 0 | 49 | 0 | 62 | 0 | 109 | -87 | 156 | 99.07% | 155 | 96.77% | 100% | 100% | 10.775 | 137.34 | 1479.8385 | 30.936 | 970 | 30007.92 | 8746.5996 | 153.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1057 | 1164 | 1488 | 107 | 8746.5996 | 62 | 2.2 | 2.2 | 27 | 27.73 | 23.74 | 30.81 | 995.6 | 50.07 | 0.9359 | 86.01 | 84.29 | -1.72 | 12330 | 11751 | -579 | 4.4 | 24 | 24 | 6.73 | 5.58 | 2.2 | 3.3 | 1.8 | 1 | 3.9
| 2018-01-28 | 50.39 | 86.33% | 47.66 | 57 | 46 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3720 | 3705 | 3705 | 3618 | 3726 | 44 | 0 | 48 | 0 | 63 | 0 | 108 | -87 | 156 | 99.52% | 155 | 97.26% | 100% | 100% | 10.76 | 135.53 | 1458.3028 | 30.894 | 976 | 30152.544 | 8737.1053 | 154.375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1058 | 1154 | 1514 | 96 | 8737.1053 | 63.0833 | 2.339 | 2.339 | 27 | 27.49 | 2335 | 30.95 | 996.6 | 50.1 | 0.9365 | 86.81 | 84.14 | -2.67 | 12223 | 11696 | -527 | 4.678 | 24 | 24 | 8.28 | 5.22 | 2.2 | 3.3 | 1.8 | 1 | 4.1
Week 5 | 2018-01-29 | 55.73 | 75.73% | 49.59 | 67 | 45 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3720 | 3683 | 3683 | 3590 | 3701 | 45 | 0 | 47 | 0 | 62 | 0 | 111 | -93 | 157 | 98.22% | 155 | 96.51% | 100% | 100% | 10.73 | 138.9 | 1490.397 | 30.675 | 977 | 29969.475 | 8763.1955 | 153.4583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1070 | 1133 | 1498 | 63 | 8763.1955 | 62.4167 | 2.295 | 2.295 | 27 | 27.58 | 22.81 | 30.9 | 997.6 | 50.11 | 0.9353 | 89.16 | 83.95 | -5.21 | 12130 | 11720 | -410 | 4.59 | 24 | 24 | 13.98 | 7.28 | 2.2 | 3.3 | 1.8 | 1.9 | 4.2
| 2018-01-30 | 61.6 | 61.3% | 51.6 | 73 | 52 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 3711 | 3496 | 3496 | 3411 | 3514 | 45 | 0 | 46 | 0 | 62 | 0 | 103 | -85 | 155 | 94.46% | 154.625 | 91.92% | 100% | 95.51% | 10.68 | 133.92 | 1430.2656 | 28.789 | 982.0005 | 28270.8124 | 8707.44 | 145.6667 | 0 | 0 | 0 | 0 | 15 | 660 | 0 | 1085 | 1110 | 1319 | 25 | 8707.44 | 54.9583 | 1.389 | 1.356 | 27 | 27.89 | 22.43 | 30.55 | 998.6 | 50.09 | 0.9377 | 92.22 | 83.85 | -8.37 | 12089 | 11784 | -305 | 2.745 | 24 | 24 | 20.7 | 7.3 | 2.2 | 4 | 1.8 | 2.3 | 4.2
| 2018-01-31 | 63 | 58% | 51 | 75 | 52 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3704 | 3236 | 3236 | 3164 | 3259 | 44 | 0 | 47 | 0 | 62 | 0 | 95 | -72 | 153 | 88.75% | 154.3333 | 85.42% | 100% | 88.89% | 10.7 | 134.24 | 1436.368 | 26.059 | 980 | 25537.82 | 8525.3439 | 134.8333 | 0 | 0 | 0 | 0 | 17 | 1440 | 0 | 1059 | 1116 | 1084 | 57 | 8525.3439 | 45.1667 | 0.095 | 0.095 | 27.5 | 27.38 | 22.45 | 30.37 | 996.4 | 50.07 | 0.9375 | 90.33 | 84.05 | -6.28 | 12144 | 11723 | -421 | 0.19 | 1 | 1 | 15.6 | 2.5 | 2.1 | 3.5 | 1.8 | 2.2 | 2.9
| 2018-02-01 | [26 empty] | 0 | 0 |  | no data | no data | no data | #DIV/0! | no data |  |  | 0 |  |  | 0 | no data | 0 | [10 empty] | 0 | no data | 0 | [11 empty] | 0 |  |  | 0 | 0 |  |  |  |  | 2.1 | 3.8 | 1.8 | 1 | 3.8
| 2018-02-02 | [26 empty] | 0 | 0 |  | no data | no data | no data | #DIV/0! | no data |  |  | 0 |  |  | 0 | no data | [11 empty] | 0 | no data | 0 | [11 empty] | 0 |  |  | 0 | 0
| 2018-02-03 | [26 empty] | 0 | 0 |  | no data | no data | no data | #DIV/0! | no data |  |  | 0 |  |  | 0 | no data | [11 empty] | 0 | no data | 0 | [11 empty] | 0 |  |  | 0 | 0
| 2018-02-04 | [26 empty] | 0 | 0 |  | no data | no data | no data | #DIV/0! | no data |  |  | 0 |  |  | 0 | no data | [11 empty] | 0 | no data | 0 | [11 empty] | 0 |  |  | 0 | 0
| Monthly | 57.3229 | 68.47% | 49.0965 | 69.1484 | 47.7613 | 741 | 26 | 724 | 5 | 0 | 0 | 0 | 0 | 1 | 58 | 115160 | 111468 | 110990 | 108893.93 | 111999 | 44.7419 | 3.871 | 47.8387 | 34.9032 | 61.0968 | 0 | 3105.07 | -2299 | 156.4839 | 96.19% | 154.7849 | 94.56% | 99.18% | 97.76% | 331.179 | 136.7426 | 45248.2317 | 923.497 | 977.8504 | 902947.4038 | 8707.516 |  | 0 | 0 | 69 | 147 | 202.7 | 4801.8 | 0 | 26726 | 27824 | 35185 | 1098 | 8707.516 | 1466.0417 | 48.504 | 46.592 | 686.08 | 689.56 | 2876.72 | 761.53 | 996.636 | 50.068 | 0.93674 | 89.934 | 84.5708 |  | 12175.1538 | 11799.8462 |  | 120.972 | 574.52 | 557.88 | 395.42 | 141.36
| Totals | Avg.F | % Avg. |  | M Avg | m Avg | hrs | min | hrs | min | hrs | min | hrs | min | Avg Int Avi | Avg Ext Avi | MWhr Total | MWhr Total | MWhr Total | MWhr Total | MWhr Total | MW Avg | Total min | Avg MW | Total min | Avg MW | Total min | MWhr | Total MW | Av Max D/Gen | Av. DailyLF | Avg. | Avg. |  | Avg. | Total | Avg. |  | Total | Avg. |  | Avg. | [7 empty] | Total |  |  |  |  | Avg.
| Weeks data | Site Avg. Amb. Temp F | Site Avg. Relative humidity % |  | M Avg: Site Maximum/Minumum Temperature; hrs: CT-1 Base Load Hours; hrs: CT-2 Base Load Hours; hrs: CT-1 stand by hours / min; hrs: CT-2 standby hours / min | Plant ambient Corrected maximum Load hours/min |  | Average Corrected Plant Capacity | Ambient Corrected Declared Avail'y (MWH) | Av Plant WAPDA Dispatch | Net Plant Export (MWH) | Gross Generation | CT1 Av Cap (MW) | CT1 Unavail minutes | CT2 Av Cap (MW) | CT2 Unavail minutes | ST Unavail minutes | ST Average Cap (MW) | Plant Aux Load including Colony Load MWH | Differenece (+/-) MW | Maximum Daily Generation | Daily Load Factor | Avg. Corrected Plant | Plant Capacity Facto | Plant Availability Factor | Equivalent Plant Availability | LBtu gas flow mmscf | 1 LBtu gas (Average Btu/scf) | LBTU MMBTU | PL gas flow (mscf/week) | 1 PL gas (Average Btu/scf) | HBTU MMBTU | Plant Net Heat Rate (Btu/Kwh) | [11 empty] | 114.25
| Week 1 | 55.7 | 68.32% |  | 67.2857 | 46 | 168 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 3718.5714 | 3679.8571 | 3679.8571 | 3600.5714 | 3708.7143 | 45.1429 | No outage | 47.5714 | No outage | 430 | no data | no data | -555 | 156.8571 | 98.52% | 154.9405 | 96.83% | 100% | 100% | 77.391 | 138.21 | 10696.2101 | 213.841 | 979.1291 | 209377.955 | 8731.6308
| Week 2 | 59.4714 | 66.03% |  | 73.8 | 48.6571 | 168 | -2 | 168 | 0 | 0 | 0 | 0 | -120 | 154 | 0 | 3712.7143 | 3647.1429 | 3604.1429 | 24688 | 25441 | 45.2857 | No outage | 328 | no data | 422 | no data | 753 | -541 | 156 | 97.08% | 154.6964 | 94.99% | 100% | 99.31% | 77.485 | 136.4186 | 10570.393 | 209.853 | 978.2869 | 205296.4318 | 8743.7615 | [5 empty] | 0.27381
| Week 3 | 60.3857 | 60.69% |  | 73.2857 | 49.4286 | 168 | 0 | 150 | 37 | 0 | 0 | 0 | 0 | 141 | 59 | 3710.2857 | 3479.7143 | 3454.4286 | 23728 | 24463 | 44.5714 | No outage | 340 | no data | 422 | no data | 735 | -453 | 157 | 92.72% | 154.5952 | 91.36% | 97.02% | 94.49% | 69.341 | 136.5229 | 9466.6314 | 171.956 | 977.2417 | 168042.568 | 8724.5428 | [5 empty] | 0.26672
| Week 4 | 52.54 | 80.34% |  | 61.1429 | 46.1429 | 165 | 26 | 165 | 28 | 0 | 0 | 0 | 0 | 162 | 16 | 3719.1429 | 3629.4286 | 3629.4286 | 24906 | 25660 | 44 | 120 | 342 | no data | 434 | no data | 754 | -500 | 156.7143 | 97.47% | 154.9643 | 95.67% | 99.34% | 98.53% | 74.852 | 136.2714 | 10200.189 | 212.358 | 976 | 207261.408 | 8731.3947
| Week 5 | 60.11 | 0.6501 |  | 71.6667 | 49.6667 | 72 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 3711.6667 | 3471.6667 | 3471.6667 | 10165 | 10474 | 44.6667 | #REF! | #REF! | no data | #REF! | no data | 309 | -250 | 155 | 93.81% | 154.6528 | 91.28% | #DIV/0! | 94.8% | 32.11 | 135.6867 | 4356.8989 | 85.523 | 979.6668 | 83784.0466 | 8665.3265
| Date | Plant Status Whether Normal Operation or Tripping (State full detail for trippings/return to normal).
| 2017-01-01 | Normal operation.Plant remained at maximum load from 0000 to 2400 hrs.
| 2017-01-02 | Normal operation.Plant remained at maximum load from 0000 to 2400 hrs.
| 2017-01-03 | Normal operation.Plant remained at maximum load from 0000 to 2400 hrs.
| 2017-01-04 | Normal operation.Plant remained at maximum load from 0000 to 2400 hrs.
| 2017-01-05 | Normal operation.Plant remained at maximum load from 0000 to 2400 hrs.
| 2017-01-06 | Normal operation.Plant remained at maximum load from 0000 to 2400 hrs.
| 2017-01-07 | Normal operation.Plant remained at maximum load from 0000 to 2400 hrs.
| 2017-01-08 | Normal operation.Plant remained at maximum load from 0000 to 2400 hrs.
| 2017-01-09 | Normal operation.Plant remained at maximum load from 0000 to 2400 hrs.
| 2017-01-10 | Normal operation. NPCC load demand of 132 MW received from 0112 to 0452 hrs.
| 2017-01-11 | Normal operation. NPCC load demand of 132 MW received from 0018 hrs to 0502 hrs.
| 2017-01-12 | Normal operation. NPCC load demand of 132 MW received from 0024 hrs to 0500 hrs.
| 2017-01-13 | Normal operation.Plant remained at maximum load from 0000 to 2400 hrs.
| 2017-01-14 | Normal operation.Plant remained at maximum load from 0000 to 2400 hrs.
| 2017-01-15 | Normal operation.Plant remained at maximum load from 0000 to 2400 hrs.
| 2017-01-16 | Gas turbine CT-2 de-synch @ 0025hrs and again synch@ 1743hrs after boroscopic inspection and compressor offline washing.
| 2017-01-17 | Normal operation.Plant remained at maximum load from 0000 to 2400 hrs.
| 2017-01-18 | Normal operation.Plant remained at maximum load from 0000 to 2400 hrs.
| 2017-01-19 | Normal operation. NPCC load demand of 133 MW received from 2223 hrs to 2400 hrs.
| 2017-01-20 | Normal operation. NPCC load demand of 133 MW received from 0000 ~ 0315 hrs and 135 MW from 0334~0501 hrs.
| 2017-01-21 | Normal operation. NPCC load demand of 134 MW remained from 0003 to 0145 hrs.
| 2017-01-22 | Normal operation.Plant remained at maximum load from 0000 to 2400 hrs.
| 2017-01-23 | Normal operation.Plant remained at maximum load from 0000 to 2400 hrs.
| 2017-01-24 | CT-2 de-synch @ 0210 hrs & again synch @ 0354 hrs for "Intake Filters Replacement".
| 2017-01-25 | Normal operation.Plant remained at maximum load from 0000 to 2400 hrs.
| 2017-01-26 | CT-1 de-synch @ 0447 hrs & again synch @ 0647 hrs for "Intake Filters Replacement".
| 2017-01-27 | Normal operation.Plant remained at maximum load from 0000 to 2400 hrs.
| 2017-01-28 | Normal operation.Plant remained at maximum load from 0000 to 2400 hrs.
| 2017-01-29 | Normal operation.Plant remained at maximum load from 0000 to 2400 hrs.
| 2017-01-30 | Plant load remained restricted 132~137MW from 0000~1100hrs to remain within contractual heatrate.
| 2017-01-31 | Plant load remained restricted 130~149MW from 0000~2400hrs to remain within contractual heatrate.

## Feb
2018-02-01
| Date | Site Avg. Ambient Temp.F | Site Avg. Relative Humidty % | Site Avg. Ambient Wetbulb Temp.F | Site Ambient Temp |  | Base load hours |  |  |  | Standby hours |  |  |  | Plant ambient corrected Max Load |  | Corrected Plant Capacity | Ambient Corrected Daclared Avail'y (MWH) | Plant WAPDA Dispatch (MWH) | Net Plant Export (MWH) | Gross Generation | CT1 Average Cap (MW) | CT1 Unavail minutes | CT2 Average Cap (MW) | CT2 Unavail minutes | ST Average Cap (MW) | ST Unavail minutes | Plant Aux Load including Colony Load MWH | Differenece (+/-) MW | Maximum Daily Generation | Daily Load Factor | Avg. Corrected Plant Capacity | Plant Capacity Factor | Plant Availability Factor | Equivalent Plant Availability | LBtu gas flow (mmscf/day) | 1 LBtu gas (Average Btu/scf) | LBTU MMBTU | 1 HBtu gas flow (mmscf/day) | 1 HBtu gas (Average Btu/scf) | HBTU MMBTU | HHV Net Heat Rate (Btu/Kwh) | Avg. declared availability | CT1 Derated MW | CT1 derated mintutes | CT-2 derated MW | CT-2 derated mintutes | ST derated MW | ST derated mintutes | WAPDA Backfeed (MWH) | CT-1 Gross Generation (MWH) | CT-2 Gross Generation (MWH) | STG Gross Generation (MWH) | CT-1 & CT-2 MWH difference | Base load Heat Rate | STG load | DB1 | DB2 | CT1 | CT1 Gas flow | CT2 Gas flow |  | Pamb | Freq. Hz | LBTU Gas Specific gravity | CT-1 compressor efficiency(%) | CT-2 compressor efficiency(%) |  | CT-1 Heat Rate (Btu/Kwh) | CT-2 Heat Rate (Btu/Kwh) |  | DB(1+2) | DB-1 Ops Hours | DB-2 Ops Hours |  | CT-1 Wetcomprssion Ops Hours | RO Operation Hours | CT1 T/G Brg |  | CT2 T/G Brg
[7 empty] | CT1 |  | CT2 |  | CT1 |  | CT2 | [43 empty] | mmscf/d | mmscf/d | WetC flow | HBTU KPPH | HBTU KPPH | LBTU KPPH | mbar | Hz | [7 empty] | mmscf/d | [5 empty] | Supply air pressure | Seal air pressure | Supply air pressure | Seal air pressure
[5 empty] | Max | Min | hrs | min | hrs | min | hrs | min | hrs | min | hrs | min | [42 empty] | gpm | [18 empty] | Psi | "WC | Psi | "WC
Week 5 | 2018-01-29 | 55.73 | 75.73% | 49.59 | 67 | 45 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3720 | 3683 | 3683 | 3590 | 3701 | 45 | 0 | 47 | 0 | 62 | 0 | 111 | -93 | 157 | 98.22% | 155 | 96.51% | 100% | 100% | 10.764 | 138.9 | 1495.1196 | 30.675 | 977 | 29969.475 | 8764.511 | 153.4583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1070 | 1133 | 1498 | 63 | 8764.511 | 62.4167 | 2.295 | 2.295 | 27 | 27.58 | 22.81 | 30.9 | 997.6 | 50.11 | 0.9353 | 89.16 | 83.95 | -5.21 | 12130 | 11720 | -410 | 4.59 | 24 | 24 |  | 13.98 | 7.28 | 2.2 | 3.3 | 1.8 | 1.9
| 2018-01-30 | 61.6 | 61.3% | 51.6 | 73 | 52 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 3711 | 3496 | 3496 | 3411 | 3514 | 45 | 0 | 46 | 0 | 62 | 0 | 103 | -85 | 155 | 94.46% | 154.625 | 91.92% | 100% | 95.51% | 10.68 | 133.92 | 1430.2656 | 28.789 | 980 | 28213.22 | 8690.5557 | 145.6667 | 0 | 0 | 0 | 0 | 15 | 660 | 0 | 1085 | 1110 | 1319 | 25 | 8690.5557 | 54.9583 | 1.389 | 1.356 | 27 | 27.89 | 22.43 | 30.55 | 998.6 | 50.09 | 0.9377 | 92.22 | 83.85 | -8.37 | 12089 | 11784 | -305 | 2.745 | 24 | 24 |  | 20.7 | 7.3 | 2.2 | 4 | 1.8 | 2.3
| 2018-01-31 | 63 | 58% | 51 | 75 | 52 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3704 | 3236 | 3236 | 3164 | 3259 | 44 | 0 | 47 | 0 | 62 | 0 | 95 | -72 | 153 | 88.75% | 154.3333 | 85.42% | 100% | 88.89% | 10.05 | 134.24 | 1349.112 | 26.34 | 980 | 25813.2 | 8584.8015 | 134.8333 | 0 | 0 | 0 | 0 | 17 | 1440 | 0 | 1059 | 1116 | 1084 | 57 | 8584.8015 | 45.1667 | 0.095 | 0.095 | 27.5 | 27.38 | 22.45 | 30.37 | 996.4 | 50.07 | 0.9375 | 90.33 | 84.05 | -6.28 | 12144 | 11723 | -421 | 0.19 | 1 | 1 |  | 15.6 | 2.5 | 2.1 | 3.5 | 1.8 | 2.2
| 2018-02-01 | 64 | 51.5% | 50 | 75 | 54 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 3705 | 3448 | 3448 | 3379 | 3482 | 44 | 0 | 46 | 0 | 62 | 0 | 103 | -69 | 155 | 93.6% | 154.375 | 91.2% | 100% | 94.57% | 10.725 | 135.45 | 1452.7012 | 28.4615 | 978.7218 | 27855.94 | 8673.7618 | 143.6667 | 0 | 0 | 0 | 0 | 18 | 660 | 0 | 1067 | 1115 | 1300 | 48 | 8673.7618 | 54.1667 | 1.269 | 1.269 | 27 | 27.6 | 22.55 | 30.55 | 996.9 | 50.07 | 0.937 | 90.53 | 84.1 | -6.43 | 12169 | 11773 | -396 | 2.538 | 13 | 13 |  | 16.5 | 4.6 | 2.1 | 3.6 | 1.8 | 2.3
| 2018-02-02 | 62.45 | 47.2% | 47.96 | 81 | 48 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3705 | 3663 | 3663 | 3590 | 3700 | 44 | 0 | 47 | 0 | 63 | 0 | 110 | -73 | 157 | 98.2% | 154.375 | 96.9% | 100% | 100% | 10.77 | 136.54 | 1470.5358 | 30.6287 | 978.0157 | 29955.34 | 8753.7258 | 152.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1056 | 1135 | 1509 | 79 | 8753.7258 | 62.875 | 2.364 | 2.358 | 27 | 22.9 | 22.9 | 30.4 | 995 | 50.06 | 0.9366 | 88.68 | 84.16 | -4.52 | 12936 | 12602 | -334 | 4.722 | 24 | 24 |  | 12.4 | 6.72 | 2.1 | 3.1 | 1.8 | 2.5
| 2018-02-03 | 61.12 | 53.7% | 48.16 | 74 | 49 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3706 | 3651 | 3651 | 3576 | 3684 | 44 | 0 | 47 | 0 | 63 | 0 | 108 | -75 | 156 | 98.4% | 154.4167 | 96.49% | 100% | 100% | 10.786 | 137.52 | 1483.2907 | 30.5628 | 977.3538 | 29870.63 | 8767.8749 | 152.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1053 | 1129 | 1502 | 76 | 8767.8749 | 62.5833 | 2.335 | 2.335 | 27 | 27.34 | 22.79 | 30.84 | 997 | 50.08 | 0.9363 | 88.32 | 84 | -4.32 | 12207 | 11747 | -460 | 4.67 | 24 | 24 |  | 11.71 | 7.3 | 2.1 | 3.2 | 1.9 | 2.2
| 2018-02-04 | 60 | 53% | 48 | 74 | 49 | 12 | 17 | 11 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 3708 | 1803 | 1803 | 1789 | 1862 | 44 | 686 | 47 | 665 | 63 | 0 | 73 | -14 | 95 | 81.67% | 154.5 | 48.25% | 72.29% | 50.47% | 5.5 | 142.38 | 783.09 | 15.9232 | 977.5239 | 15565.28 | 9138.2728 | 75.125 | 20 | 17 | 23 | 86 | 32 | 1440 | 0 | 523 | 599 | 740 | 76 | 9138.2728 | 30.8333 | 1.267 | 1.135 | 0 | 13.9 | 12.25 | 15.67 | 998 | 50.06 | 0.9348 | 83.6 | 86.02 | 2.42 | 13846 | 12510 | -1336 | 2.402 | 11.87 | 12.35 |  | 0 | 0.4 | 2.2 | 2.9 | 2 | 2.3
Week 6 | 2018-02-05 | 59.6 | 56% | 47.6 | 74 | 47 | 21 | 45 | 24 | 0 | 0 | 0 | 0 | 0 | 21 | 42 | 3706 | 3516 | 3516 | 3460 | 3563 | 45 | 95 | 49 | 0 | 62 | 0 | 103 | -56 | 157 | 94.56% | 154.4167 | 93.36% | 98.1% | 95.82% | 10.81 | 137.3 | 1484.213 | 29.3502 | 974.7041 | 28607.74 | 8697.0962 | 146.5 | 21 | 40 | 0 | 0 | 31 | 138 | 0 | 1014 | 1182 | 1367 | 168 | 8697.0962 | 56.9583 | 1.773 | 1.979 | 28 | 25.83 | 23.61 | 30.48 | 998.96 | 50.08 | 0.9364 | 90.4 | 85.73 | -4.67 | 11917 | 11511 | -406 | 3.752 | 22 | 24 |  | 11.25 | 4.63 | 2.2 | 3.6 | 1.8 | 2.5
| 2018-02-06 | 60.1 | 53.6% | 47.5 | 73 | 49 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3709 | 3663 | 3663 | 3608 | 3713 | 45 | 0 | 49 | 0 | 60 | 0 | 105 | -55 | 157 | 98.54% | 154.5417 | 97.28% | 100% | 100% | 10.79 | 134.96 | 1456.2184 | 30.5303 | 974.2613 | 29744.46 | 8647.6381 | 152.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1093 | 1171 | 1449 | 78 | 8647.6381 | 60.375 | 1.987 | 1.987 | 28 | 27.9 | 23.46 | 30.26 | 1000.21 | 50.07 | 0.9372 | 89.82 | 85.53 | -4.29 | 11994 | 11553 | -441 | 3.974 | 24 | 24 |  | 11.33 | 5.6 | 2.1 | 3.6 | 1.7 | 2.3
| 2018-02-07 | 60.6 | 58.7% | 49.2 | 73 | 48 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 20 | 36 | 3709 | 3674 | 3603 | 3548 | 3650 | 45 | 0 | 48 | 0 | 58 | 0 | 102 | -55 | 157 | 96.87% | 154.5417 | 95.66% | 100% | 98.97% | 10.755 | 135.48 | 1457.0874 | 29.8567 | 975.1868 | 29115.86 | 8616.9525 | 153.0833 | 0 | 0 | 0 | 0 | 11 | 204 | 0 | 1092 | 1164 | 1394 | 72 | 8616.9525 | 58.0833 | 1.771 | 1.764 | 28 | 27.79 | 23.24 | 30.51 | 996.25 | 50.07 | 0.9367 | 90.83 | 85.41 | -5.42 | 11965 | 11548 | -417 | 3.535 | 24 | 24 |  | 13.2 | 7.02 | 2.1 | 3.7 | 1.8 | 1.5
| 2018-02-08 | 60.32 | 58.41% | 48.99 | 72 | 48 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3711 | 3696 | 3696 | 3640 | 3747 | 45 | 0 | 48 | 0 | 63 | 0 | 107 | -56 | 157 | 99.44% | 154.625 | 98.09% | 100% | 100% | 10.72 | 136.84 | 1466.9248 | 31.064 | 975.3322 | 30297.71 | 8726.548 | 154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1088 | 1156 | 1503 | 68 | 8726.548 | 62.625 | 2.324 | 2.324 | 27.5 | 27.79 | 23.31 | 29.97 | 994.9 | 50.11 | 0.9365 | 90.55 | 85.25 | -5.3 | 12012 | 11619 | -393 | 4.648 | 24 | 24 |  | 12.77 | 6.82 | 2.1 | 3.8 | 1.8 | 1
| 2018-02-09 | 60.37 | 60.34% | 49.64 | 72 | 48 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3710 | 3698 | 3698 | 3611 | 3714 | 45 | 0 | 48 | 0 | 61 | 0 | 103 | -87 | 158 | 97.94% | 154.5833 | 97.33% | 100% | 99.37% | 10.745 | 138.22 | 1485.1739 | 30.8264 | 972.0422 | 29964.609 | 8709.4386 | 154.0833 | 0 | 0 | 0 | 0 | 16 | 87 | 0 | 1090 | 1153 | 1471 | 63 | 8709.4386 | 61.2917 | 2.232 | 2.232 | 27.5 | 27.92 | 23.32 | 30.35 | 994.92 | 50.12 | 0.9363 | 91.13 | 85.14 | -5.99 | 12045 | 11673 | -372 | 4.464 | 24 | 24 |  | 14 | 3.67 | 2.1 | 3.5 | 1.8 | 1.5
| 2018-02-10 | 60.7 | 58% | 49.49 | 72 | 50 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3712 | 3699 | 3699 | 3630 | 3736 | 45 | 0 | 48 | 0 | 63 | 0 | 106 | -69 | 157 | 99.15% | 154.6667 | 97.79% | 100% | 100% | 10.72 | 137.22 | 1470.9984 | 31.1067 | 973.2315 | 30274.01 | 8745.1814 | 154.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1088 | 1043 | 1505 | -45 | 8745.1814 | 62.7083 | 2.381 | 2.381 | 27.5 | 27.89 | 23.25 | 29.9 | 997 | 50.08 | 0.9365 | 90.91 | 84.97 | -5.94 | 12059 | 11729 | -330 | 4.762 | 24 | 24 |  | 13.47 | 4.33 | 2.1 | 3.34 | 1.8 | 2.4
| 2018-02-11 | 56 | 70% | 50 | 59 | 52 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3720 | 3715 | 3715 | 3650 | 3754 | 45 | 0 | 48 | 0 | 63 | 0 | 104 | -65 | 159 | 98.38% | 155 | 98.12% | 100% | 100% | 10.6 | 134.87 | 1429.622 | 31.3682 | 971.3266 | 30468.779 | 8739.2879 | 154.7917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1092 | 1152 | 1510 | 60 | 8739.2879 | 62.9167 | 2.347 | 2.347 | 27.5 | 28.16 | 23.54 | 30.34 | 997.6 | 50.16 | 0.9368 | 90.88 | 84.99 | -5.89 | 12117 | 11771 | -346 | 4.694 | 24 | 24 | 0 | 13.2 | 3.7 | 2 | 3.5 | 1.8 | 2.4
Week 7 | 2018-02-12 | 58.8 | 73.4% | 52.5 | 68 | 52 | 20 | 19 | 20 | 19 | 0 | 0 | 0 | 0 | 16 | 49 | 3720 | 3714 | 3415 | 3368 | 3466 | 45 | 0 | 47 | 0 | 62 | 0 | 98 | -47 | 157 | 91.99% | 155 | 90.54% | 100% | 93.22% | 10.3 | 133.34 | 1373.402 | 29.2745 | 957.7595 | 28037.949 | 8732.5864 | 154.75 | 14 | 221 | 15 | 221 | 20 | 431 | 0 | 1063 | 1086 | 1317 | 23 | 8732.5864 | 54.875 | 1.691 | 1.676 | 27.5 | 27.71 | 22.47 | 29.76 | 996.5 | 50.15 | 0.9374 | 95.91 | 85.1 | -10.81 | 12346 | 12066 | -280 | 3.367 | 24 | 24 |  | 17.3 | 10.2 | 2.2 | 3.5 | 1.8 | 2.3
| 2018-02-13 | 58 | 76% | 52 | 68 | 50 | 19 | 53 | 19 | 53 | 0 | 0 | 0 | 0 | 19 | 53 | 3720 | 3706 | 3452 | 3401 | 3501 | 46 | 0 | 47 | 0 | 62 | 0 | 100 | -51 | 158 | 92.33% | 155 | 91.42% | 100% | 93.25% | 10.25 | 138.24 | 1416.96 | 29.6546 | 964.0258 | 28587.83 | 8822.3434 | 154.4167 | 14 | 247 | 15 | 247 | 32 | 247 | 0 | 1061 | 1076 | 1364 | 15 | 8822.3434 | 56.8333 | 1.964 | 1.956 | 27.5 | 27.75 | 22.42 | 29.66 | 1004.1 | 50.09 | 0.9356 | 92.5 | 85.1 | -7.4 | 12363 | 12152 | -211 | 3.92 | 24 | 24 |  | 16.9 | 3.8 | 2.2 | 3.4 | 1.8 | 2.2
| 2018-02-14 | 59.7 | 68% | 51.2 | 68 | 51 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3720 | 3703 | 3703 | 3649 | 3756 | 47 | 0 | 48 | 0 | 62 | 0 | 107 | -54 | 159 | 98.43% | 155 | 98.09% | 100% | 100% | 10.3 | 138.31 | 1424.593 | 31.3631 | 967.5784 | 30346.289 | 8706.7366 | 154.2917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1131 | 1145 | 1480 | 14 | 8706.7366 | 61.6667 | 2.227 | 2.227 | 27.5 | 28.93 | 23.42 | 30.02 | 1004.7 | 50.13 | 0.9358 | 94.98 | 85 | -9.98 | 12444 | 12100 | -344 | 4.454 | 24 | 24 |  | 22.42 | 7 | 2.2 | 3.8 | 1.7 | 2
| 2018-02-15 | 62.6 | 79.98% | 59.07 | 72 | 53 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3709 | 3697 | 3697 | 3632 | 3739 | 47 | 0 | 47 | 0 | 62 | 0 | 107 | -65 | 160 | 97.37% | 154.5417 | 97.92% | 100% | 100% | 10.308 | 136.06 | 1402.5065 | 31.2414 | 968.488 | 30256.914 | 8716.8008 | 154.0417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1127 | 1135 | 1477 | 8 | 8716.8008 | 61.5417 | 2.225 | 2.225 | 27.5 | 28.9 | 23.28 | 29.6 | 1001.7 | 50.1 | 0.937 | 95.86 | 84.92 | -10.94 | 12396 | 12255 | -141 | 4.45 | 24 | 24 |  | 24 | 7.03 | 2.1 | 3.7 | 1.7 | 1.4
| 2018-02-16 | 62.52 | 69.02% | 56.74 | 75 | 56 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 22 | 50 | 3699 | 3673 | 3642 | 3581 | 3684 | 46 | 0 | 46 | 0 | 62 | 0 | 103 | -61 | 158 | 97.15% | 154.125 | 96.81% | 100% | 99.53% | 10.28 | 135.38 | 1391.7064 | 30.916 | 967.7503 | 29918.9678 | 8743.556 | 153.0417 | 0 | 0 | 0 | 0 | 15 | 70 | 0 | 1107 | 1108 | 1469 | 1 | 8743.556 | 61.2083 | 2.192 | 2.179 | 27.5 | 28.47 | 22.91 | 29.71 | 999 | 50.09 | 0.937 | 95.44 | 84.82 | -10.62 | 12089 | 11941 | -148 | 4.371 | 24 | 24 |  | 22.85 | 8.28 | 2.2 | 3.5 | 1.8 | 1.3
| 2018-02-17 | 66.9 | 69.6% | 58.2 | 79 | 56 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 3689 | 3659 | 3513 | 3462 | 3563 | 45 | 0 | 46 | 0 | 60 | 0 | 101 | -51 | 156 | 95.17% | 153.7083 | 93.85% | 100% | 97.52% | 10.18 | 134.17 | 1365.8506 | 29.751 | 968.8403 | 28823.9688 | 8720.3407 | 152.4583 | 0 | 0 | 0 | 0 | 15 | 360 | 0 | 1077 | 1094 | 1392 | 17 | 8720.3407 | 58 | 1.893 | 1.861 | 27.5 | 27.87 | 22.59 | 29.64 | 994.96 | 50.05 | 0.9377 | 93.57 | 84.71 | -8.86 | 12171 | 11966 | -205 | 3.754 | 23.67 | 23.67 |  | 18.62 | 7 | 2.1 | 3.5 | 1.7 | 1
| 2018-02-18 | 65.6 | 70.3% | 56.6 | 80 | 51 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3689 | 3334 | 3214 | 3178 | 3265 | 46 | 0 | 46 | 0 | 60 | 0 | 87 | -36 | 140 | 97.17% | 153.7083 | 86.15% | 100% | 90.13% | 10.165 | 137 | 1392.605 | 26.347 | 965.9164 | 25449 | 8446.0683 | 138.9167 | 0 | 0 | 0 | 0 | 15 | 1440 | 0 | 1108 | 1100 | 1057 | -8 | 8446.0683 | 44.0417 | 0.042 | 0.053 | 27.5 | 28.5 | 22.71 | 29.71 | 992.88 | 50.07 | 0.9368 | 95.9 | 84.57 | -11.33 | 12098 | 11948 | -150 | 0.095 | 1 | 1.1 |  | 24 | 6.83 | 2.2 | 3.6 | 1.9 | 1.2
Week 8 | 2018-02-19 | 68.8 | 58.4% | 55.9 | 80 | 56 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 18 | 54 | 3677 | 3654 | 3555 | 3505 | 3608 | 46 | 0 | 46 | 0 | 60 | 0 | 103 | -50 | 155 | 96.99% | 153.2083 | 95.32% | 100% | 97.9% | 10.144 | 137.54 | 1395.2058 | 30.179 | 965.1733 | 29127.9652 | 8708.4653 | 152.25 | 0 | 0 | 0 | 0 | 15 | 306 | 0 | 1105 | 1095 | 1408 | -10 | 8708.4653 | 58.6667 | 1.996 | 1.975 | 27.5 | 28.53 | 22.68 | 29.66 | 994.54 | 50.09 | 0.9366 | 95.7 | 84.46 | -11.24 | 12130 | 12002 | -128 | 3.971 | 24 | 24 |  | 24 | 7 | 2.2 | 3.4 | 1.7 | 1.5
| 2018-02-20 | 68.81 | 61.41% | 57.05 | 80 | 58 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3679 | 3651 | 3651 | 3575 | 3678 | 46 | 0 | 45 | 0 | 62 | 0 | 103 | -76 | 157 | 97.61% | 153.2917 | 97.17% | 100% | 100% | 10.13 | 136.43 | 1382.0359 | 30.902 | 964.4982 | 29804.9229 | 8723.6248 | 152.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1099 | 1089 | 1490 | -10 | 8723.6248 | 62.0833 | 2.429 | 2.429 | 27.5 | 28.45 | 22.66 | 29.55 | 993.5 | 50.06 | 0.9369 | 95.85 | 84.49 | -11.36 | 12163 | 12055 | -108 | 4.858 | 24 | 24 |  | 24 | 7.62 | 2.2 | 3.8 | 1.85 | 1.6
| 2018-02-21 | 70.94 | 60.45% | 58.29 | 82 | 61 | 22 | 41 | 22 | 14 | 0 | 0 | 0 | 0 | 19 | 22 | 3670 | 3599 | 3599 | 3279 | 3379 | 46 | 68 | 45 | 83 | 62 | 94 | 101 | -320 | 156 | 90.25% | 152.9167 | 89.35% | 94.24% | 93.37% | 9.32 | 138.87 | 1294.2684 | 28.523 | 964.4751 | 27509.7232 | 8784.3829 | 149.9583 | 25 | 17 | 21 | 23 | 29 | 35 | 1 | 1031 | 1012 | 1336 | -19 | 8784.3829 | 55.6667 | 2.16 | 2.147 | 27.5 | 26.93 | 21.3 | 27.99 | 992.75 | 50.1 | 0.9364 | 95.79 | 84.36 | -11.43 | 12130 | 12055 | -75 | 4.307 | 22.1167 | 22.1167 |  | 21.77 | 9.18 | 2.2 | 3.5 | 1.8 | 1.6
| 2018-02-22 | 71.92 | 61.28% | 59.48 | 83 | 63 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3670 | 3604 | 3604 | 3519 | 3627 | 45 | 0 | 45 | 0 | 61 | 0 | 108 | -85 | 154 | 98.13% | 152.9167 | 95.89% | 100% | 100% | 10.1 | 137.12 | 1384.912 | 30.3021 | 963.3786 | 29192.3555 | 8689.1922 | 150.1667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1081 | 1073 | 1473 | -8 | 8689.1922 | 61.375 | 2.415 | 2.415 | 27.2 | 28.17 | 22.46 | 29.42 | 991.46 | 50.08 | 0.9364 | 95.94 | 84.58 | -11.36 | 12256 | 12128 | -128 | 4.83 | 24 | 24 |  | 24 | 6.58 | 2.1 | 3.6 | 1.65 | 1.6
| 2018-02-23 | 69 | 65% | 59 | 78 | 60 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3691 | 3620 | 3620 | 3550 | 3659 | 45 | 0 | 45 | 0 | 62 | 0 | 109 | -70 | 155 | 98.36% | 153.7917 | 96.18% | 100% | 100% | 10.04 | 135.85 | 1363.934 | 30.815 | 966.5642 | 29784.6758 | 8774.2563 | 150.8333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1084 | 1081 | 1494 | -3 | 8774.2563 | 62.25 | 2.474 | 2.474 | 27.2 | 28.16 | 22.5 | 29.38 | 991.7 | 50.07 | 0.937 | 95.9 | 84.6 | -11.3 | 12218 | 12057 | -161 | 4.948 | 24 | 24 |  | 24 | 7.3 | 2.1 | 3.5 | 1.8 | 1.3
| 2018-02-24 | 66 | 73% | 59 | 74 | 60 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3696 | 3641 | 3641 | 3573 | 3679 | 45 | 0 | 45 | 0 | 63 | 0 | 106 | -68 | 156 | 98.26% | 154 | 96.67% | 100% | 100% | 10.02 | 135.52 | 1357.9104 | 30.775 | 968.2017 | 29796.4077 | 8719.3725 | 151.7083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1087 | 1088 | 1504 | 1 | 8719.3725 | 62.6667 | 2.476 | 2.476 | 27.2 | 28.23 | 22.65 | 29.35 | 994.75 | 50.1 | 0.9369 | 95.78 | 84.76 | -11.02 | 12199 | 12015 | -184 | 4.952 | 24 | 24 |  | 23.9 | 7.9 | 2.1 | 3.6 | 1.8 | 1.5
| 2018-02-25 | 66 | 69% | 58 | 78 | 55 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 2 | 24 | 3697 | 3307 | 3275 | 3212 | 3306 | 45 | 0 | 45 | 0 | 62 | 0 | 94 | -63 | 153 | 90.03% | 154.0417 | 86.88% | 100% | 89.93% | 10.005 | 135.59 | 1356.578 | 26.815 | 969.5554 | 25998.6272 | 8516.5645 | 137.7917 | 0 | 0 | 0 | 0 | 17 | 1296 | 0 | 1095 | 1101 | 1110 | 6 | 8516.5645 | 46.25 | 0.248 | 0.239 | 27.2 | 28.37 | 22.76 | 29.34 | 999.5 | 50.11 | 0.937 | 95.71 | 84.7 | -11.01 | 12175 | 11944 | -231 | 0.487 | 3.8 | 3.7 |  | 24 | 7.1 | 2.1 | 3.5 | 1.8 | 1.5
Week 9 | 2018-02-26 | 70.5 | 66.4% | 60.3 | 81 | 60 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 18 | 56 | 3668 | 3637 | 3530 | 3477 | 3583 | 45 | 0 | 45 | 0 | 62 | 0 | 106 | -53 | 157 | 95.09% | 152.8333 | 94.79% | 100% | 97.92% | 10.003 | 134.38 | 1344.2031 | 30.155 | 966.2948 | 29138.62 | 8766.9897 | 151.5417 | 0 | 0 | 0 | 0 | 15 | 304 | 0 | 1081 | 1085 | 1417 | 4 | 8766.9897 | 59.0417 | 2.109 | 2.078 | 27.4 | 28.31 | 22.73 | 29.43 | 995.7 | 50.07 | 0.9376 | 96 | 84.7 | -11.3 | 12625 | 12522 | -103 | 4.187 | 24 | 24 |  | 24 | 7.92 | 2.2 | 3.6 | 1.8 | 1.5
| 2018-02-27 | 73.2 | 64% | 61.9 | 84 | 61 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 3 | 26 | 3651 | 3608 | 3540 | 3473 | 3579 | 45 | 0 | 45 | 0 | 62 | 0 | 106 | -67 | 154 | 96.83% | 152.125 | 95.12% | 100% | 98.49% | 10.001 | 137.99 | 1380.038 | 30.339 | 960.8781 | 29152.08 | 8791.2807 | 150.3333 | 0 | 0 | 0 | 0 | 16 | 206 | 0 | 1071 | 1068 | 1440 | -3 | 8791.2807 | 60 | 2.301 | 2.295 | 27.2 | 28.18 | 22.5 | 29.29 | 993.5 | 50.05 | 0.9375 | 95.88 | 84.72 | -11.16 | 12368 | 12192 | -176 | 4.596 | 24 | 24 |  | 24 | 10.85 | 2.1 | 3.4 | 1.8 | 1.5
| 2018-02-28 | 73.8 | 63.9% | 62.3 | 84 | 64 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3648 | 3603 | 3603 | 3518 | 3627 | 44 | 0 | 44 | 0 | 62 | 0 | 109 | -85 | 154 | 98.13% | 152 | 96.44% | 100% | 100% | 9.996 | 136.75 | 1366.953 | 30.939 | 962.0238 | 29764.0543 | 8849.064 | 150.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1067 | 1061 | 1499 | -6 | 8849.064 | 62.4583 | 2.6 | 2.6 | 27.2 | 28.12 | 22.49 | 28.53 | 993.5 | 50.05 | 0.9376 | 96 | 84.66 | -11.34 | 12383 | 12221 | -162 | 5.2 | 24 | 24 |  | 24 | 6.75 | 2.1 | 3.5 | 1.8 | 1.5
| 2018-03-01 | [26 empty] | 0 | 0 |  | no data | no data | no data | no data | no data |  |  | 0 |  |  | 0 | no data | [11 empty] | 0 | no data | 0 | [11 empty] | 0 |  |  | 0 | 0
| 2018-03-02 | [26 empty] | 0 | 0 |  | no data | no data | no data | no data | no data |  |  | 0 |  |  | 0 | no data | [11 empty] | 0 | no data | 0 | [11 empty] | 0 |  |  | 0 | 0
| 2018-03-03 | [26 empty] | 0 | 0 |  | no data | no data | no data | no data | no data |  |  | 0 |  |  | 0 | no data | [11 empty] | 0 | no data | 0 | [11 empty] | 0 |  |  | 0 | 0
| 2018-03-04 | [26 empty] | 0 | 0 |  | no data | no data | no data | no data | no data |  |  | 0 |  |  | 0 | no data | [11 empty] | 0 | no data | 0 | [11 empty] | 0 |  |  | 0 | 0
| Monthly | 64.2268 | 63.2% | 54.0739 | 75.4643 | 53.8929 | 648 | 55 | 649 | 55 | 0 | 0 | 0 | 0 | 45 | 52 | 103494 | 99636 | 98409 | 96624.53 | 99304 | 45.1786 | 849 | 46.5 | 748 | 61.75 | 94 | 2680.47 | -1976 | 153.7143 | 95.93% | 154.0089 | 93.36% | 98.74% | 96.09% | 284.463 | 136.6186 | 38833.5177 | 827.9704 | 969.2536 | 802410.7083 | 8706.3215 |  | 94 | 542 | 74 | 577 | 297 | 7224 | 1 | 29731 | 30496 | 38977 | 765 | 8706.3215 | 58.0015 | 55.492 | 55.416 | 26.45 | 27.3071 | 22.4554 | 29.2611 | 996.4814 | 50.0864 | 0.93673 | 93.1557 | 84.8411 |  | 12279.3214 | 11987.6786 |  | 110.908 | 601.4567 | 603.9367 |  | 513.59 | 183.13
| Totals | Avg.F | % Avg. |  | M Avg | m Avg | hrs | min | hrs | min | hrs | min | hrs | min | Avg Int Avi | Avg Ext Avi | MWhr Total | MWhr Total | MWhr Total | MWhr Total | MWhr Total | MW Avg | Total min | Avg MW | Total min | Avg MW | Total min | MWhr | Total MW | Av Max D/Gen | Av. DailyLF | Avg. | Avg. |  | Avg. | Total | Avg. |  | Total | Avg. |  | Avg. | [7 empty] | Total |  |  |  |  | Avg.
| Weeks data | Site Avg. Amb. Temp F | Site Avg. Relative humidity % |  | M Avg: Site Maximum/Minumum Temperature; hrs: CT-1 Base Load Hours; hrs: CT-2 Base Load Hours; hrs: CT-1 stand by hours / min; hrs: CT-2 standby hours / min | Plant ambient Corrected maximum Load hours/min |  | Average Corrected Plant Capacity | Ambient Corrected Declared Avail'y (MWH) | Av Plant WAPDA Dispatch | Net Plant Export (MWH) | Gross Generation | CT1 Av Cap (MW) | CT1 Unavail minutes | CT2 Av Cap (MW) | CT2 Unavail minutes | ST Unavail minutes | ST Average Cap (MW) | Plant Aux Load including Colony Load MWH | Differenece (+/-) MW | Maximum Daily Generation | Daily Load Factor | Avg. Corrected Plant | Plant Capacity Facto | Plant Availability Factor | Equivalent Plant Availability | LBtu gas flow mmscf | 1 LBtu gas (Average Btu/scf) | LBTU MMBTU | PL gas flow (mscf/week) | 1 PL gas (Average Btu/scf) | HBTU MMBTU | Plant Net Heat Rate (Btu/Kwh) | [11 empty] | -10
| Week 5 | 61.1286 | 57.2043 | 49.4729 | 74.1429 | 49.8571 | 156 | 17 | 155 | 29 | 0 | 0 | 0 | 0 | 98 | 0 | 3708.4286 | 3282.8571 | 3282.8571 | 22499 | 23202 | 44.2857 | 686 | 46.7143 | 665 | No outage | 62.4286 | no data | -481 | 146.8571 | 93.33% | 154.5179 | 86.67% | 96.04% | 89.92% | 69.275 | 136.9929 | 9490.1802 | 191.3802 | 978.3736 | 187241.3083 | 8767.6434
| Week 6 | 59.67 | 59.29% | 48.9171 | 70.7143 | 48.8571 | 165 | 43 | 168 | 0 | 0 | 0 | 0 | 0 | 162 | -18 | 3711 | 3665.8571 | 3655.7143 | 25147 | 25877 | 45 | 95 | 48.2857 | No outage | No outage | 61.4286 | 730 | -443 | 157.4286 | 97.84% | 154.625 | 96.8% | 99.73% | 99.17% | 75.14 | 136.4129 | 10250.0621 | 214.1025 | 973.7264 | 208477.2433 | 8697.449 | [5 empty] | 0.27381
| Week 7 | 62.0171 | 72.33% | 55.1871 | 72.8571 | 52.7143 | 160 | 72 | 160 | 12 | 0 | 0 | 0 | 0 | 125 | 32 | 3706.5714 | 3640.8571 | 3519.4286 | 24271 | 24974 | 46 | No outage | 46.7143 | No outage | No outage | 61.4286 | 703 | -365 | 155.4286 | 95.66% | 154.4405 | 93.54% | 100% | 96.24% | 71.783 | 136.0714 | 9767.6154 | 182.2007 | 965.7404 | 175958.5509 | 8698.3475 | [5 empty] | 0.26672
| Week 8 | 68.7814 | 0.64077 | 58.1029 | 79.2857 | 59 | 166 | 41 | 166 | 14 | 0 | 0 | 0 | 0 | 136 | 40 | 3682.8571 | 3582.2857 | 3563.5714 | 24213 | 24936 | 45.4286 | 68 | 45.1429 | 83 | 432 | 61.7143 | 724 | -732 | 155.1429 | 95.66% | 153.4524 | 93.92% | 99.18% | 97.31% | 69.759 | 136.7029 | 9536.2546 | 208.3111 | 965.9781 | 201223.9144 | 8702.2655
| Week 9 | 72.5 | 0.64767 | 61.5 | 83 | 61.6667 | 72 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 46 | 22 | 3655.6667 | 3616 | 3557.6667 | 10468 | 10789 | 44.6667 | No outage | 44.6667 | No outage | 186 | 62 | 321 | -205 | 155 | 96.69% | 152.3194 | 95.45% | 100% | 98.8% | 30 | 136.3733 | 4091.2 | 91.433 | 963.0656 | 88055.9735 | 8802.4448
| Date | Plant Status Whether Normal Operation or Tripping (State full detail for trippings/return to normal).
| 2018-02-01 | Plant load remained restricted 127~134 MW from 0000~1100 hrs to remain within contractual heatrate.
| 2018-02-02 | Normal operation.Plant remained at maximum load from 0000 to 2400 hrs.
| 2018-02-03 | Normal operation.Plant remained at maximum load from 0000 to 2400 hrs.
| 2018-02-04 | Gas turbine CT-2 de-synch @ 0029 hrs and again synch@ 1134 hrs after compressor offline washing. Gas turbine CT-1 de-synch @ 1234 hrs for compressor offline washing.
| 2018-02-05 | CT-1 synch @ 0135 hrs after "compressor offline washing".
| 2018-02-06 | Normal operation.Plant remained at maximum load from 0000 to 2400 hrs.
| 2018-02-07 | Complex load remained 136 MW from 0019 hrs to 0343 hrs at NPCC demand.
| 2018-02-08 | Normal operation.Plant remained at maximum load from 0000 to 2400 hrs.
| 2018-02-09 | Plant load remained 133 MW from 0216 hrs to 0343 hrs at NPCC demand.
| 2018-02-10 | Normal operation.Plant remained at maximum load from 0000 to 2400 hrs.
| 2018-02-11 | Normal operation. Plant remained at maximum load from 0000 to 2400 hrs.
| 2018-02-12 | NPCC load demand of 134 MW received at 0042hrs, 90 MW load demand at 0310hrs, 152 MW ( ambient corrected) load demand at 0642 hrs, 132 MW load demand at 0754hrs and 152 MW (ambient corrected) load demand at 0848 hrs.
| 2018-02-13 | NPCC load demand of 90 MW received at 0113hrs and 154 MW (ambient corrected) load demand received at 0508 hrs.
| 2018-02-14 | Normal operation.Plant remained at maximum load from 0000 to 2400 hrs.
| 2018-02-15 | Normal operation.Plant remained at maximum load from 0000 to 2400 hrs.
| 2018-02-16 | NPCC load demand of 130 MW received at 2250 hrs.
| 2018-02-17 | NPCC load demand of 154 MW received at 0522 hrs & load demand of 131 MW received at 2334 hrs.
| 2018-02-18 | NPCC load demand of 154 MW received at 0523 hrs. Duct burners remained OFF from 0000 to 2300 hrs to remain within contractual heat rate.
| 2018-02-19 | Plant load remained 136 MW from 0036 hrs to 0542 hrs at NPCC demand.
| 2018-02-20 | Normal operation.Plant remained at maximum load from 0000 to 2400 hrs.
| 2018-02-21 | Plant tripped @ 1216 hrs due to WAPDA supply failure. After restoration of Wapda supply at 1226hrs, CT-1 synch @ 1318 hrs, CT-2 synch @ 1339 hrs and STG synch @ 1350 hrs.
| 2018-02-22 | Normal operation.Plant remained at maximum load from 0000 to 2400 hrs.
| 2018-02-23 | Normal operation.Plant remained at maximum load from 0000 to 2400 hrs.
| 2018-02-24 | Normal operation.Plant remained at maximum load from 0000 to 2400 hrs.
| 2018-02-25 | Plant load remained restricted 129~135 MW from 0000~2023 hrs to remain within contractual heatrate. NPCC load demand of 134 MW received at 2247 hrs.
| 2018-02-26 | NPCC load demand of 155 MW received at 0504 hrs.
| 2018-02-27 | Plant load remained 132 MW from 0108 hrs to 0434 hrs at NPCC demand.
| 2018-02-28 | Normal operation.Plant remained at maximum load from 0000 to 2400 hrs.

## March
2018-03-01
| Date | Site Avg. Ambient Temp.F | Site Avg. Relative Humidty % | Site Avg. Ambient Wetbulb Temp.F | Site Ambient Temp |  | Base load hours |  |  |  | Standby hours |  |  |  | Plant ambient corrected Max Load |  | Corrected Plant Capacity | Ambient Corrected Daclared Avail'y (MWH) | Plant WAPDA Dispatch (MWH) | Net Plant Export (MWH) | Gross Generation | CT1 Average Cap (MW) | CT1 Unavail minutes | CT2 Average Cap (MW) | CT2 Unavail minutes | ST Average Cap (MW) | ST Unavail minutes | Plant Aux Load including Colony Load MWH | Differenece (+/-) MW | Maximum Daily Generation | Daily Load Factor | Avg. Corrected Plant Capacity | Plant Capacity Factor | Plant Availability Factor | Equivalent Plant Availability | LBtu gas flow (mmscf/day) | 1 LBtu gas (Average Btu/scf) | LBTU MMBTU | 1 HBtu gas flow (mmscf/day) | 1 HBtu gas (Average Btu/scf) | HBTU MMBTU | HHV Net Heat Rate (Btu/Kwh) | Avg. declared availability | CT1 Derated MW | CT1 derated mintutes | CT-2 derated MW | CT-2 derated mintutes | ST derated MW | ST derated mintutes | WAPDA Backfeed (MWH) | CT-1 Gross Generation (MWH) | CT-2 Gross Generation (MWH) | STG Gross Generation (MWH) | CT-1 & CT-2 MWH difference | Base load Heat Rate | STG load | DB1 | DB2 | CT1 | CT1 Gas flow | CT2 Gas flow |  | Pamb | Freq. Hz | LBTU Gas Specific gravity | CT-1 compressor efficiency(%) | CT-2 compressor efficiency(%) |  | CT-1 Heat Rate (Btu/Kwh) | CT-2 Heat Rate (Btu/Kwh) |  | DB(1+2) | DB-1 Ops Hours | DB-2 Ops Hours | CT-1 Wetcomprssion Ops Hours | RO Operation Hours | CT1 T/G Brg |  | CT2 T/G Brg
[7 empty] | CT1 |  | CT2 |  | CT1 |  | CT2 | [43 empty] | mmscf/d | mmscf/d | WetC flow | HBTU KPPH | HBTU KPPH | LBTU KPPH | mbar | Hz | [7 empty] | mmscf/d |  |  |  |  | Supply air pressure | Seal air pressure | Supply air pressure | Seal air pressure
[5 empty] | Max | Min | hrs | min | hrs | min | hrs | min | hrs | min | hrs | min | [42 empty] | gpm | [17 empty] | Psi | "WC | Psi | "WC
Week 9 | 2018-02-26 | 70.5 | 66.4% | 60.3 | 81 | 60 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 18 | 56 | 3668 | 3637 | 3530 | 3477 | 3583 | 45 | 0 | 45 | 0 | 62 | 0 | 106 | -53 | 157 | 95.09% | 152.8333 | 94.79% | 100% | 97.92% | 10.41 | 134.38 | 1398.8958 | 29.98 | 965 | 28930.7 | 8722.9209 | 151.5417 | 0 | 0 | 0 | 0 | 15 | 304 | 0 | 1081 | 1085 | 1417 | 4 | 8722.9209 | 59.0417 | 2.109 | 2.078 | 27.4 | 28.31 | 22.73 | 29.43 | 995.7 | 50.07 | 0.9376 | 96 | 84.7 | -11.3 | 12625 | 12522 | -103 | 4.187 | 24 | 24 | 24 | 7.92 | 2.2 | 3.6 | 1.8 | 1.5
| 2018-02-27 | 73.2 | 64% | 61.9 | 84 | 61 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 3 | 26 | 3651 | 3608 | 3540 | 3473 | 3579 | 45 | 0 | 45 | 0 | 62 | 0 | 106 | -67 | 154 | 96.83% | 152.125 | 95.12% | 100% | 98.49% | 10.41 | 137.99 | 1436.4759 | 30.19 | 960 | 28982.4 | 8758.6743 | 150.3333 | 0 | 0 | 0 | 0 | 16 | 206 | 0 | 1071 | 1068 | 1440 | -3 | 8758.6743 | 60 | 2.301 | 2.295 | 27.2 | 28.18 | 22.5 | 29.29 | 993.5 | 50.05 | 0.9375 | 95.88 | 84.72 | -11.16 | 12368 | 12192 | -176 | 4.596 | 24 | 24 | 24 | 10.85 | 2.1 | 3.4 | 1.8 | 1.5
| 2018-02-28 | 73.8 | 63.9% | 62.3 | 84 | 64 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3648 | 3603 | 3603 | 3518 | 3627 | 44 | 0 | 44 | 0 | 62 | 0 | 109 | -85 | 154 | 98.13% | 152 | 96.44% | 100% | 100% | 10.15 | 136.75 | 1388.0125 | 30.8 | 961 | 29598.8 | 8808.0763 | 150.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1067 | 1061 | 1499 | -6 | 8808.0763 | 62.4583 | 2.6 | 2.6 | 27.2 | 28.12 | 22.49 | 28.53 | 993.5 | 50.05 | 0.9376 | 96 | 84.66 | -11.34 | 12383 | 12221 | -162 | 5.2 | 24 | 24 | 24 | 6.75 | 2.1 | 3.5 | 1.8 | 1.5
| 2018-03-01 | 72.7 | 66.2% | 62.7 | 83 | 65 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3665 | 3586 | 3586 | 3503 | 3613 | 44 | 0 | 44 | 0 | 62 | 0 | 110 | -83 | 153 | 98.39% | 152.7083 | 95.58% | 100% | 100% | 10.03 | 135.26 | 1356.6578 | 30.7854 | 961.8254 | 29610.21 | 8840.0993 | 149.4167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1060 | 1063 | 1490 | 3 | 8840.0993 | 62.0833 | 2.549 | 2.549 | 27.2 | 28.02 | 22.47 | 29.01 | 992.7 | 50.07 | 0.9373 | 95.39 | 84.76 | -10.63 | 12406 | 12222 | -184 | 5.098 | 24 | 24 | 24 | 7.55 | 2.2 | 3.5 | 1.8 | 1.5
| 2018-03-02 | 71.4 | 71% | 63.1 | 85 | 62 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3664 | 3598 | 3598 | 3520 | 3629 | 45 | 0 | 44 | 0 | 62 | 0 | 109 | -78 | 155 | 97.55% | 152.6667 | 96.07% | 100% | 100% | 9.985 | 136.85 | 1366.4472 | 30.8156 | 963.4393 | 29688.99 | 8822.5674 | 149.9167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1072 | 1064 | 1493 | -8 | 8822.5674 | 62.2083 | 2.562 | 2.562 | 27.2 | 28.07 | 22.36 | 29.01 | 990.21 | 50.07 | 0.9368 | 96.09 | 84.82 | -11.27 | 12324 | 12163 | -161 | 5.124 | 24 | 24 | 24 | 9.94 | 2.1 | 3.5 | 1.7 | 1.5
| 2018-03-03 | 70.4 | 74.2% | 63.64 | 81 | 62 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3690 | 3603 | 3603 | 3518 | 3621 | 45 | 0 | 44 | 0 | 62 | 0 | 103 | -85 | 154 | 97.97% | 153.75 | 95.34% | 100% | 100% | 9.885 | 137.23 | 1356.5185 | 31.0289 | 962.2603 | 29857.87 | 8872.7654 | 150.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1068 | 1055 | 1498 | -13 | 8872.7654 | 62.4167 | 2.627 | 2.611 | 27.2 | 28.14 | 22.41 | 29.01 | 989.4 | 50.07 | 0.9365 | 96.15 | 84.76 | -11.39 | 12381 | 12285 | -96 | 5.238 | 24 | 24 | 24 | 7 | 2.1 | 3.4 | 1.6 | 1.4
| 2018-03-04 | 68.16 | 67.41% | 58.79 | 82 | 58 | 24 | 0 | 12 | 10 | 0 | 0 | 0 | 0 | 12 | 2 | 3683 | 2744 | 2744 | 2695 | 2789 | 45 | 0 | 46 | 643 | 62 | 0 | 94 | -49 | 154 | 75.46% | 153.4583 | 73.17% | 86.57% | 76.1% | 5.185 | 153.48 | 795.7938 | 24.188 | 962.104 | 23271.38 | 8930.3057 | 114.3333 | 0 | 0 | 23 | 67 | 30 | 718 | 0 | 1088 | 597 | 1104 | -491 | 8930.3057 | 46 | 2.442 | 1.215 | 27.2 | 28.49 | 12.64 | 16.19 | 991.46 | 50.08 | 0.9307 | 95.82 | 86.75 | -9.07 | 12305 | 11871 | -434 | 3.657 | 24 | 12.42 | 24 | 8.22 | 2.2 | 3.6 | 1.8 | 1.9
Week 10 | 2018-03-05 | 71.24 | 67.14% | 61.13 | 84 | 62 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3667 | 3609 | 3609 | 3532 | 3638 | 45 | 0 | 47 | 0 | 60 | 0 | 106 | -77 | 156 | 97.17% | 152.7917 | 96.32% | 100% | 100% | 9.92 | 134.84 | 1337.6128 | 30.4743 | 962.3532 | 29327.03 | 8681.9487 | 150.375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1078 | 1129 | 1431 | 51 | 8681.9487 | 59.625 | 2.152 | 2.152 | 27.2 | 28.21 | 23.18 | 29.15 | 994.4 | 50.08 | 0.9374 | 95.89 | 86.75 | -9.14 | 12295 | 11795 | -500 | 4.304 | 24 | 24 | 24 | 7.93 | 2.2 | 3.6 | 1.8 | 1.5
| 2018-03-06 | 72.06 | 66.01% | 61.56 | 81 | 61 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3665 | 3609 | 3609 | 3526 | 3636 | 45 | 0 | 47 | 0 | 60 | 0 | 110 | -83 | 155 | 97.74% | 152.7083 | 96.21% | 100% | 100% | 9.9 | 136.13 | 1347.687 | 30.4459 | 964.9877 | 29379.89 | 8714.5709 | 150.375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1074 | 1124 | 1438 | 50 | 8714.5709 | 59.9167 | 2.177 | 2.177 | 27.2 | 28.09 | 23.01 | 29 | 995.2 | 49.99 | 0.9372 | 95.96 | 86.64 | -9.32 | 12291 | 11784 | -507 | 4.354 | 24 | 24 | 24 | 9.53 | 2.1 | 3.5 | 1.8 | 1.5
| 2018-03-07 | 74 | 63% | 62 | 88 | 64 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3648 | 3611 | 3611 | 3528 | 3637 | 45 | 0 | 46 | 0 | 61 | 0 | 109 | -83 | 155 | 97.77% | 152 | 96.71% | 100% | 100% | 9.914 | 133.79 | 1326.3941 | 30.1611 | 978.3784 | 29508.95 | 8740.1769 | 150.4583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1069 | 1113 | 1455 | 44 | 8740.1769 | 60.625 | 2.278 | 2.291 | 27.2 | 27.51 | 22.48 | 28.71 | 992.8 | 50.02 | 0.9379 | 95.89 | 86.54 | -9.35 | 12082 | 11651 | -431 | 4.569 | 24 | 24 | 24 | 6.21 | 2.1 | 3.6 | 1.7 | 1.6
| 2018-03-08 | 75 | 58% | 61 | 86 | 65 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 23 | 34 | 3643 | 3592 | 3585 | 3517 | 3626 | 44 | 0 | 46 | 0 | 60 | 0 | 109 | -68 | 155 | 97.47% | 151.7917 | 96.54% | 100% | 99.83% | 9.9 | 134.58 | 1332.342 | 30.5469 | 966.372 | 29519.66 | 8772.2496 | 149.6667 | 0 | 0 | 0 | 0 | 14 | 26 | 0 | 1072 | 1114 | 1440 | 42 | 8772.2496 | 60 | 2.257 | 2.257 | 27.2 | 28.07 | 22.9 | 28.8 | 993.5 | 50.07 | 0.9379 | 95.8 | 86.5 | -9.3 | 12319 | 11836 | -483 | 4.514 | 24 | 24 | 24 | 9.4 | 2.1 | 3.6 | 1.8 | 1.6
| 2018-03-09 | 72 | 60% | 59 | 81 | 60 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 23 | 18 | 3670 | 3598 | 3589 | 3519 | 3626 | 45 | 0 | 47 | 0 | 59 | 0 | 107 | -70 | 154 | 98.11% | 152.9167 | 95.89% | 100% | 99.83% | 9.86 | 134.1 | 1322.226 | 30.4988 | 961.2837 | 29317.99 | 8707.0804 | 149.9167 | 0 | 0 | 0 | 0 | 9 | 42 | 0 | 1081 | 1127 | 1418 | 46 | 8707.0804 | 59.0833 | 2.059 | 2.059 | 27.2 | 28.45 | 23.31 | 28.63 | 995.5 | 50.04 | 0.9379 | 95.74 | 86.44 | -9.3 | 12368 | 11855 | -513 | 4.118 | 24 | 24 | 24 | 7.1 | 2.1 | 3.5 | 1.8 | 1.7
| 2018-03-10 | 73.2 | 59.8% | 60.06 | 88 | 62 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3653 | 3592 | 3592 | 3517 | 3624 | 45 | 0 | 47 | 0 | 59 | 0 | 107 | -75 | 154 | 98.05% | 152.2083 | 96.28% | 100% | 100% | 9.763 | 135.36 | 1321.5197 | 30.3662 | 962.4971 | 29227.38 | 8686.0676 | 149.6667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1075 | 1125 | 1424 | 50 | 8686.0676 | 59.3333 | 2.091 | 2.091 | 27.2 | 28.21 | 23.12 | 28.65 | 994.1 | 50.05 | 0.9374 | 95.77 | 86.45 | -9.32 | 12333 | 11806 | -527 | 4.182 | 24 | 24 | 24 | 6.9 | 2.2 | 3.6 | 1.8 | 1.6
| 2018-03-11 | 75.61 | 60.64% | 62.24 | 91 | 67 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3636 | 3189 | 3189 | 3122 | 3216 | 44 | 0 | 46 | 0 | 59 | 0 | 94 | -67 | 137 | 97.81% | 151.5 | 85.86% | 100% | 89.26% | 9.878 | 137.73 | 1360.4969 | 25.9822 | 962.7961 | 25015.57 | 8448.4519 | 132.875 | 0 | 0 | 0 | 0 | 16 | 1440 | 0 | 1066 | 1112 | 1038 | 46 | 8448.4519 | 43.25 | 0 | 0 | 27.2 | 28.06 | 22.9 | 28.75 | 992.6 | 50.03 | 0.9364 | 95.96 | 86.48 | -9.48 | 12653 | 12347 | -306 | 0 | 0 | 0 | 24 | 7.53 | 2.2 | 3.7 | 1.7 | 1.6
Week 11 | 2018-03-12 | 76.7 | 61.09% | 63.34 | 94 | 64 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 3621 | 3388 | 3388 | 3314 | 3416 | 44 | 0 | 46 | 0 | 59 | 0 | 102 | -74 | 151 | 94.26% | 150.875 | 91.52% | 100% | 95.08% | 9.7 | 132.62 | 1286.414 | 28.3887 | 963.185 | 27343.58 | 8639.105 | 141.1667 | 0 | 0 | 0 | 0 | 16 | 660 | 0 | 1060 | 1105 | 1251 | 45 | 8639.105 | 52.125 | 1.305 | 1.305 | 27.2 | 27.99 | 22.9 | 28.7 | 991.4 | 50.02 | 0.9382 | 95.98 | 86.48 | -9.5 | 12846 | 12584 | -262 | 2.61 | 13 | 13 | 24 | 7.33 | 2.1 | 3.6 | 1.7 | 1.5
| 2018-03-13 | 77.8 | 61.8% | 64.5 | 98 | 66 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3617 | 3553 | 3553 | 3467 | 3576 | 44 | 0 | 46 | 0 | 60 | 0 | 109 | -86 | 152 | 98.03% | 150.7083 | 95.85% | 100% | 100% | 9.728 | 135.75 | 1320.576 | 30.2841 | 959.0907 | 29045.19 | 8758.5134 | 148.0417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1053 | 1097 | 1426 | 44 | 8758.5134 | 59.4167 | 2.16 | 2.253 | 27.2 | 27.88 | 22.77 | 28.75 | 988.3 | 50.07 | 0.9373 | 96.02 | 86.53 | -9.49 | 12436 | 11956 | -480 | 4.413 | 24 | 24 | 24 | 6.98 | 2.1 | 3.4 | 1.7 | 1.6
| 2018-03-14 | 73.9 | 65.9% | 63.2 | 83 | 65 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3656 | 3553 | 3553 | 3473 | 3581 | 44 | 0 | 46 | 0 | 59 | 0 | 108 | -80 | 152 | 98.16% | 152.3333 | 94.99% | 100% | 100% | 9.662 | 134.83 | 1302.7275 | 30.2085 | 963.2991 | 29099.83 | 8753.9757 | 148.0417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1058 | 1103 | 1420 | 45 | 8753.9757 | 59.1667 | 2.16 | 2.16 | 27.2 | 27.93 | 22.79 | 28.71 | 987.13 | 50.07 | 0.9379 | 95.99 | 86.48 | -9.51 | 12390 | 11912 | -478 | 4.32 | 24 | 24 | 24 | 5.78 | 2.2 | 3.6 | 1.8 | 1.6
| 2018-03-15 | 74.56 | 53.48% | 59.15 | 87 | 64 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3643 | 3570 | 3570 | 3512 | 3621 | 45 | 0 | 47 | 0 | 59 | 0 | 109 | -58 | 154 | 97.97% | 151.7917 | 96.4% | 100% | 100% | 9.73 | 134.97 | 1313.2581 | 30.2923 | 965.2462 | 29239.5 | 8699.5325 | 148.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1076 | 1123 | 1422 | 47 | 8699.5325 | 59.25 | 2.093 | 2.093 | 27.2 | 28.13 | 23.03 | 28.69 | 989.63 | 50.11 | 0.9377 | 95.53 | 86.28 | -9.25 | 12286 | 11789 | -497 | 4.186 | 24 | 24 | 24 | 6.58 | 2.2 | 3.65 | 1.8 | 1.7
| 2018-03-16 | 75 | 52.17% | 58.5 | 88 | 63 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3637 | 3578 | 3578 | 3501 | 3611 | 45 | 0 | 47 | 0 | 59 | 0 | 110 | -77 | 153 | 98.34% | 151.5417 | 96.26% | 100% | 100% | 9.649 | 135.79 | 1310.2377 | 30.2423 | 964.0736 | 29155.85 | 8702.1102 | 149.0833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1077 | 1122 | 1412 | 45 | 8702.1102 | 58.8333 | 2.025 | 2.025 | 27.2 | 28.22 | 23.09 | 28.38 | 990.71 | 50.05 | 0.9374 | 95.51 | 86.31 | -9.2 | 12313 | 11811 | -502 | 4.05 | 24 | 24 | 24 | 8.42 | 2.2 | 3.6 | 1.8 | 1.6
| 2018-03-17 | 75.89 | 54.67% | 60.38 | 90 | 64 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 23 | 31 | 3633 | 3572 | 3564 | 3488 | 3597 | 45 | 0 | 47 | 0 | 59 | 0 | 109 | -76 | 154 | 97.32% | 151.375 | 96.01% | 100% | 99.85% | 9.68 | 138.41 | 1339.8088 | 29.8629 | 974.9009 | 29113.369 | 8730.8423 | 148.8333 | 0 | 0 | 0 | 0 | 11 | 29 | 0 | 1070 | 1116 | 1411 | 46 | 8730.8423 | 58.7917 | 2.072 | 2.072 | 27.2 | 27.78 | 22.71 | 28.52 | 991.8 | 50.06 | 0.9365 | 95.61 | 86.37 | -9.24 | 12203 | 11728 | -475 | 4.144 | 24 | 24 | 24 | 8.4 | 2.1 | 3.6 | 1.8 | 1.6
| 2018-03-18 | 74.98 | 55.93% | 59.98 | 87 | 65 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3645 | 3210 | 3210 | 3137 | 3230 | 45 | 0 | 46 | 0 | 59 | 0 | 93 | -73 | 138 | 97.52% | 151.875 | 86.06% | 100% | 89.33% | 9.725 | 135.02 | 1313.0695 | 25.9309 | 968.4592 | 25113 | 8423.9941 | 133.75 | 0 | 0 | 0 | 0 | 16 | 1440 | 0 | 1072 | 1115 | 1043 | 43 | 8423.9941 | 43.4583 | 0 | 0 | 27.2 | 28 | 22.88 | 28.43 | 992.5 | 50.08 | 0.9374 | 95.61 | 86.38 | -9.23 | 12273 | 11788 | -485 | 0 | 0 | 0 | 24 | 8.26 | 2.1 | 3.7 | 1.7 | 1.6
Week 12 | 2018-03-19 | 75 | 56% | 61 | 85 | 66 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 12 | 42 | 3643 | 3388 | 3388 | 3322 | 3424 | 44 | 0 | 46 | 0 | 59 | 0 | 102 | -66 | 151 | 94.48% | 151.7917 | 91.19% | 100% | 95.26% | 9.64 | 135.04 | 1301.7856 | 28.1734 | 972.5082 | 27398.91 | 8639.5833 | 141.1667 | 0 | 0 | 0 | 0 | 15 | 678 | 0 | 1068 | 1111 | 1245 | 43 | 8639.5833 | 51.875 | 1.158 | 1.158 | 27.2 | 27.89 | 22.74 | 28.54 | 993.8 | 50.08 | 0.9374 | 95.63 | 86.41 | -9.22 | 12267 | 11784 | -483 | 2.316 | 13 | 12.7 | 24 | 6.3 | 2.2 | 3.6 | 1.8 | 1.8
| 2018-03-20 | 75 | 60.9% | 62.5 | 87 | 65 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3647 | 3557 | 3557 | 3478 | 3588 | 44 | 0 | 46 | 0 | 59 | 0 | 110 | -79 | 153 | 97.71% | 151.9583 | 95.37% | 100% | 100% | 9.635 | 134.24 | 1293.4024 | 30.2509 | 962.6034 | 29119.59 | 8744.3911 | 148.2083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1063 | 1105 | 1420 | 42 | 8744.3911 | 59.1667 | 2.122 | 2.122 | 27.2 | 27.98 | 22.88 | 28.31 | 991.1 | 50.09 | 0.9377 | 95.8 | 86.5 | -9.3 | 12376 | 11898 | -478 | 4.244 | 24 | 24 | 24 | 6.1 | 2.2 | 3.5 | 1.8 | 1.6
| 2018-03-21 | 70 | 67% | 60 | 79 | 61 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3680 | 3592 | 3592 | 3519 | 3625 | 44 | 0 | 46 | 0 | 60 | 0 | 106 | -73 | 154 | 98.08% | 153.3333 | 95.62% | 100% | 100% | 9.6 | 135.95 | 1305.12 | 30.3587 | 969.5748 | 29435.051 | 8735.4848 | 149.6667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1075 | 1118 | 1432 | 43 | 8735.4848 | 59.6667 | 2.122 | 2.122 | 27.2 | 28.05 | 22.96 | 28.28 | 991.3 | 50.06 | 0.9368 | 95.8 | 86.38 | -9.42 | 12262 | 11798 | -464 | 4.244 | 24 | 24 | 24 | 8.2 | 2.1 | 3.4 | 1.8 | 1.6
| 2018-03-22 | 71.72 | 64.7% | 61.09 | 82 | 61 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3663 | 3589 | 3589 | 3511 | 3618 | 45 | 0 | 46 | 0 | 60 | 0 | 107 | -78 | 153 | 98.53% | 152.625 | 95.85% | 100% | 100% | 9.596 | 137.7 | 1321.3692 | 30.3028 | 970.5671 | 29410.881 | 8753.1331 | 149.5417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1071 | 1112 | 1435 | 41 | 8753.1331 | 59.7917 | 2.149 | 2.149 | 27 | 27.93 | 22.89 | 27.65 | 992.08 | 50.05 | 0.9365 | 95.8 | 86.44 | -9.36 | 12252 | 11781 | -471 | 4.298 | 24 | 24 | 24 | 4.45 | 2.2 | 3.5 | 1.6 | 1.4
| 2018-03-23 | 75.1 | 60.3% | 61.83 | 87 | 62 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3636 | 3566 | 3566 | 3497 | 3606 | 44 | 0 | 46 | 0 | 60 | 0 | 109 | -69 | 153 | 98.2% | 151.5 | 96.18% | 100% | 100% | 9.591 | 135.72 | 1301.6905 | 30.2248 | 970.5259 | 29333.961 | 8760.5523 | 148.5833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1066 | 1104 | 1436 | 38 | 8760.5523 | 59.8333 | 2.185 | 2.185 | 27 | 27.76 | 22.75 | 27.83 | 992.3 | 50.05 | 0.9368 | 95.68 | 86.4 | -9.28 | 12243 | 11800 | -443 | 4.37 | 24 | 24 | 24 | 7.12 | 2 | 3.4 | 1.6 | 1.2
| 2018-03-24 | 76.4 | 58.3% | 62.18 | 88 | 64 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3630 | 3564 | 3564 | 3490 | 3597 | 44 | 0 | 46 | 0 | 60 | 0 | 107 | -74 | 153 | 97.96% | 151.25 | 96.14% | 100% | 100% | 9.519 | 132.09 | 1257.3647 | 30.609 | 958.3236 | 29333.3268 | 8765.2411 | 148.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1064 | 1105 | 1428 | 41 | 8765.2411 | 59.5 | 2.173 | 2.173 | 27 | 28.15 | 23.02 | 28.2 | 994.7 | 50.02 | 0.9381 | 95.7 | 86.4 | -9.3 | 12435 | 11958 | -477 | 4.346 | 24 | 24 | 24 | 7 | 2.1 | 3.5 | 1.8 | 1.1
| 2018-03-25 | 79.2 | 56.8% | 64 | 94 | 64 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3612 | 3210 | 3210 | 3145 | 3239 | 44 | 0 | 46 | 0 | 60 | 0 | 94 | -65 | 139 | 97.09% | 150.5 | 87.07% | 100% | 92% | 9.383 | 134.27 | 1259.8554 | 26.681 | 959.834 | 25609.331 | 8543.4615 | 133.75 | 0 | 0 | 0 | 0 | 12 | 1440 | 0 | 1057 | 1098 | 1084 | 41 | 8543.4615 | 45.1667 | 0.381 | 0.32 | 27 | 28.06 | 22.82 | 28.26 | 995.17 | 50.03 | 0.9374 | 95.71 | 86.45 | -9.26 | 12472 | 11951 | -521 | 0.701 | 24 | 24 | 24 | 7.07 | 2.1 | 3.4 | 1.8 | 1.2
Week 13 | 2018-03-26 | 80.1 | 53.6% | 66 | 96 | 66 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3596 | 3516 | 3516 | 3459 | 3569 | 44 | 0 | 46 | 0 | 59 | 0 | 110 | -57 | 153 | 97.19% | 149.8333 | 96.19% | 100% | 100% | 9.503 | 134.85 | 1281.4796 | 30.746 | 941.5583 | 28949.1511 | 8739.7024 | 146.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1057 | 1096 | 1416 | 39 | 8739.7024 | 59 | 2.196 | 2.196 | 27 | 28.65 | 23.33 | 28.15 | 991.96 | 50.02 | 0.9377 | 95.64 | 86.45 | -9.19 | 12739 | 12193 | -546 | 4.392 | 24 | 24 | 24 | 5.83 | 2.1 | 3.4 | 1.8 | 1.2
| 2018-03-27 | 80.2 | 53.2% | 63.5 | 94 | 65 | 11 | 8 | 24 | 0 | 0 | 0 | 0 | 0 | 11 | 8 | 3594 | 2624 | 2624 | 2580 | 2675 | 45 | 744 | 45 | 0 | 59 | 0 | 95 | -44 | 153 | 72.85% | 149.75 | 71.79% | 84.4% | 73.25% | 9.496 | 135.91 | 1290.6014 | 22.66 | 958.3295 | 21715.7469 | 8917.1893 | 109.3333 | 20 | 76 | 0 | 0 | 29 | 772 | 0 | 523 | 1088 | 1064 | 565 | 8917.1893 | 44.3333 | 1 | 2.444 | 27.9 | 14.26 | 22.76 | 27.72 | 987.42 | 50 | 0.9374 | 95.5 | 86.55 | -8.95 | 12365 | 12001 | -364 | 3.444 | 11.37 | 24 | 10.38 | 6.92 | 2.1 | 3.6 | 1.8 | 1.2
| 2018-03-28 | 82.03 | 56.68% | 66.29 | 96 | 68 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3575 | 3502 | 3502 | 3432 | 3543 | 44 | 0 | 45 | 0 | 58 | 0 | 111 | -70 | 150 | 98.42% | 148.9583 | 96% | 100% | 100% | 9.548 | 137.28 | 1310.7494 | 29.71 | 965.4578 | 28683.7517 | 8739.6565 | 145.9167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1063 | 1081 | 1399 | 18 | 8739.6565 | 58.2917 | 2.029 | 2.063 | 28.93 | 27.81 | 22.33 | 28.15 | 989.4 | 50.07 | 0.9368 | 96.63 | 86.63 | -10 | 12289 | 11929 | -360 | 4.092 | 24 | 24 | 24 | 7.25 | 2 | 4 | 1.8 | 1.3
| 2018-03-29 | 83.88 | 48.86% | 64.45 | 98 | 70 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3556 | 3519 | 3519 | 3448 | 3557 | 44 | 0 | 45 | 0 | 58 | 0 | 109 | -71 | 152 | 97.51% | 148.1667 | 96.96% | 100% | 100% | 9.576 | 134.64 | 1289.3126 | 29.839 | 969.8335 | 28938.862 | 8766.872 | 146.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1067 | 1089 | 1401 | 22 | 8766.872 | 58.375 | 2.051 | 2.051 | 28.86 | 27.83 | 22.43 | 27.99 | 988.5 | 50.14 | 0.938 | 96.45 | 86.43 | -10.02 | 12253 | 11869 | -384 | 4.102 | 24 | 24 | 24 | 8.95 | 2.2 | 4.2 | 1.8 | 1.5
| 2018-03-30 | 85.96 | 41.87% | 63.13 | 103 | 72 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 3537 | 3491 | 3491 | 3416 | 3527 | 44 | 0 | 45 | 0 | 58 | 0 | 111 | -75 | 153 | 96.05% | 147.375 | 96.58% | 100% | 99.63% | 9.592 | 136.52 | 1309.4998 | 29.238 | 969.6547 | 28350.7634 | 8682.7468 | 145.4583 | 0 | 0 | 0 | 0 | 13 | 60 | 0 | 1068 | 1088 | 1371 | 20 | 8682.7468 | 57.125 | 1.863 | 1.863 | 28.74 | 27.66 | 22.27 | 27.99 | 985.67 | 50.1 | 0.9375 | 96.16 | 86.43 | -9.73 | 12168 | 11811 | -357 | 3.726 | 23 | 23 | 24 | 7.77 | 2.1 | 4.2 | 1.8 | 1.5
| 2018-03-31 | 85 | 44% | 63 | 101 | 70 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 3540 | 3359 | 3359 | 3305 | 3407 | 44 | 0 | 45 | 0 | 58 | 0 | 102 | -54 | 152 | 93.39% | 147.5 | 93.36% | 100% | 95.32% | 9.62 | 138.31 | 1330.5422 | 28.209 | 968.1199 | 27309.6936 | 8665.7294 | 139.9583 | 0 | 0 | 0 | 0 | 15 | 660 | 0 | 1069 | 1086 | 1252 | 17 | 8665.7294 | 52.1667 | 1.259 | 1.255 | 28.8 | 27.88 | 22.44 | 27.8 | 986.2 | 50.08 | 0.937 | 96.25 | 86.52 | -9.73 | 12254 | 11901 | -353 | 2.514 | 13 | 13 | 24 | 7.2 | 2.1 | 4.2 | 1.8 | 1.3
| 2018-04-01 | [26 empty] | 0 | 0 |  | no data | no data | no data | no data | no data |  |  | 0 |  |  | 0 | no data | [11 empty] | 0 | no data | 0 | [11 empty] | 0 |  |  | 0 | 0
| Monthly | 75.619 | 60.93% | 61.8807 | 87.3214 | 63.6071 | 659 | 8 | 660 | 10 | 0 | 0 | 0 | 0 | 9 | 15 | 112645 | 96863 | 96839 | 105205.76 | 97771 | 44.5 | 744 | 45.9643 | 643 | 59.7857 | 0 | -7434.76 | -2017 | 151.7143 | 95.89% | 151.4046 | 93.4% | 99.06% | 96.93% | 296.393 | 136.1052 | 40262.5603 | 907.5056 | 964.6272 | 875424.2585 | 8703.7708 |  | 20 | 76 | 23 | 67 | 168 | 7245 | 0 | 29376 | 30422 | 37973 | 1046 | 8703.7708 | 56.5074 | 52.524 | 52.804 | 27.2511 | 27.5639 | 22.4796 | 28.0779 | 991.8775 | 50.0536 | 0.93709 | 95.8071 | 86.2975 |  | 12364.4286 | 11938.4286 |  | 105.328 | 589.37 | 590.12 | 658.38 | 205.3
| Totals | Avg.F | % Avg. |  | M Avg | m Avg | hrs | min | hrs | min | hrs | min | hrs | min | Avg Int Avi | Avg Ext Avi | MWhr Total | MWhr Total | MWhr Total | MWhr Total | MWhr Total | MW Avg | Total min | Avg MW | Total min | Avg MW | Total min | MWhr | Total MW | Av Max D/Gen | Av. DailyLF | Avg. | Avg. |  | Avg. | Total | Avg. |  | Total | Avg. |  | Avg. | [7 empty] | Total |  |  |  |  | Avg.
| Weeks data | Site Avg. Amb. Temp F | Site Avg. Relative humidity % |  | M Avg: Site Maximum/Minumum Temperature; hrs: CT-1 Base Load Hours; hrs: CT-2 Base Load Hours; hrs: CT-1 stand by hours / min; hrs: CT-2 standby hours / min | Plant ambient Corrected maximum Load hours/min |  | Average Corrected Plant Capacity | Ambient Corrected Declared Avail'y (MWH) | Av Plant WAPDA Dispatch | Net Plant Export (MWH) | Gross Generation | CT1 Av Cap (MW) | CT1 Unavail minutes | CT2 Av Cap (MW) | CT2 Unavail minutes | ST Unavail minutes | ST Average Cap (MW) | Plant Aux Load including Colony Load MWH | Differenece (+/-) MW | Maximum Daily Generation | Daily Load Factor | Avg. Corrected Plant | Plant Capacity Facto | Plant Availability Factor | Equivalent Plant Availability | LBtu gas flow mmscf | 1 LBtu gas (Average Btu/scf) | LBTU MMBTU | PL gas flow (mscf/week) | 1 PL gas (Average Btu/scf) | HBTU MMBTU | Plant Net Heat Rate (Btu/Kwh) | [11 empty] | 41
| Week 9 | 71.4514 | 67.5871 | 61.8186 | 82.8571 | 61.7143 | 168 | 0 | 156 | 10 | 0 | 0 | 0 | 0 | 130 | 24 | 3667 | 3482.7143 | 3457.7143 | 23704 | 24441 | 44.7143 | No outage | 44.5714 | 643 | No outage | 62 | no data | -500 | 154.4286 | 94.21% | 152.7917 | 92.36% | 98.08% | 96.07% | 66.055 | 138.8486 | 9171.6424 | 207.788 | 962.2327 | 199940.3747 | 8822.2013
| Week 10 | 73.3014 | 62.08% | 60.9986 | 85.5714 | 63 | 168 | -2 | 168 | 0 | 0 | 0 | 0 | 0 | 142 | 2 | 3654.5714 | 3542.8571 | 3540.5714 | 24261 | 25003 | 44.7143 | No outage | 46.5714 | No outage | No outage | 59.7143 | 742 | -523 | 152.2857 | 97.73% | 152.2738 | 94.83% | 100% | 98.42% | 69.135 | 135.2186 | 9348.3359 | 208.4753 | 965.524 | 201287.9418 | 8678.6494
| Week 11 | 75.5471 | 57.86% | 61.2929 | 89.5714 | 64.4286 | 168 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 132 | 31 | 3636 | 3489.1429 | 3488 | 23892 | 24632 | 44.5714 | No outage | 46.4286 | No outage | No outage | 59.1429 | 740 | -524 | 150.5714 | 97.37% | 151.5 | 93.87% | 100% | 97.75% | 67.874 | 135.3414 | 9186.1641 | 179.2788 | 964.9659 | 172997.9625 | 8672.5819
| Week 12 | 74.6314 | 0.60571 | 61.8 | 86 | 63.2857 | 168 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 132 | 42 | 3644.4286 | 3495.1429 | 3495.1429 | 23962 | 24697 | 44.1429 | No outage | 46 | No outage | 418 | 59.7143 | 735 | -504 | 150.8571 | 97.44% | 151.8512 | 93.92% | 100% | 98.18% | 66.964 | 135.0014 | 9040.2357 | 206.6006 | 966.2767 | 199633.3771 | 8705.9782
| Week 13 | 82.8617 | 0.49702 | 64.395 | 98 | 68.5 | 131 | 8 | 144 | 0 | 0 | 0 | 0 | 0 | 119 | 8 | 3566.3333 | 3335.1667 | 3335.1667 | 19640 | 20278 | 44.1667 | 744 | 45.1667 | No outage | 350 | 58.3333 | 638 | -371 | 152.1667 | 92.57% | 148.5972 | 91.81% | 97.4% | 94.7% | 57.335 | 136.2517 | 7811.9893 | 170.402 | 962.1589 | 163953.8089 | 8751.9827
| Date | Plant Status Whether Normal Operation or Tripping (State full detail for trippings/return to normal).
| 2018-03-01 | Normal operation.Plant remained at maximum load from 0000 to 2400 hrs.
| 2018-03-02 | Normal operation.Plant remained at maximum load from 0000 to 2400 hrs.
| 2018-03-03 | Normal operation.Plant remained at maximum load from 0000 to 2400 hrs.
| 2018-03-04 | Gas turbine CT-2 de-synch @0019hrs and again synch @1102hrs after compressor offline washing.
| 2018-03-05 | Normal operation.Plant remained at maximum load from 0000 to 2400 hrs.
| 2018-03-06 | Normal operation.Plant remained at maximum load from 0000 to 2400 hrs.
| 2018-03-07 | Normal operation.Plant remained at maximum load from 0000 to 2400 hrs.
| 2018-03-08 | Normal operation. NPCC load demand of 132 MW received from 0359 ~ 0416 hrs.
| 2018-03-09 | Normal operation. NPCC load demand of 134 MW received from 0102 ~ 0136 hrs.
| 2018-03-10 | Normal operation.Plant remained at maximum load from 0000 to 2400 hrs.
| 2018-03-11 | Plant load remained 128 ~ 133 MW from 0000 hrs to 2400 hrs, as both duct burners kept off to remain within contractual heat rate.
| 2018-03-12 | Plant load remained restricted 129-132 MW from 0000-1100hrs to remain within contractual heatrate.
| 2018-03-13 | Normal operation.Plant remained at maximum load from 0000 to 2400 hrs.
| 2018-03-14 | Normal operation.Plant remained at maximum load from 0000 to 2400 hrs.
| 2018-03-15 | Normal operation.Plant remained at maximum load from 0000 to 2400 hrs.
| 2018-03-16 | Normal operation.Plant remained at maximum load from 0000 to 2400 hrs.
| 2018-03-17 | Normal operation.NPCC load demand of 133 MW remained from 0409 hrs to 0432 hrs.
| 2018-03-18 | Plant load remained 128 ~ 133 MW from 0000 hrs to 2400 hrs, as both duct burners kept off to remain within contractual heat rate.
| 2018-03-19 | Plant load remained restricted 130-133 MW from 0000-1100hrs to remain within contractual heatrate.
| 2018-03-20 | Normal operation. Plant remained at maximum load from 0000 to 2400 hrs.
| 2018-03-21 | Normal operation. Plant remained at maximum load from 0000 to 2400 hrs.
| 2018-03-22 | Normal operation. Plant remained at maximum load from 0000 to 2400 hrs.
| 2018-03-23 | Normal operation. Plant remained at maximum load from 0000 to 2400 hrs.
| 2018-03-24 | Normal operation. Plant remained at maximum load from 0000 to 2400 hrs.
| 2018-03-25 | Plant load remained 128 ~ 134 MW from 0000 hrs to 2400 hrs, as duct firing reduced to minimum to remain within contractual heat rate.
| 2018-03-26 | Normal operation. Plant remained at maximum load from 0000 to 2400 hrs.
| 2018-03-27 | CT-1 de-synch @ 0650 hrs & synch @ 1826 hrs for compressor offline washing, availing "Approved Scheduled Outage-2018".
| 2018-03-28 | Normal operation. Plant remained at maximum load from 0000 to 2400 hrs.
| 2018-03-29 | Normal operation. Plant remained at maximum load from 0000 to 2400 hrs.
| 2018-03-30 | Normal operation.Plant remained at maximum load from 0000 to 2300 hrs.Duct burners taken out of service at 2300 hrs to keep within restricted plant heat rate.
| 2018-03-31 | Plant load remained 128 ~ 132 MW from 0000 hrs to 1100 hrs, as both duct burners kept off to remain within contractual heat rate.

## April
2018-04-01
| Date | Site Avg. Ambient Temp.F | Site Avg. Relative Humidty % | Site Avg. Ambient Wetbulb Temp.F | Site Ambient Temp |  | Base load hours |  |  |  | Standby hours |  |  |  | Plant ambient corrected Max Load |  | Corrected Plant Capacity | Ambient Corrected Daclared Avail'y (MWH) | Plant WAPDA Dispatch (MWH) | Net Plant Export (MWH) | Gross Generation | CT1 Average Cap (MW) | CT1 Unavail minutes | CT2 Average Cap (MW) | CT2 Unavail minutes | ST Average Cap (MW) | ST Unavail minutes | Plant Aux Load including Colony Load MWH | Differenece (+/-) MW | Maximum Daily Generation | Daily Load Factor | Avg. Corrected Plant Capacity | Plant Capacity Factor | Plant Availability Factor | Equivalent Plant Availability | LBtu gas flow (mmscf/day) | 1 LBtu gas (Average Btu/scf) | LBTU MMBTU | 1 HBtu gas flow (mmscf/day) | 1 HBtu gas (Average Btu/scf) | HBTU MMBTU | HHV Net Heat Rate (Btu/Kwh) | Avg. declared availability | CT1 Derated MW | CT1 derated mintutes | CT-2 derated MW | CT-2 derated mintutes | ST derated MW | ST derated mintutes | WAPDA Backfeed (MWH) | CT-1 Gross Generation (MWH) | CT-2 Gross Generation (MWH) | STG Gross Generation (MWH) | CT-1 & CT-2 MWH difference | Base load Heat Rate | STG load | DB1 | DB2 | CT1 | CT1 Gas flow | CT2 Gas flow |  | Pamb | Freq. Hz | LBTU Gas Specific gravity | CT-1 compressor efficiency(%) | CT-2 compressor efficiency(%) | CT-1 Heat Rate (Btu/Kwh) | CT-2 Heat Rate (Btu/Kwh) |  | DB(1+2) | DB-1 Ops Hours | DB-2 Ops Hours | CT-1 Wetcomprssion Ops Hours | RO Operation Hours | CT1 T/G Brg |  | CT2 T/G Brg
[7 empty] | CT1 |  | CT2 |  | CT1 |  | CT2 | [43 empty] | mmscf/d | mmscf/d | WetC flow | HBTU KPPH | HBTU KPPH | LBTU KPPH | mbar | Hz | [6 empty] | mmscf/d |  |  |  |  | Supply air pressure | Seal air pressure | Supply air pressure | Seal air pressure
[5 empty] | Max | Min | hrs | min | hrs | min | hrs | min | hrs | min | hrs | min | [42 empty] | gpm | [16 empty] | Psi | "WC | Psi | "WC
Week 13 | 2018-03-26 | 80.1 | 53.6% | 66 | 96 | 66 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3596 | 3516 | 3516 | 3459 | 3569 | 44 | 0 | 46 | 0 | 59 | 0 | 110 | -57 | 153 | 97.19% | 149.8333 | 96.19% | 100% | 100% | 9.503 | 134.85 | 1281.4796 | 30.746 | 941.6 | 28950.4336 | 8740.0732 | 146.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1057 | 1096 | 1416 | 39 | 8740.0732 | 59 | 2.196 | 2.196 | 27 | 28.65 | 23.33 | 28.15 | 991.96 | 50.02 | 0.9377 | 95.64 | 86.45 | 12739 | 12193 | -546 | 4.392 | 24 | 24 | 24 | 5.83 | 2.1 | 3.4 | 1.8 | 1.2
| 2018-03-27 | 80.2 | 53.2% | 63.5 | 94 | 65 | 11 | 8 | 24 | 0 | 0 | 0 | 0 | 0 | 11 | 8 | 3594 | 2624 | 2624 | 2580 | 2675 | 45 | 744 | 45 | 0 | 59 | 0 | 95 | -44 | 153 | 72.85% | 149.75 | 71.79% | 84.4% | 73.25% | 9.496 | 135.91 | 1290.6014 | 22.66 | 958.3 | 21715.078 | 8916.93 | 109.3333 | 20 | 76 | 0 | 0 | 29 | 772 | 0 | 523 | 1088 | 1064 | 565 | 8916.93 | 44.3333 | 1 | 2.444 | 27.9 | 14.26 | 22.76 | 27.72 | 987.42 | 50 | 0.9374 | 95.5 | 86.55 | 12365 | 12001 | -364 | 3.444 | 11.37 | 24 | 10.38 | 6.92 | 2.1 | 3.6 | 1.8 | 1.2
| 2018-03-28 | 82.03 | 56.68% | 66.29 | 96 | 68 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3575 | 3502 | 3502 | 3432 | 3543 | 44 | 0 | 45 | 0 | 58 | 0 | 111 | -70 | 150 | 98.42% | 148.9583 | 96% | 100% | 100% | 9.548 | 137.28 | 1310.7494 | 29.71 | 965.4 | 28682.034 | 8739.156 | 145.9167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1063 | 1081 | 1399 | 18 | 8739.156 | 58.2917 | 2.029 | 2.063 | 28.93 | 27.81 | 22.33 | 28.15 | 989.4 | 50.07 | 0.9368 | 96.63 | 86.63 | 12289 | 11929 | -360 | 4.092 | 24 | 24 | 24 | 7.25 | 2 | 4 | 1.8 | 1.3
| 2018-03-29 | 83.88 | 48.86% | 64.45 | 98 | 70 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3556 | 3519 | 3519 | 3448 | 3557 | 44 | 0 | 45 | 0 | 58 | 0 | 109 | -71 | 152 | 97.51% | 148.1667 | 96.96% | 100% | 100% | 9.82 | 134.64 | 1322.1648 | 29.84 | 970 | 28944.8 | 8778.122 | 146.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1067 | 1089 | 1401 | 22 | 8778.122 | 58.375 | 2.051 | 2.051 | 28.86 | 27.83 | 22.43 | 27.99 | 988.5 | 50.14 | 0.938 | 96.45 | 86.43 | 12253 | 11869 | -384 | 4.102 | 24 | 24 | 24 | 8.95 | 2.2 | 4.2 | 1.8 | 1.5
| 2018-03-30 | 85.96 | 41.87% | 63.13 | 103 | 72 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 3537 | 3491 | 3491 | 3416 | 3527 | 44 | 0 | 45 | 0 | 58 | 0 | 111 | -75 | 153 | 96.05% | 147.375 | 96.58% | 100% | 99.63% | 9.85 | 136.52 | 1344.722 | 29.4 | 970 | 28518 | 8742.0146 | 145.4583 | 0 | 0 | 0 | 0 | 13 | 60 | 0 | 1068 | 1088 | 1371 | 20 | 8742.0146 | 57.125 | 1.863 | 1.863 | 28.74 | 27.66 | 22.27 | 27.99 | 985.67 | 50.1 | 0.9375 | 96.16 | 86.43 | 12168 | 11811 | -357 | 3.726 | 23 | 23 | 24 | 7.77 | 2.1 | 4.2 | 1.8 | 1.5
| 2018-03-31 | 85 | 44% | 63 | 101 | 70 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 3540 | 3359 | 3359 | 3305 | 3407 | 44 | 0 | 45 | 0 | 58 | 0 | 102 | -54 | 152 | 93.39% | 147.5 | 93.36% | 100% | 95.32% | 9.78 | 138.31 | 1352.6718 | 28.35 | 967.3 | 27422.955 | 8706.6949 | 139.9583 | 0 | 0 | 0 | 0 | 15 | 660 | 0 | 1069 | 1086 | 1252 | 17 | 8706.6949 | 52.1667 | 1.259 | 1.255 | 28.8 | 27.88 | 22.44 | 27.8 | 986.2 | 50.08 | 0.937 | 96.25 | 86.52 | 12254 | 11901 | -353 | 2.514 | 13 | 13 | 24 | 7.2 | 2.1 | 4.2 | 1.8 | 1.3
| 2018-04-01 | 82 | 52% | 64 | 97 | 68 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3571 | 3504 | 3504 | 3431 | 3539 | 44 | 0 | 45 | 0 | 58 | 0 | 108 | -73 | 152 | 97.01% | 148.7917 | 96.08% | 100% | 100% | 9.59 | 136.05 | 1304.7195 | 29.715 | 967.69 | 28754.9084 | 8761.1856 | 146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1066 | 1080 | 1393 | 14 | 8761.1856 | 58.0417 | 2.024 | 2.053 | 28.9 | 27.78 | 22.28 | 27.8 | 987.9 | 50.01 | 0.9372 | 96.61 | 86.59 | 12249 | 11914 | -335 | 4.077 | 24 | 24 | 24 | 7.6 | 2.2 | 4.2 | 1.8 | 1.5
Week 14 | 2018-04-02 | 82.3 | 54.9% | 63 | 95 | 70 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3572 | 3489 | 3489 | 3413 | 3522 | 44 | 0 | 45 | 0 | 58 | 0 | 109 | -76 | 150 | 97.83% | 148.8333 | 95.55% | 100% | 100% | 9.365 | 133.26 | 1247.9799 | 29.6 | 969.32 | 28691.872 | 8772.2977 | 145.375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1061 | 1075 | 1386 | 14 | 8772.2977 | 57.75 | 2.021 | 2.021 | 29 | 27.68 | 22.22 | 27.46 | 988.8 | 50 | 0.9378 | 96.86 | 86.81 | 12255 | 11895 | -360 | 4.042 | 24 | 24 | 24 | 7.9 | 2.1 | 4.2 | 1.8 | 1.3
| 2018-04-03 | 83.9 | 58.4% | 68 | 97 | 75 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3558 | 3457 | 3457 | 3388 | 3500 | 44 | 0 | 44 | 0 | 58 | 0 | 112 | -69 | 148 | 98.54% | 148.25 | 95.22% | 100% | 100% | 9.405 | 135.35 | 1272.9667 | 29.326 | 968.69 | 28407.8029 | 8760.5578 | 144.0417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1052 | 1068 | 1380 | 16 | 8760.5578 | 57.5 | 2.021 | 2.021 | 28.93 | 27.39 | 22.02 | 27.37 | 988.17 | 50.1 | 0.9368 | 97.07 | 86.78 | 12241 | 11910 | -331 | 4.042 | 24 | 24 | 24 | 7.3 | 2.2 | 4.2 | 1.8 | 1.3
| 2018-04-04 | 84.4 | 54.5% | 67.6 | 96 | 75 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3554 | 3456 | 3456 | 3387 | 3497 | 44 | 0 | 44 | 0 | 58 | 0 | 110 | -69 | 148 | 98.45% | 148.0833 | 95.3% | 100% | 100% | 9.375 | 134.98 | 1265.4375 | 29.377 | 969.34 | 28476.3012 | 8781.1452 | 144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1050 | 1066 | 1381 | 16 | 8781.1452 | 57.5417 | 2.021 | 2.021 | 28.93 | 27.41 | 21.96 | 27.63 | 987.1 | 50.04 | 0.9375 | 97.05 | 86.57 | 12254 | 11892 | -362 | 4.042 | 24 | 24 | 24 | 8.38 | 2.2 | 4 | 1.6 | 1.8
| 2018-04-05 | 86.7 | 42.2% | 64.4 | 99 | 74 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3532 | 3483 | 3483 | 3417 | 3527 | 44 | 0 | 45 | 0 | 58 | 0 | 110 | -66 | 150 | 97.97% | 147.1667 | 96.74% | 100% | 100% | 9.44 | 137.13 | 1294.5072 | 29.359 | 973.25 | 28573.6468 | 8741.0459 | 145.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1060 | 1079 | 1388 | 19 | 8741.0459 | 57.8333 | 2 | 2 | 28.85 | 27.4 | 22 | 27.63 | 984.8 | 50.05 | 0.9372 | 96.52 | 86.33 | 12152 | 11786 | -366 | 4 | 24 | 24 | 24 | 6.37 | 2.2 | 4.2 | 1.8 | 1.5
| 2018-04-06 | 86.8 | 42.9% | 64.1 | 100 | 73 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3530 | 3471 | 3471 | 3406 | 3517 | 44 | 0 | 45 | 0 | 57 | 0 | 111 | -65 | 150 | 97.69% | 147.0833 | 96.49% | 100% | 100% | 9.475 | 135.85 | 1287.1787 | 29.141 | 976.3 | 28450.3583 | 8730.9269 | 144.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1058 | 1081 | 1378 | 23 | 8730.9269 | 57.4167 | 1.905 | 1.905 | 28.8 | 27.2 | 21.97 | 27.79 | 985.63 | 50.01 | 0.9376 | 96.33 | 86.45 | 12072 | 11745 | -327 | 3.81 | 24 | 24 | 24 | 8.17 | 2.1 | 4.2 | 1.7 | 1.5
| 2018-04-07 | 87.8 | 47.9% | 66.4 | 103 | 74 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3521 | 3435 | 3435 | 3360 | 3470 | 43 | 0 | 44 | 0 | 56 | 0 | 110 | -75 | 148 | 97.69% | 146.7083 | 95.43% | 100% | 100% | 9.47 | 135.41 | 1282.3327 | 28.782 | 977.3 | 28128.6486 | 8753.2682 | 143.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1050 | 1069 | 1351 | 19 | 8753.2682 | 56.2917 | 1.815 | 1.815 | 28.7 | 26.99 | 21.78 | 27.61 | 986.63 | 49.96 | 0.9376 | 96.5 | 86.6 | 12094 | 11791 | -303 | 3.63 | 24 | 24 | 24 | 9.2 | 2.1 | 3.9 | 1.8 | 1.6
| 2018-04-08 | 90.5 | 42.2% | 66.2 | 105 | 76 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3494 | 3118 | 3118 | 3047 | 3143 | 43 | 0 | 44 | 0 | 56 | 0 | 96 | -71 | 134 | 97.73% | 145.5833 | 87.21% | 100% | 90.21% | 9.52 | 137.45 | 1308.524 | 24.938 | 980.7 | 24456.6966 | 8455.9306 | 129.9167 | 0 | 0 | 0 | 0 | 14 | 1440 | 0 | 1048 | 1075 | 1020 | 27 | 8455.9306 | 42.5 | 0 | 0 | 28.6 | 26.9 | 21.65 | 27.87 | 985.04 | 50.09 | 0.9369 | 96.14 | 86.55 | 12050 | 11715 | -335 | 0 | 0 | 0 | 24 | 7.57 | 2.1 | 3.2 | 1.7 | 1.8
Week 15 | 2018-04-09 | 83.26 | 52.42% | 65.79 | 93 | 73 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 3563 | 3306 | 3306 | 3240 | 3341 | 44 | 0 | 45 | 0 | 56 | 0 | 101 | -66 | 147 | 94.7% | 148.4583 | 90.93% | 100% | 95.89% | 9.515 | 136.26 | 1296.5139 | 27.2841 | 979.7508 | 26731.66 | 8650.671 | 137.75 | 0 | 0 | 0 | 0 | 13 | 660 | 0 | 1058 | 1076 | 1207 | 18 | 8650.671 | 50.2917 | 1.021 | 1.017 | 29 | 27.2 | 21.93 | 27.78 | 989.7 | 50.05 | 0.9371 | 96.87 | 86.66 | 12084 | 11783 | -301 | 2.038 | 13 | 13 | 24 | 7.63 | 2.2 | 4.38 | 1.8 | 1.73
| 2018-04-10 | 85.5 | 52.4% | 67.1 | 95 | 74 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3548 | 3495 | 3495 | 3419 | 3529 | 44 | 0 | 45 | 0 | 58 | 0 | 110 | -76 | 150 | 98.03% | 147.8333 | 96.36% | 100% | 100% | 9.5 | 136.25 | 1294.375 | 29.3959 | 978.4229 | 28761.67 | 8790.8877 | 145.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1053 | 1075 | 1401 | 22 | 8790.8877 | 58.375 | 2.08 | 2.08 | 28.86 | 27.04 | 21.81 | 27.82 | 987.1 | 50.11 | 0.9371 | 96.76 | 86.64 | 12070 | 11737 | -333 | 4.16 | 24 | 24 | 24 | 8.23 | 2.1 | 4 | 1.8 | 1.7
| 2018-04-11 | 82.2 | 51.7% | 64.4 | 92 | 73 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3574 | 3497 | 3497 | 3422 | 3532 | 44 | 0 | 45 | 0 | 58 | 0 | 110 | -75 | 150 | 98.11% | 148.9167 | 95.75% | 100% | 100% | 9.56 | 138.41 | 1323.1996 | 29.2669 | 982.5813 | 28757.09 | 8790.2658 | 145.7083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1063 | 1087 | 1382 | 24 | 8790.2658 | 57.5833 | 1.949 | 1.949 | 28.83 | 27.1 | 21.87 | 27.83 | 987 | 50.12 | 0.9363 | 96.7 | 86.62 | 11978 | 11664 | -314 | 3.898 | 24 | 24 | 24 | 8.03 | 2.1 | 4 | 1.8 | 1.7
| 2018-04-12 | 82.7 | 48.7% | 63.5 | 95 | 70 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3566 | 3510 | 3510 | 3437 | 3546 | 44 | 0 | 45 | 0 | 58 | 0 | 109 | -73 | 150 | 98.5% | 148.5833 | 96.38% | 100% | 100% | 9.54 | 137.04 | 1307.3616 | 29.5247 | 977.6661 | 28865.25 | 8778.7639 | 146.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1067 | 1087 | 1392 | 20 | 8778.7639 | 58 | 1.958 | 1.962 | 28.8 | 27.37 | 22.03 | 27.64 | 989 | 50.12 | 0.9372 | 96.45 | 86.33 | 12039 | 11692 | -347 | 3.92 | 24 | 24 | 24 | 7 | 2.1 | 4 | 1.8 | 1.6
| 2018-04-13 | 85 | 36.2% | 60 | 98 | 70 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3545 | 3530 | 3530 | 3456 | 3569 | 45 | 0 | 45 | 0 | 58 | 0 | 113 | -74 | 153 | 97.19% | 147.7083 | 97.49% | 100% | 100% | 9.515 | 135.52 | 1289.4728 | 29.5026 | 979.1828 | 28888.391 | 8732.0208 | 147.0833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1080 | 1101 | 1388 | 21 | 8732.0208 | 57.8333 | 1.876 | 1.876 | 28.74 | 27.47 | 22.08 | 27.61 | 989.04 | 50.13 | 0.9377 | 95.88 | 86.05 | 11959 | 11598 | -361 | 3.752 | 24 | 24 | 24 | 7.6 | 2.1 | 4 | 1.8 | 1.5
| 2018-04-14 | 88 | 39% | 63 | 100 | 74 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3521 | 3497 | 3497 | 3419 | 3528 | 44 | 0 | 45 | 0 | 57 | 0 | 109 | -78 | 150 | 98% | 146.7083 | 97.1% | 100% | 100% | 9.535 | 136.81 | 1304.4833 | 29.4256 | 974.7584 | 28682.83 | 8770.7848 | 145.7083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1063 | 1083 | 1382 | 20 | 8770.7848 | 57.5833 | 1.92 | 1.92 | 28.68 | 27.37 | 21.98 | 27.44 | 987.9 | 50.05 | 0.9378 | 96.12 | 86.23 | 12102 | 11726 | -376 | 3.84 | 24 | 24 | 24 | 6.8 | 2.1 | 4.2 | 1.5 | 1.8
| 2018-04-15 | 88.2 | 39.5% | 64.1 | 102 | 75 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3515 | 3131 | 3131 | 3064 | 3160 | 44 | 0 | 45 | 0 | 57 | 0 | 96 | -67 | 135 | 97.53% | 146.4583 | 87.17% | 100% | 90.41% | 9.525 | 136.1 | 1296.3525 | 25.4158 | 972.3605 | 24713.359 | 8488.8092 | 130.4583 | 0 | 0 | 0 | 0 | 14 | 1440 | 0 | 1059 | 1076 | 1025 | 17 | 8488.8092 | 42.7083 | 0 | 0 | 28.6 | 27.31 | 21.92 | 27.2 | 985.9 | 50.03 | 0.9376 | 96.1 | 86.31 | 12084 | 11756 | -328 | 0 | 0 | 0 | 24 | 7.87 | 2.1 | 4 | 1.8 | 1.7
Week 16 | 2018-04-16 | 80.9 | 57.2% | 66 | 92 | 69 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 3588 | 3334 | 3334 | 3262 | 3367 | 44 | 0 | 45 | 0 | 57 | 0 | 105 | -72 | 151 | 92.91% | 149.5 | 90.91% | 100% | 95.61% | 9.52 | 135.75 | 1292.34 | 27.631 | 977.23 | 27001.8421 | 8673.8756 | 138.9167 | 0 | 0 | 0 | 0 | 14 | 660 | 0 | 1058 | 1079 | 1230 | 21 | 8673.8756 | 51.25 | 1.187 | 1.162 | 28.8 | 27.29 | 21.91 | 27.55 | 988.3 | 50.07 | 0.9373 | 96.84 | 86.49 | 12123 | 11752 | -371 | 2.349 | 13 | 13 | 24 | 7.1 | 2.1 | 4 | 1.8 | 1.4
| 2018-04-17 | 79.5 | 54.2% | 64 | 90 | 68 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3602 | 3523 | 3523 | 3444 | 3553 | 45 | 0 | 45 | 0 | 58 | 0 | 109 | -79 | 151 | 98.04% | 150.0833 | 95.61% | 100% | 100% | 9.505 | 135.14 | 1284.5057 | 29.66 | 976.09 | 28950.8294 | 8779.1333 | 146.7917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1069 | 1087 | 1397 | 18 | 8779.1333 | 58.2083 | 1.989 | 1.989 | 28.8 | 22.22 | 27.45 | 26.5 | 989.9 | 50.08 | 0.9373 | 96.75 | 86.37 | 12076 | 11702 | -374 | 3.978 | 24 | 24 | 24 | 10.5 | 2.2 | 4.2 | 1.8 | 1.5
| 2018-04-18 | 84.1 | 52.8% | 66.4 | 96 | 70 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3555 | 3489 | 3489 | 3410 | 3520 | 44 | 0 | 45 | 0 | 58 | 0 | 110 | -79 | 149 | 98.43% | 148.125 | 95.92% | 100% | 100% | 9.48 | 134.83 | 1278.1884 | 29.413 | 976 | 28707.088 | 8793.3362 | 145.375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1055 | 1075 | 1390 | 20 | 8793.3362 | 57.9167 | 2.021 | 2.021 | 28.8 | 27.25 | 21.88 | 27.42 | 989.8 | 50.04 | 0.9376 | 96.76 | 86.46 | 12132 | 11759 | -373 | 4.042 | 24 | 24 | 24 | 5.68 | 2.1 | 4 | 1.7 | 1.6
| 2018-04-19 | 85.4 | 40.6% | 62.7 | 96 | 75 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3543 | 3489 | 3489 | 3424 | 3533 | 44 | 0 | 45 | 0 | 58 | 0 | 109 | -65 | 149 | 98.8% | 147.625 | 96.64% | 100% | 100% | 9.485 | 135.83 | 1288.3475 | 29.375 | 977.46 | 28712.8875 | 8762.0429 | 145.375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1063 | 1080 | 1390 | 17 | 8762.0429 | 57.9167 | 1.973 | 1.973 | 28.8 | 27.29 | 21.97 | 27.04 | 986.25 | 50.02 | 0.9375 | 96.26 | 86.22 | 12052 | 12058 | 6 | 3.946 | 24 | 24 | 24 | 9.75 | 2.1 | 4 | 1.8 | 1.7
| 2018-04-20 | 75.1 | 57.3% | 60.1 | 87 | 64 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 22 | 21 | 3646 | 3539 | 3525 | 3463 | 3569 | 45 | 0 | 46 | 0 | 58 | 0 | 106 | -62 | 152 | 97.83% | 151.9167 | 94.98% | 100% | 99.35% | 9.49 | 136.83 | 1298.5167 | 29.45 | 979.79 | 28854.8155 | 8707.2862 | 147.4583 | 0 | 0 | 0 | 0 | 14 | 99 | 0 | 1084 | 1105 | 1380 | 21 | 8707.2862 | 57.5 | 1.859 | 1.855 | 28.8 | 27.57 | 22.27 | 27.51 | 984.38 | 50.08 | 0.9367 | 96.46 | 86.1 | 11954 | 11592 | -362 | 3.714 | 24 | 24 | 24 | 5.62 | 2.1 | 4.2 | 1.8 | 1.7
| 2018-04-21 | 74.9 | 52.69% | 59.36 | 87 | 62 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3634 | 3551 | 3551 | 3473 | 3581 | 45 | 0 | 46 | 0 | 58 | 0 | 108 | -78 | 152 | 98.16% | 151.4167 | 95.57% | 100% | 100% | 9.44 | 134.23 | 1267.1312 | 29.574 | 977.58 | 28910.9509 | 8689.3412 | 147.9583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1089 | 1111 | 1381 | 22 | 8689.3412 | 57.5417 | 1.813 | 1.813 | 28.83 | 27.76 | 22.41 | 27.39 | 991 | 50.08 | 0.9378 | 96.31 | 86.18 | 11978 | 11588 | -390 | 3.626 | 24 | 24 | 24 | 8 | 2.1 | 4 | 1.8 | 1.7
| 2018-04-22 | 82.9 | 37.9% | 59.6 | 96 | 69 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3563 | 3215 | 3215 | 3139 | 3232 | 45 | 0 | 46 | 0 | 58 | 0 | 93 | -76 | 137 | 98.3% | 148.4583 | 88.1% | 100% | 90.6% | 9.5 | 137.16 | 1303.02 | 25.698 | 979.37 | 25167.8503 | 8432.8991 | 133.9583 | 0 | 0 | 0 | 0 | 14 | 1440 | 0 | 1081 | 1107 | 1044 | 26 | 8432.8991 | 43.5 | 0 | 0 | 28.8 | 27.52 | 22.31 | 27.31 | 991.67 | 50.06 | 0.9372 | 96.03 | 86.07 | 11956 | 11590 | -366 | 0 | 0 | 0 | 24 | 7.3 | 2.1 | 4 | 1.8 | 1.65
Week 17 | 2018-04-23 | 86.8 | 36.2% | 60.4 | 101 | 72 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 3525 | 3340 | 3340 | 3268 | 3370 | 45 | 0 | 46 | 0 | 58 | 0 | 102 | -72 | 150 | 93.61% | 146.875 | 92.71% | 100% | 95.69% | 9.51 | 137.64 | 1308.9564 | 27.133 | 984.64 | 26716.2371 | 8575.6406 | 139.1667 | 0 | 0 | 0 | 0 | 14 | 660 | 0 | 1072 | 1099 | 1199 | 27 | 8575.6406 | 49.9583 | 0.886 | 0.886 | 27.71 | 27.14 | 21.97 | 27.42 | 988.63 | 50.08 | 0.937 | 95.36 | 86.07 | 11909 | 11545 | -364 | 1.772 | 13 | 13 | 24 | 6.9 | 2.1 | 4 | 1.8 | 1.65
| 2018-04-24 | 90.1 | 30.6% | 61 | 106 | 73 | 21 | 54 | 22 | 8 | 0 | 0 | 0 | 0 | 21 | 14 | 3492 | 3485 | 3485 | 3139 | 3240 | 44 | 105 | 45 | 79 | 58 | 128 | 102 | -346 | 152 | 88.82% | 145.5 | 89.89% | 92.63% | 91.81% | 8.761 | 136.99 | 1200.1694 | 26.8653 | 985.4 | 26473.0666 | 8815.9401 | 145.2083 | 20 | 21 | 16 | 33 | 21 | 38 | 1 | 973 | 1023 | 1244 | 50 | 8815.9401 | 51.8333 | 1.636 | 1.636 | 26.9 | 24.84 | 20.55 | 26.72 | 985.8 | 50.05 | 0.9376 | 94.86 | 85.99 | 11902 | 11531 | -371 | 3.272 | 21.58 | 21.43 | 20.92 | 5.55 | 2.2 | 3.8 | 1.8 | 1.6
| 2018-04-25 | 90 | 33% | 63 | 104 | 78 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3492 | 3484 | 3484 | 3420 | 3533 | 44 | 0 | 45 | 0 | 59 | 0 | 113 | -64 | 151 | 97.49% | 145.5 | 97.94% | 100% | 100% | 9.525 | 136.87 | 1303.6868 | 29.3631 | 984.8531 | 28918.3703 | 8836.8588 | 145.1667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1049 | 1074 | 1410 | 25 | 8836.8588 | 58.75 | 2.076 | 2.076 | 27 | 26.72 | 21.61 | 27.2 | 984.3 | 50.07 | 0.9376 | 95.19 | 86.06 | 11969 | 11638 | -331 | 4.152 | 24 | 24 | 24 | 7.6 | 2.2 | 4.1 | 1.8 | 1.7
| 2018-04-26 | 94 | 33% | 65 | 107 | 79 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3454 | 3455 | 3455 | 3385 | 3498 | 43 | 0 | 44 | 0 | 58 | 0 | 113 | -70 | 149 | 97.82% | 143.9167 | 98% | 100% | 100% | 9.49 | 137.84 | 1308.1016 | 29.1205 | 979.9285 | 28535.96 | 8816.5618 | 143.9583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1038 | 1064 | 1396 | 26 | 8816.5618 | 58.1667 | 2.076 | 2.076 | 27 | 26.61 | 21.57 | 27.26 | 987 | 50.06 | 0.9375 | 95.09 | 86.1 | 12041 | 11738 | -303 | 4.152 | 24 | 24 | 24 | 6.7 | 2.1 | 3.8 | 1.8 | 1.9
| 2018-04-27 | 95 | 32% | 64 | 107 | 79 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3449 | 3427 | 3427 | 3375 | 3483 | 43 | 0 | 44 | 0 | 58 | 0 | 108 | -52 | 148 | 98.06% | 143.7083 | 97.85% | 100% | 100% | 9.5 | 136.72 | 1298.84 | 29.1627 | 979.0312 | 28551.2338 | 8844.4663 | 142.7917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1039 | 1062 | 1382 | 23 | 8844.4663 | 57.5833 | 2.034 | 2.034 | 27 | 26.79 | 21.73 | 26.83 | 988 | 50.01 | 0.9376 | 94.92 | 86.17 | 12108 | 11803 | -305 | 4.068 | 24 | 24 | 24 | 7.23 | 2.1 | 3.7 | 1.9 | 1.9
| 2018-04-28 | 94 | 35% | 66 | 108 | 82 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3454 | 3411 | 3411 | 3348 | 3457 | 43 | 0 | 44 | 0 | 57 | 0 | 109 | -63 | 147 | 97.99% | 143.9167 | 96.93% | 100% | 100% | 9.488 | 136.85 | 1298.4328 | 28.9985 | 975.5201 | 28288.6 | 8837.226 | 142.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1032 | 1055 | 1370 | 23 | 8837.226 | 57.0833 | 2.002 | 2.002 | 27 | 26.72 | 21.61 | 27.22 | 989 | 49.98 | 0.9374 | 95.27 | 86.35 | 12166 | 11861 | -305 | 4.004 | 24 | 24 | 24 | 6.7 | 2 | 3.5 | 1.8 | 1.7
| 2018-04-29 | 95 | 40% | 69 | 108 | 81 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3446 | 3046 | 3046 | 2980 | 3074 | 43 | 0 | 44 | 0 | 57 | 0 | 94 | -66 | 132 | 97.03% | 143.5833 | 86.48% | 100% | 89.58% | 9.503 | 139.33 | 1324.053 | 24.8728 | 974.7917 | 24245.78 | 8580.4809 | 126.9167 | 0 | 0 | 0 | 0 | 15 | 1440 | 0 | 1024 | 1045 | 1005 | 21 | 8580.4809 | 41.875 | 0 | 0 | 27 | 26.56 | 21.44 | 27.15 | 987 | 50.09 | 0.9374 | 95.61 | 86.68 | 12182 | 11878 | -304 | 0 | 0 | 0 | 24 | 7 | 2.1 | 3.9 | 1.8 | 1.4
Week 18 | 2018-04-30 | 96.1 | 38% | 68.9 | 109 | 82 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 3432 | 3199 | 3199 | 3130 | 3233 | 42 | 0 | 43 | 0 | 57 | 0 | 103 | -69 | 145 | 92.9% | 143 | 91.2% | 100% | 94.28% | 9.481 | 140.94 | 1336.2521 | 26.7325 | 973.2573 | 26017.65 | 8739.2659 | 133.2917 | 0 | 0 | 0 | 0 | 15 | 780 | 0 | 1019 | 1043 | 1171 | 24 | 8739.2659 | 48.7917 | 0.958 | 0.958 | 27 | 26.56 | 21.52 | 27.06 | 982.83 | 50.01 | 0.9391 | 95.48 | 86.85 | 12242 | 11948 | -294 | 1.916 | 11 | 11 | 24 | 6.73 | 2.2 | 3.9 | 1.8 | 1.5
| 2018-05-01 | [26 empty] | 0 | 0 |  | no data | no data | no data | no data | no data |  |  | 0 |  |  | 0 | no data | no data | [10 empty] | 0 | no data | 0 | [13 empty] | 0 | 0
| 2018-05-02 | [26 empty] | 0 | 0 |  | no data | no data | no data | no data | no data |  |  | 0 |  |  | 0 | no data | no data | [10 empty] | 0 | no data | 0 | [13 empty] | 0 | 0
| 2018-05-03 | [26 empty] | 0 | 0 |  | no data | no data | no data | no data | no data |  |  | 0 |  |  | 0 | no data | no data | [10 empty] | 0 | no data | 0 | [13 empty] | 0 | 0
| 2018-05-04 | [26 empty] | 0 | 0 |  | no data | no data | no data | no data | no data |  |  | 0 |  |  | 0 | no data | no data | [10 empty] | 0 | no data | 0 | [13 empty] | 0 | 0
| 2018-05-05 | [26 empty] | 0 | 0 |  | no data | no data | no data | no data | no data |  |  | 0 |  |  | 0 | no data | no data | [10 empty] | 0 | no data | 0 | [13 empty] | 0 | 0
| 2018-05-06 | [26 empty] | 0 | 0
| Monthly | 86.102 | 44.85% | 64.235 | 98.7 | 73.2333 | 717 | 54 | 718 | 8 | 0 | 0 | 0 | 0 | 33 | 35 | 106039 | 102366 | 102352 | 100174.15 | 103163 | 43.9333 | 105 | 44.8 | 79 | 57.6 | 128 | 2989.85 | -2586 | 147.6667 | 97.04% | 147.2764 | 94.47% | 99.75% | 97.78% | 284.008 | 136.494 | 38765.9467 | 853.103 | 976.9418 | 833393.6463 | 8706.4337 | 142.175 | 20 | 21 | 16 | 33 | 148 | 8657 | 1 | 31633 | 32287 | 39243 | 654 | 8706.4337 | 54.5042 | 47.121 | 47.121 | 28.3487 | 26.9483 | 22.0567 | 27.402 | 987.4523 | 50.055 | 0.9374 | 96.1717 | 86.3893 | 12082.4333 | 11752.9 |  | 94.242 | 575.58 | 575.43 | 716.92 | 224.01
| Totals | Avg.F | % Avg. |  | M Avg | m Avg | hrs | min | hrs | min | hrs | min | hrs | min | hrs | min | MWhr Total | MWhr Total | MWhr Total | MWhr Total | MWhr Total | MW Avg | Total min | Avg MW | Total min | Avg MW | Total min | MWhr | Total MW | Av Max D/Gen | Av. DailyLF | Avg. | Avg. |  | Avg. | Total | Avg. |  | Total | Avg. |  | Avg. | [7 empty] | Total |  |  |  |  | Avg.
| Weeks data | Site Avg. Amb. Temp F | Site Avg. Relative humidity % |  | M Avg: Site Maximum/Minumum Temperature; hrs: CT-1 Base Load Hours; hrs: CT-2 Base Load Hours; hrs: CT-1 stand by hours / min; hrs: CT-2 standby hours / min; hrs: Plant ambient Corrected maximum Load hours/min | Average Corrected Plant Capacity | Ambient Corrected Declared Avail'y (MWH) | Av Plant WAPDA Dispatch | Net Plant Export (MWH) | Gross Generation | CT1 Av Cap (MW) | CT1 Unavail minutes | CT2 Av Cap (MW) | CT2 Unavail minutes | ST Unavail minutes | ST Average Cap (MW) | Plant Aux Load including Colony Load MWH | Differenece (+/-) MW | Maximum Daily Generation | Daily Load Factor | Avg. Corrected Plant | Plant Capacity Facto | Plant Availability Factor | Equivalent Plant Availability | LBtu gas flow mmscf | 1 LBtu gas (Average Btu/scf) | LBTU MMBTU | PL gas flow (mscf/week) | 1 PL gas (Average Btu/scf) | HBTU MMBTU | Plant Net Heat Rate (Btu/Kwh) | [11 empty] | 19
| Week 13 | 82.7386 | 50.03 | 64.3386 | 97.8571 | 68.4286 | 155 | 8 | 168 | 0 | 0 | 0 | 0 | 0 | 143 | 8 | 3567 | 3359.2857 | 3359.2857 | 23071 | 23817 | 44.1429 | 744 | 45.1429 | No outage | No outage | 58.2857 | no data | -444 | 152.1429 | 93.2% | 148.625 | 92.42% | 97.77% | 95.46% | 67.587 | 136.2229 | 9206.8942 | 200.421 | 962.8986 | 192985.0946 | 8769.1681
| Week 14 | 86.0571 | 49% | 65.6714 | 99.2857 | 73.8571 | 168 | -2 | 168 | 0 | 0 | 0 | 0 | 0 | 144 | 0 | 3537.2857 | 3415.5714 | 3415.5714 | 23418 | 24176 | 43.7143 | No outage | 44.4286 | No outage | No outage | 57.2857 | 758 | -491 | 146.8571 | 97.99% | 147.3869 | 94.56% | 100% | 98.6% | 66.05 | 135.6329 | 8958.5502 | 200.523 | 973.5571 | 195220.599 | 8713.596
| Week 15 | 84.98 | 45.7% | 63.9843 | 96.4286 | 72.7143 | 168 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 133 | 0 | 3547.4286 | 3423.7143 | 3423.7143 | 23457 | 24205 | 44.1429 | No outage | 45 | No outage | No outage | 57.4286 | 748 | -509 | 147.8571 | 97.44% | 147.8095 | 94.46% | 100% | 98.04% | 66.69 | 136.6271 | 9111.6642 | 174.3998 | 978.7271 | 170689.756 | 8714.6005
| Week 16 | 80.4 | 0.50384 | 62.5943 | 92 | 68.1429 | 168 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 131 | 21 | 3590.1429 | 3448.5714 | 3446.5714 | 23615 | 24355 | 44.5714 | No outage | 45.4286 | No outage | 405 | 57.8571 | 740 | -511 | 148.7143 | 97.5% | 149.5893 | 93.96% | 100% | 97.94% | 66.42 | 135.6814 | 9011.9605 | 200.801 | 977.6457 | 196312.2371 | 8691.1307
| Week 17 | 96.1 | 0.38 | 68.9 | 109 | 82 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 3432 | 3199 | 3199 | 3130 | 3233 | 42 | #REF! | 43 | #REF! | #REF! | 57 | 103 | -69 | 145 | 92.9% | 143 | 91.2% | 100% | 94.28% | 9.481 | 140.94 | 1336.2521 | 26.7325 | 973.2573 | 26017.65 | 8739.2659
| Date | Plant Status Whether Normal Operation or Tripping (State full detail for trippings/return to normal).
| 2018-04-01 | Normal operation. Plant remained at maximum load from 0000 to 2400 hrs.
| 2018-04-02 | Normal operation. Plant remained at maximum load from 0000 to 2400 hrs.
| 2018-04-03 | Normal operation. Plant remained at maximum load from 0000 to 2400 hrs.
| 2018-04-04 | Normal operation. Plant remained at maximum load from 0000 to 2400 hrs.
| 2018-04-05 | Normal operation. Plant remained at maximum load from 0000 to 2400 hrs.
| 2018-04-06 | Normal operation. Plant remained at maximum load from 0000 to 2400 hrs.
| 2018-04-07 | Normal operation. Plant remained at maximum load from 0000 to 2400 hrs.
| 2018-04-08 | Plant load remained 125 ~ 130 MW from 0000 hrs to 2400 hrs, as both duct burners kept off to remain within contractual heat rate.
| 2018-04-09 | Plant load increased from 128 to 140 MW by taking both duct burners into service at 1100 hrs to achieve maximum export.
| 2018-04-10 | Normal operation. Plant remained at maximum load from 0000 to 2400 hrs.
| 2018-04-11 | Normal operation. Plant remained at maximum load from 0000 to 2400 hrs.
| 2018-04-12 | Normal operation. Plant remained at maximum load from 0000 to 2400 hrs.
| 2018-04-13 | Normal operation. Plant remained at maximum load from 0000 to 2400 hrs.
| 2018-04-14 | Normal operation. Plant remained at maximum load from 0000 to 2400 hrs.
| 2018-04-15 | Plant load remained 125 ~ 131 MW from 0000 hrs to 2400 hrs, as both duct burners kept off to remain within contractual heat rate.
| 2018-04-16 | Plant load increased from 128 to 141 MW by taking both duct burners into service at 1100 hrs to achieve maximum export.
| 2018-04-17 | Normal operation. Plant remained at maximum load from 0000 to 2400 hrs.
| 2018-04-18 | Normal operation. Plant remained at maximum load from 0000 to 2400 hrs.
| 2018-04-19 | Normal operation. Plant remained at maximum load from 0000 to 2400 hrs.
| 2018-04-20 | Plant load remained 132 MW from 0812 hrs to 0911 hrs & from 1013 hrs to 1042 hrs at "NPCC Demand".
| 2018-04-21 | Normal operation. Plant remained at maximum load from 0000 to 2400 hrs.
| 2018-04-22 | Plant load restricted to 128~133 MW from 0000~2400 hrs, as both duct burners kept off to remain within contractual heat rate.
| 2018-04-23 | Plant load increased from 129 to 141 MW by taking both duct burners into service at 1100 hrs to achieve maximum export.
| 2018-04-24 | Complex tripped @ 1554 hrs due to "Wapda Supply Failure". After restoration of Wapda supply @ 1603 hrs, CT-2 synch @ 1713 hrs, CT-1 synch @ 1739 hrs & STG synch @ 1802 hrs.
| 2018-04-25 | Normal operation. Plant remained at maximum load from 0000 to 2400 hrs.
| 2018-04-26 | Normal operation. Plant remained at maximum load from 0000 to 2400 hrs.
| 2018-04-27 | Normal operation. Plant remained at maximum load from 0000 to 2400 hrs.
| 2018-04-28 | Normal operation. Plant remained at maximum load from 0000 to 2400 hrs.
| 2018-04-29 | Plant load restricted to 122~127 MW from 0000~2400 hrs, as both duct burners kept off to remain within contractual heat rate.
| 2018-04-30 | Plant load increased from 123 to 135 MW by taking both duct burners into service at 1300 hrs to achieve maximum export.

## May
2018-05-01
| Date | Site Avg. Ambient Temp.F | Site Avg. Relative Humidty % | Site Avg. Ambient Wetbulb Temp.F | Site Ambient Temp |  | Base load hours |  |  |  | Standby hours |  |  |  | Plant ambient corrected Max Load |  | Corrected Plant Capacity | Ambient Corrected Daclared Avail'y (MWH) | Plant WAPDA Dispatch (MWH) | Net Plant Export (MWH) | Gross Generation | CT1 Average Cap (MW) | CT1 Unavail minutes | CT2 Average Cap (MW) | CT2 Unavail minutes | ST Average Cap (MW) | ST Unavail minutes | Plant Aux Load including Colony Load MWH | Differenece (+/-) MW | Maximum Daily Generation | Daily Load Factor | Avg. Corrected Plant Capacity | Plant Capacity Factor | Plant Availability Factor | Equivalent Plant Availability | LBtu gas flow (mmscf/day) | 1 LBtu gas (Average Btu/scf) | LBTU MMBTU | 1 HBtu gas flow (mmscf/day) | 1 HBtu gas (Average Btu/scf) | HBTU MMBTU | HHV Net Heat Rate (Btu/Kwh) | Avg. declared availability | CT1 Derated MW | CT1 derated mintutes | CT-2 derated MW | CT-2 derated mintutes | ST derated MW | ST derated mintutes | WAPDA Backfeed (MWH) |  | CT-1 Gross Generation (MWH) | CT-2 Gross Generation (MWH) | STG Gross Generation (MWH) | CT-1 & CT-2 MWH difference | Base load Heat Rate | STG load | DB1 | DB2 | CT1 | CT1 Gas flow | CT2 Gas flow |  | Pamb | Freq. Hz | LBTU Gas Specific gravity | CT-1 compressor efficiency(%) | CT-2 compressor efficiency(%) | CT-1 Heat Rate (Btu/Kwh) | CT-2 Heat Rate (Btu/Kwh) |  | DB(1+2) | DB-1 Ops Hours | DB-2 Ops Hours | CT-1 Wetcomprssion Ops Hours | RO Operation Hours | CT1 T/G Brg |  | CT2 T/G Brg
[7 empty] | CT1 |  | CT2 |  | CT1 |  | CT2 | [44 empty] | mmscf/d | mmscf/d | WetC flow | HBTU KPPH | HBTU KPPH | LBTU KPPH | mbar | Hz | [6 empty] | mmscf/d |  |  |  |  | Supply air pressure | Seal air pressure | Supply air pressure | Seal air pressure
[5 empty] | Max | Min | hrs | min | hrs | min | hrs | min | hrs | min | hrs | min | [43 empty] | gpm | [16 empty] | Psi | "WC | Psi | "WC
Week 18 | 2018-04-30 | 96.1 | 38% | 68.9 | 109 | 82 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 3432 | 3199 | 3199 | 3130 | 3233 | 42 | 0 | 43 | 0 | 57 | 0 | 103 | -69 | 145 | 92.9% | 143 | 91.2% | 100% | 94.28% | 9.58 | 140.94 | 1350.2052 | 26.68 | 960.92 | 25637.3456 | 8622.2207 | 133.2917 | 0 | 0 | 0 | 0 | 15 | 780 | 0 |  | 1019 | 1043 | 1171 | 24 | 8622.2207 | 48.7917 | 0.958 | 0.958 | 27 | 26.56 | 21.52 | 27.06 | 982.83 | 50.01 | 0.9391 | 95.48 | 86.85 | 12242 | 11948 | -294 | 1.916 | 11 | 11 | 24 | 6.73 | 2.2 | 3.9 | 1.8 | 1.5
| 2018-05-01 | 95.3 | 37.2% | 68 | 109 | 82 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3441 | 3378 | 3378 | 3308 | 3416 | 42 | 0 | 43 | 0 | 56 | 0 | 108 | -70 | 147 | 96.83% | 143.375 | 96.13% | 100% | 100% | 9.485 | 142.37 | 1350.3794 | 28.647 | 975.91 | 27956.8938 | 8859.5143 | 140.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1022 | 1044 | 1350 | 22 | 8859.5143 | 56.25 | 1.907 | 1.907 | 27 | 26.51 | 21.39 | 27.14 | 983.92 | 49.96 | 0.94 | 95.3 | 85.65 | 12193 | 11883 | -310 | 3.814 | 24 | 24 | 24 | 6.95 | 2.1 | 3.8 | 1.8 | 1.7
| 2018-05-02 | 92.2 | 35.4% | 65.7 | 99 | 86 | 22 | 21 | 23 | 42 | 0 | 0 | 0 | 0 | 20 | 0 | 3350 | 3244 | 3244 | 3188 | 3290 | 43 | 62 | 44 | 0 | 56 | 0 | 102 | -56 | 146 | 93.89% | 139.5833 | 95.16% | 98.71% | 95.96% | 9.48 | 140.82 | 1334.9736 | 27.503 | 976.117 | 26846.1459 | 8839.7489 | 135.1667 | 18 | 37 | 10 | 18 | 20 | 240 | 0 | 80 | 974 | 1054 | 1262 | 80 | 8839.7489 | 52.5833 | 1.541 | 1.541 | 27 | 25.42 | 21.67 | 27 | 984.88 | 50 | 0.9394 | 95.05 | 86.51 | 12157 | 11868 | -289 | 3.082 | 20.1 | 20.1 | 21.38 | 6.5 | 2.2 | 3.9 | 1.8 | 1.8
| 2018-05-03 | 89.9 | 40.88% | 66 | 99 | 80 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 3500 | 3241 | 3241 | 3171 | 3275 | 43 | 0 | 44 | 0 | 56 | 0 | 104 | -70 | 144 | 94.76% | 145.8333 | 90.6% | 100% | 95.51% | 9.484 | 140.9 | 1336.2956 | 26.98 | 973.999 | 26278.493 | 8708.5426 | 135.0417 | 0 | 0 | 0 | 0 | 14 | 660 | 0 | 21 | 1039 | 1060 | 1176 | 21 | 8708.5426 | 49 | 0.958 | 0.962 | 27 | 27.03 | 21.84 | 26.83 | 984.58 | 50.03 | 0.9397 | 95.82 | 86.45 | 12228 | 11882 | -346 | 1.92 | 13 | 13 | 24 | 7.7 | 2.1 | 3.9 | 1.8 | 1.5
| 2018-05-04 | 89.97 | 44.5% | 67.79 | 101 | 78 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3494 | 3403 | 3403 | 3321 | 3428 | 43 | 0 | 44 | 0 | 56 | 0 | 107 | -82 | 147 | 97.17% | 145.5833 | 95.05% | 100% | 100% | 9.49 | 141.22 | 1340.1778 | 28.756 | 972.9796 | 27979 | 8828.4185 | 141.7917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 1033 | 1052 | 1343 | 19 | 8828.4185 | 55.9583 | 1.84 | 1.84 | 27 | 26.91 | 21.8 | 26.52 | 985.83 | 50.04 | 0.9396 | 96.13 | 86.57 | 12243 | 11914 | -329 | 3.68 | 24 | 24 | 24 | 8.3 | 2 | 3.73 | 1.8 | 1.71
| 2018-05-05 | 91.78 | 41.38% | 67.6 | 106 | 81 | 24 | 0 | 22 | 2 | 0 | 0 | 0 | 0 | 22 | 2 | 3481 | 3270 | 3270 | 3192 | 3296 | 43 | 0 | 44 | 99 | 56 | 0 | 104 | -78 | 145 | 94.71% | 145.0417 | 91.7% | 97.88% | 96.52% | 8.655 | 145.07 | 1255.5808 | 27.91 | 972.8771 | 27153 | 8899.9313 | 136.25 | 0 | 0 | 17 | 19 | 21 | 118 | 0 | -60 | 1031 | 971 | 1294 | -60 | 8899.9313 | 53.9167 | 1.874 | 1.638 | 27 | 26.96 | 20.39 | 24.58 | 985.13 | 50.05 | 0.9396 | 95.93 | 86.5 | 12272 | 11923 | -349 | 3.512 | 24 | 22.13 | 24 | 7.18 | 2.1 | 3.2 | 1.8 | 1.7
| 2018-05-06 | 87 | 46% | 66 | 95 | 78 | 24 | 0 | 8 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 3531 | 2332 | 2332 | 2284 | 2379 | 43 | 0 | 45 | 819 | 56 | 0 | 95 | -48 | 139 | 71.31% | 147.125 | 64.68% | 82.23% | 68.06% | 3.722 | 153.97 | 573.0763 | 20.971 | 971.0553 | 20364 | 9166.846 | 97.1667 | 0 | 0 | 22 | 92 | 19 | 1440 | 0 | -604 | 1043 | 439 | 897 | -604 | 9166.846 | 37.375 | 2.232 | 0 | 27 | 27.1 | 9.46 | 11.43 | 986.6 | 50.1 | 0.9349 | 95.95 | 86.8 | 12232 | 11785 | -447 | 2.232 | 21.2 | 0 | 24 | 12.4 | 2.1 | 3.9 | 1.9 | 1.6
Week 19 | 2018-05-07 | 84 | 48.2% | 65 | 92 | 77 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 3559 | 3285 | 3285 | 3208 | 3310 | 43 | 0 | 45 | 0 | 55 | 0 | 102 | -77 | 144 | 95.78% | 148.2917 | 90.14% | 100% | 95.51% | 9.499 | 143.23 | 1360.5418 | 27.25 | 973.46 | 26526.785 | 8693.057 | 136.875 | 0 | 0 | 0 | 0 | 14 | 660 | 0 | 31 | 1049 | 1080 | 1181 | 31 | 8693.057 | 49.2083 | 0.96 | 0.907 | 27 | 27.1 | 22.2 | 26.86 | 986.3 | 50.09 | 0.9383 | 95.99 | 86.49 | 12186 | 11788 | -398 | 1.867 | 13 | 13 | 24 | 6.8 | 2.1 | 3.8 | 1.8 | 1.3
| 2018-05-08 | 86.8 | 45.4% | 65.2 | 98 | 73 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3529 | 3420 | 3420 | 3341 | 3448 | 43 | 0 | 44 | 0 | 56 | 0 | 107 | -79 | 147 | 97.73% | 147.0417 | 94.67% | 100% | 100% | 9.474 | 142.62 | 1351.1819 | 28.737 | 974.7 | 28009.9539 | 8788.128 | 142.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 1043 | 1069 | 1336 | 26 | 8788.128 | 55.6667 | 1.714 | 1.714 | 27 | 27.04 | 22 | 26.89 | 985 | 50.04 | 0.9399 | 95.92 | 86.18 | 12182 | 11839 | -343 | 3.428 | 24 | 24 | 24 | 6.8 | 2.1 | 3.8 | 1.8 | 1.5
| 2018-05-09 | 86.4 | 45.5% | 65.7 | 97 | 74 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3529 | 3432 | 3432 | 3363 | 3472 | 43 | 0 | 44 | 0 | 57 | 0 | 109 | -69 | 148 | 97.75% | 147.0417 | 95.3% | 100% | 100% | 9.324 | 144.21 | 1344.614 | 29.161 | 975.7018 | 28452.4412 | 8860.2603 | 143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 1043 | 1063 | 1366 | 20 | 8860.2603 | 56.9167 | 1.92 | 1.92 | 27 | 27.03 | 22 | 26.96 | 987.2 | 50.06 | 0.9395 | 95.96 | 86.12 | 12184 | 11900 | -284 | 3.84 | 24 | 24 | 24 | 6.72 | 2.1 | 3.7 | 1.8 | 1.6
| 2018-05-10 | 92.5 | 40.7% | 67.2 | 107 | 79 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3474 | 3409 | 3409 | 3335 | 3447 | 43 | 0 | 44 | 0 | 57 | 0 | 112 | -74 | 152 | 94.49% | 144.75 | 96% | 100% | 100% | 9.316 | 144.7 | 1348.0252 | 28.975 | 974.8788 | 28247.1121 | 8874.1041 | 142.0417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 1034 | 1048 | 1365 | 14 | 8874.1041 | 56.875 | 1.941 | 1.941 | 27 | 26.92 | 21.84 | 26.87 | 990.79 | 50.07 | 0.9399 | 95.73 | 85.83 | 12236 | 11992 | -244 | 3.882 | 24 | 24 | 24 | 6.93 | 2.2 | 3.8 | 1.8 | 1.3
| 2018-05-11 | 96.27 | 37.36% | 68.14 | 110 | 83 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3427 | 3435 | 3435 | 3378 | 3488 | 43 | 0 | 44 | 0 | 59 | 0 | 110 | -57 | 153 | 94.99% | 142.7917 | 98.57% | 100% | 100% | 9.312 | 145.41 | 1354.0579 | 29.46 | 974.2064 | 28700.1213 | 8897.0335 | 143.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 1033 | 1044 | 1411 | 11 | 8897.0335 | 58.7917 | 2.198 | 2.196 | 27.3 | 26.93 | 21.77 | 27.19 | 989 | 50.09 | 0.9414 | 95.67 | 85.43 | 12253 | 12048 | -205 | 4.394 | 24 | 24 | 24 | 5.75 | 2.1 | 4.2 | 1.8 | 1.2
| 2018-05-12 | 96.3 | 37.2% | 68.2 | 108 | 83 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 17 | 92 | 3435 | 3381 | 3281 | 3232 | 3338 | 42 | 0 | 43 | 0 | 57 | 0 | 106 | -49 | 145 | 95.92% | 143.125 | 94.09% | 100% | 97.68% | 9.38 | 145.96 | 1369.1048 | 28.054 | 969.5555 | 27199.9106 | 8839.4231 | 140.875 | 0 | 0 | 0 | 0 | 13 | 365 | 0 | 11 | 1028 | 1039 | 1271 | 11 | 8839.4231 | 52.9583 | 1.406 | 1.377 | 27.5 | 27.06 | 21.91 | 27.16 | 988.4 | 50.1 | 0.9412 | 95.81 | 85.48 | 12387 | 12147 | -240 | 2.783 | 24 | 24 | 24 | 9.6 | 2.2 | 4.1 | 1.8 | 1.3
| 2018-05-13 | 88.6 | 44.3% | 67.1 | 96 | 80 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3515 | 3197 | 3050 | 3011 | 3107 | 43 | 0 | 43 | 0 | 57 | 0 | 96 | -39 | 131 | 98.82% | 146.4583 | 85.66% | 100% | 89.51% | 9.331 | 146.12 | 1363.4457 | 25.413 | 965.5772 | 24538.2135 | 8602.3445 | 133.2083 | 0 | 0 | 0 | 0 | 15 | 1440 | 0 | 16 | 1037 | 1053 | 1017 | 16 | 8602.3445 | 42.375 | 0 | 0 | 27.5 | 27.34 | 22.12 | 27.12 | 984.6 | 50.09 | 0.94 | 96.1 | 85.75 | 12379 | 12095 | -284 | 0 | 0 | 0 | 24 | 5.33 | 2.1 | 4.1 | 1.8 | 1.2
Week 20 | 2018-05-14 | 92.8 | 42.2% | 68.1 | 104 | 81 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 3473 | 3207 | 3207 | 3135 | 3239 | 43 | 0 | 43 | 0 | 54 | 0 | 104 | -72 | 142 | 95.04% | 144.7083 | 90.27% | 100% | 95.71% | 9.324 | 143.65 | 1339.3926 | 26.72 | 969.7902 | 25912.7948 | 8692.8827 | 133.625 | 0 | 0 | 0 | 0 | 12 | 720 | 0 | 16 | 1029 | 1045 | 1165 | 16 | 8692.8827 | 48.5417 | 0.903 | 0.876 | 27.3 | 26.96 | 21.83 | 27.43 | 982.71 | 50.06 | 0.9407 | 95.9 | 85.73 | 12317 | 12060 | -257 | 1.779 | 12 | 12 | 24 | 7.1 | 2.1 | 4.1 | 1.7 | 1.4
| 2018-05-15 | 89.27 | 44.98% | 67.46 | 101 | 83 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3508 | 3122 | 3122 | 3050 | 3148 | 43 | 0 | 44 | 0 | 57 | 0 | 98 | -72 | 133 | 98.62% | 146.1667 | 86.94% | 100% | 91.67% | 9.333 | 146.44 | 1366.7245 | 25.773 | 970.9803 | 25025.0748 | 8653.049 | 130.0833 | 0 | 0 | 0 | 0 | 12 | 1440 | 0 | 15 | 1033 | 1048 | 1067 | 15 | 8653.049 | 44.4583 | 0.354 | 0.303 | 27.01 | 27.03 | 21.76 | 27.54 | 983.1 | 50.18 | 0.94 | 95.74 | 85.57 | 12293 | 12008 | -285 | 0.657 | 24 | 24 | 24 | 6.7 | 2.1 | 4.1 | 1.8 | 1.4
| 2018-05-16 | 87.66 | 48.34% | 67.23 | 101 | 76 | 9 | 30 | 9 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 3515 | 2106 | 2028 | 1295 | 1339 | 43 | 870 | 44 | 715 | 57 | 870 | 53 | -733 | 133 | 41.95% | 146.4583 | 36.84% | 42.87% | 38.68% | 5.004 | 140.3 | 702.0612 | 12.1707 | 972.8019 | 11839.68 | 9684.7422 | 87.75 | 0 | 0 | 12 | 155 | 12 | 570 | 9 | 88 | 413 | 501 | 425 | 88 | 9684.7422 | 17.7083 | 0.118 | 0.118 | 27 | 10.88 | 10.81 | 13.14 | 983.04 | 50.12 | 0.9402 | 96.19 | 85.66 | 12204 | 11959 | -245 | 0.236 | 8.3 | 8.3 | 9.5 | 6.57 | 2.1 | 4.2 | 1.8 | 1.2
| 2018-05-17 | 87.9 | 46.8% | 66.9 | 99 | 82 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3520 | 212 | 212 | 213 | 235 | 43 | 1026 | 44 | 1422 | 57 | 1387 | 39 | 1 | 57 | 17.18% | 146.6667 | 6.051% | 10.42% | 6.812% | 0 | 0 | 0 | 3.2584 | 980.793 | 3195.817 | 15003.8357 | 8.8333 | 13 | 366 | 34 | 18 | 40 | 53 | 17 | -212 | 216 | 4 | 15 | -212 | 15003.8357 | 0.625 | 0 | 0 | 0 | 6.43 | 0.39 | 0 | 983.25 | 50.1 | 0 | 85.74 | 0 | 13641 | 0 | -13641 | 0 | 0 | 0 | 0 | 4.42 | 2 | 4.2 | 0 | 0
| 2018-05-18 | 91.2 | 40.9% | 66.8 | 104 | 80 | 24 | 0 | 23 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 3483 | 3123 | 3061 | 3007 | 3106 | 43 | 0 | 45 | 0 | 57 | 0 | 99 | -54 | 132 | 98.04% | 145.125 | 86.33% | 100% | 89.43% | 9.584 | 147.14 | 1410.1898 | 25.0635 | 978.5398 | 24525.68 | 8625.1645 | 130.125 | 0 | 0 | 14 | 33 | 15 | 1440 | 0 | 47 | 1031 | 1078 | 997 | 47 | 8625.1645 | 41.5417 | 0 | 0 | 27 | 26.76 | 22.1 | 28.2 | 982.2 | 50.11 | 0.9395 | 95.1 | 86.65 | 12203 | 11874 | -329 | 0 | 0 | 0 | 23.5 | 6.7 | 2.2 | 4.3 | 1.9 | -0.5
| 2018-05-19 | 88 | 40% | 64 | 99 | 79 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3524 | 3138 | 3138 | 3069 | 3163 | 44 | 0 | 45 | 0 | 57 | 0 | 94 | -69 | 134 | 98.35% | 146.8333 | 87.09% | 100% | 90.41% | 9.461 | 144.84 | 1370.3312 | 25.3585 | 973.0477 | 24675.03 | 8486.5954 | 130.75 | 0 | 0 | 0 | 0 | 14 | 1440 | 0 | 46 | 1047 | 1093 | 1023 | 46 | 8486.5954 | 42.625 | 0 | 0 | 27 | 27.09 | 22.15 | 27.63 | 983.8 | 50.11 | 0.9395 | 95.8 | 86.56 | 12169 | 11670 | -499 | 0 | 0 | 0 | 24 | 7 | 2 | 4.1 | 2.1 | 0
| 2018-05-20 | 91.4 | 37% | 65 | 103 | 78 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3485 | 3116 | 3116 | 3046 | 3143 | 43 | 0 | 45 | 0 | 57 | 0 | 97 | -70 | 133 | 98.46% | 145.2083 | 87.4% | 100% | 89.66% | 9.404 | 147.9 | 1390.8516 | 25.213 | 975.8874 | 24605.06 | 8534.4424 | 129.8333 | 0 | 0 | 0 | 0 | 15 | 1440 | 0 | 46 | 1039 | 1085 | 1019 | 46 | 8534.4424 | 42.4583 | 0 | 0 | 27 | 26.9 | 22 | 26.94 | 984.1 | 50.06 | 0.9403 | 95.45 | 86.58 | 12157 | 11652 | -505 | 0 | 0 | 0 | 24 | 6.5 | 2.1 | 4.1 | 2.1 | 0
Week 21 | 2018-05-21 | 92.9 | 34.19% | 65.1 | 104 | 82 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3470 | 3113 | 3113 | 3043 | 3140 | 43 | 0 | 45 | 0 | 57 | 0 | 97 | -70 | 133 | 98.37% | 144.5833 | 87.69% | 100% | 89.66% | 9.388 | 150.78 | 1415.5226 | 25.1732 | 975.0207 | 24544.4 | 8531.0295 | 129.7083 | 0 | 0 | 0 | 0 | 15 | 1440 | 0 | 46 | 1038 | 1084 | 1018 | 46 | 8531.0295 | 42.4167 | 0 | 0 | 27 | 26.84 | 21.94 | 26.87 | 983.67 | 50.1 | 0.9399 | 95.23 | 86.56 | 12157 | 11637 | -520 | 0 | 0 | 0 | 23.83 | 6.9 | 2.1 | 4.1 | 2 | 0
| 2018-05-22 | 92.8 | 31.9% | 64.1 | 104 | 82 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3470 | 3115 | 3115 | 3045 | 3145 | 43 | 0 | 45 | 0 | 57 | 0 | 100 | -70 | 133 | 98.53% | 144.5833 | 87.75% | 100% | 89.66% | 9.362 | 148.86 | 1393.6273 | 25.1889 | 977.9355 | 24633.1 | 8547.3653 | 129.7917 | 0 | 0 | 0 | 0 | 15 | 1440 | 0 | 46 | 1040 | 1086 | 1019 | 46 | 8547.3653 | 42.4583 | 0 | 0 | 27 | 26.83 | 21.9 | 26.84 | 984.5 | 50.13 | 0.9401 | 95.09 | 86.51 | 12107 | 11608 | -499 | 0 | 0 | 0 | 24 | 6.42 | 2.1 | 4.2 | 2 | 0
| 2018-05-23 | 92.9 | 33.6% | 63.9 | 106 | 78 | 19 | 29 | 20 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 3463 | 3119 | 3119 | 2543 | 2629 | 43 | 251 | 45 | 170 | 57 | 232 | 89 | -576 | 133 | 82.36% | 144.2917 | 73.43% | 84.83% | 75.59% | 7.832 | 147.68 | 1156.6298 | 21.3846 | 973.85 | 20825.3528 | 8644.1143 | 129.9583 | 19 | 20 | 15 | 54 | 15 | 1208 | 3 | 92 | 850 | 942 | 837 | 92 | 8644.1143 | 34.875 | 0 | 0 | 27 | 22.19 | 19.41 | 23.49 | 983 | 50.09 | 0.9407 | 95.01 | 86.5 | 12178 | 11649 | -529 | 0 | 0 | 0 | 18.61 | 7 | 2.1 | 4.1 | 2 | 0
| 2018-05-24 | 94.9 | 31.7% | 64.04 | 107 | 81 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3449 | 3113 | 3113 | 3040 | 3141 | 43 | 0 | 45 | 0 | 57 | 0 | 101 | -73 | 133 | 98.4% | 143.7083 | 88.14% | 100% | 89.66% | 9.322 | 154.03 | 1435.8677 | 25.0779 | 978.2434 | 24532.26 | 8542.1473 | 129.7083 | 0 | 0 | 0 | 0 | 15 | 1440 | 0 | 47 | 1037 | 1084 | 1020 | 47 | 8542.1473 | 42.5 | 0 | 0 | 27 | 26.83 | 21.92 | 27.54 | 981.21 | 50.08 | 0.9397 | 95.29 | 86.51 | 12158 | 11681 | -477 | 0 | 0 | 0 | 24 | 6.22 | 2.2 | 4.2 | 2.1 | 0
| 2018-05-25 | 95.6 | 30.7% | 64.1 | 110 | 78 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3439 | 3104 | 3104 | 3032 | 3130 | 43 | 0 | 45 | 0 | 57 | 0 | 98 | -72 | 133 | 98.06% | 143.2917 | 88.17% | 100% | 89.66% | 9.313 | 151.5 | 1410.9195 | 25.1778 | 972.1839 | 24477.48 | 8538.3903 | 129.3333 | 0 | 0 | 0 | 0 | 15 | 1440 | 0 | 44 | 1034 | 1078 | 1018 | 44 | 8538.3903 | 42.4167 | 0 | 0 | 27 | 26.91 | 22.04 | 26.7 | 980.58 | 50.08 | 0.9409 | 94.94 | 86.54 | 12233 | 11724 | -509 | 0 | 0 | 0 | 24 | 9 | 2.1 | 4.1 | 2 | 0
| 2018-05-26 | 95.1 | 34.5% | 65.4 | 107 | 82 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3449 | 3092 | 3092 | 3023 | 3121 | 43 | 0 | 45 | 0 | 57 | 0 | 98 | -69 | 133 | 97.78% | 143.7083 | 87.65% | 100% | 89.66% | 9.375 | 151.68 | 1422 | 25.0697 | 975.6978 | 24460.47 | 8561.8492 | 128.8333 | 0 | 0 | 0 | 0 | 15 | 1440 | 0 | 50 | 1027 | 1077 | 1017 | 50 | 8561.8492 | 42.375 | 0 | 0 | 27 | 26.74 | 21.95 | 26.24 | 978.29 | 50.06 | 0.9396 | 95.32 | 86.49 | 12225 | 11681 | -544 | 0 | 0 | 0 | 24 | 6.88 | 2.1 | 4.2 | 2.1 | 0
| 2018-05-27 | 96.4 | 30.47% | 65.08 | 111 | 82 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3427 | 3089 | 3089 | 3020 | 3115 | 43 | 0 | 45 | 0 | 57 | 0 | 95 | -69 | 133 | 97.59% | 142.7917 | 88.12% | 100% | 89.66% | 9.327 | 150.86 | 1407.0712 | 25.113 | 971.0907 | 24386.99 | 8541.0799 | 128.7083 | 0 | 0 | 0 | 0 | 15 | 1440 | 0 | 42 | 1029 | 1071 | 1015 | 42 | 8541.0799 | 42.2917 | 0 | 0 | 27 | 26.88 | 21.96 | 26.42 | 978.9 | 50.07 | 0.9402 | 95.12 | 86.59 | 12277 | 11740 | -537 | 0 | 0 | 0 | 24 | 7.05 | 2.1 | 4.2 | 2 | 0
Week 22 | 2018-05-28 | 97.22 | 34.15% | 66.68 | 108 | 84 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3422 | 3068 | 3068 | 2995 | 3100 | 43 | 0 | 45 | 0 | 57 | 0 | 105 | -73 | 131 | 98.6% | 142.5833 | 87.52% | 100% | 89.66% | 9.323 | 151.62 | 1413.5533 | 24.9637 | 974.1372 | 24318.03 | 8591.5136 | 127.8333 | 0 | 0 | 0 | 0 | 15 | 1440 | 0 | 51 | 1019 | 1070 | 1011 | 51 | 8591.5136 | 42.125 | 0 | 0 | 27 | 26.66 | 21.85 | 26.14 | 977.2 | 50.08 | 0.9407 | 95.09 | 86.57 | 12287 | 11717 | -570 | 0 | 0 | 0 | 24 | 7.2 | 2.1 | 4.1 | 2.1 | 0
| 2018-05-29 | 96.22 | 34.8% | 66.34 | 108 | 85 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3432 | 3066 | 3066 | 2997 | 3095 | 43 | 0 | 45 | 0 | 57 | 0 | 98 | -69 | 132 | 97.7% | 143 | 87.33% | 100% | 89.66% | 9.32 | 151.25 | 1409.65 | 24.8697 | 973.037 | 24199.12 | 8544.8015 | 127.75 | 0 | 0 | 0 | 0 | 15 | 1440 | 0 | 48 | 1019 | 1067 | 1009 | 48 | 8544.8015 | 42.0417 | 0 | 0 | 27 | 26.58 | 21.79 | 26.2 | 972.75 | 50.05 | 0.9408 | 95.3 | 86.62 | 12259 | 11718 | -541 | 0 | 0 | 0 | 24 | 5.7 | 2.1 | 4.1 | 2.1 | 0
| 2018-05-30 | 97 | 37.4% | 70 | 109 | 85 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3425 | 3029 | 3029 | 2953 | 3050 | 42 | 0 | 44 | 0 | 57 | 0 | 97 | -76 | 130 | 97.76% | 142.7083 | 86.22% | 100% | 89.51% | 9.345 | 149.97 | 1401.4697 | 24.5979 | 978.7856 | 24076.03 | 8627.6667 | 126.2083 | 0 | 0 | 0 | 0 | 15 | 1440 | 0 | 42 | 1005 | 1047 | 998 | 42 | 8627.6667 | 41.5833 | 0 | 0 | 27 | 26.3 | 21.45 | 26.3 | 975.5 | 50.05 | 0.9404 | 95.3 | 86.87 | 12288 | 11768 | -520 | 0 | 0 | 0 | 23.8 | 7.2 | 2.2 | 4.2 | 2 | 0
| 2018-05-31 | 98 | 39% | 71 | 109 | 85 | 15 | 56 | 17 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 3413 | 3019 | 3019 | 2086 | 2163 | 42 | 465 | 44 | 307 | 57 | 417 | 85 | -933 | 129 | 69.86% | 142.2083 | 61.12% | 72.41% | 61.65% | 7.04 | 154.71 | 1089.1584 | 17.7679 | 980.3736 | 17419.1801 | 8872.6455 | 125.7917 | 22 | 19 | 16 | 80 | 20 | 1023 | 8 | 137 | 672 | 809 | 682 | 137 | 8872.6455 | 28.4167 | 0 | 0 | 27 | 17.8 | 16.88 | 20.25 | 976.9 | 50.05 | 0.9387 | 96.15 | 86.9 | 12251 | 11700 | -551 | 0 | 0 | 0 | 14.8 | 13.1 | 2.1 | 4.2 | 2.1 | 0
| 2018-06-01 | [26 empty] | 0 | 0 |  | no data | no data | no data | no data | no data |  |  | 0 |  |  | 0 | no data | no data | [11 empty] | 0 | no data | 0 | [13 empty] | 0
| 2018-06-02 | [26 empty] | 0 | 0 |  | no data | no data | no data | no data | no data |  |  | 0 |  |  | 0 | no data | no data | [11 empty] | 0 | no data | 0 | [13 empty] | 0
| 2018-06-03 | [26 empty] | 0 | 0 |  | no data | no data | no data | no data | no data |  |  | 0 |  |  | 0 | no data | no data | [11 empty] | 0 | no data | 0 | [13 empty] | 0
| Monthly | 92.0739 | 0.39247 | 66.4148 | 103.5806 | 80.5484 | 692 | 4 | 676 | 33 | 0 | 0 | 0 | 0 | 1 | 34 | 107632 | 94378 | 93991 | 90125.04 | 92896 | 42.9032 | 2674 | 44.3226 | 3532 | 56.6774 | 2906 | 2807.96 | -4067 | 135.6452 | 90.54% | 144.6667 | 83.73% | 93.21% | 86.62% | 267.009 | 142.2519 | 39216.4753 | 765.7583 | 974.2972 | 745903.6196 | 8711.4535 | 126.8522 | 72 | 442 | 140 | 469 | 406 | 27217 | 37 |  | 29987 | 30285 | 32624 | 298 | 8711.4535 | 43.8495 | 21.866 | 19.24 | 26.181 | 25.2245 | 20.1458 | 24.7232 | 983.1268 | 50.0742 | 0.90953 | 95.2619 | 83.5216 | 12275.3548 | 11448.7097 |  | 41.106 | 303.6 | 280.53 | 687.42 | 224.62
| Totals | Avg.F | % Avg. |  | M Avg | m Avg | hrs | min | hrs | min | hrs | min | hrs | min | hrs | min | MWhr Total | MWhr Total | MWhr Total | MWhr Total | MWhr Total | MW Avg | Total min | Avg MW | Total min | Avg MW | Total min | MWhr | Total MW | Av Max D/Gen | Av. DailyLF | Avg. | Avg. |  | Avg. | Total | Avg. |  | Total | Avg. |  | Avg. | [7 empty] | Total | [5 empty] | Avg.
| Weeks data | Site Avg. Amb. Temp F | Site Avg. Relative humidity % |  | M Avg: Site Maximum/Minumum Temperature; hrs: CT-1 Base Load Hours; hrs: CT-2 Base Load Hours; hrs: CT-1 stand by hours / min; hrs: CT-2 standby hours / min; hrs: Plant ambient Corrected maximum Load hours/min | Average Corrected Plant Capacity | Ambient Corrected Declared Avail'y (MWH) | Av Plant WAPDA Dispatch | Net Plant Export (MWH) | Gross Generation | CT1 Av Cap (MW) | CT1 Unavail minutes | CT2 Av Cap (MW) | CT2 Unavail minutes | ST Unavail minutes | ST Average Cap (MW) | Plant Aux Load including Colony Load MWH | Differenece (+/-) MW | Maximum Daily Generation | Daily Load Factor | Avg. Corrected Plant | Plant Capacity Facto | Plant Availability Factor | Equivalent Plant Availability | LBtu gas flow mmscf | 1 LBtu gas (Average Btu/scf) | LBTU MMBTU | PL gas flow (mscf/week) | 1 PL gas (Average Btu/scf) | HBTU MMBTU | Plant Net Heat Rate (Btu/Kwh) | [12 empty] | 57.25
| Week 13 | 91.75 | 40.48 | 67.1414 | 102.5714 | 81 | 166 | 21 | 150 | 33 | 0 | 0 | 0 | 0 | 114 | 2 | 3461.2857 | 3152.4286 | 3152.4286 | 21594 | 22317 | 42.7143 | 62 | 43.8571 | 918 | No outage | 56.1429 | no data | -473 | 144.7143 | 91.65% | 144.2202 | 89.22% | 96.97% | 92.9% | 59.896 | 143.6129 | 8601.8357 | 187.447 | 971.9797 | 182194.6795 | 8846.4603
| Week 14 | 90.1243 | 42.67% | 66.6486 | 101.1429 | 78.4286 | 168 | -2 | 168 | 0 | 0 | 0 | 0 | 0 | 127 | -58 | 3495.4286 | 3365.5714 | 3330.2857 | 22868 | 23610 | 42.8571 | No outage | 43.8571 | No outage | No outage | 56.8571 | 742 | -444 | 145.7143 | 96.5% | 145.6429 | 93.49% | 100% | 97.53% | 65.636 | 144.6071 | 9491.4344 | 197.05 | 972.5828 | 191647.4448 | 8793.4786
| Week 15 | 89.7471 | 42.89% | 66.4986 | 101.5714 | 79.8571 | 130 | 78 | 128 | 57 | 0 | 0 | 0 | 0 | 12 | 0 | 3501.1429 | 2574.8571 | 2554.8571 | 16815 | 17373 | 43.1429 | 1896 | 44.2857 | 2137 | 2257 | 56.5714 | 584 | -1069 | 123.4286 | 78.24% | 145.881 | 68.7% | 79.04% | 71.77% | 52.11 | 124.3243 | 6478.5385 | 118.3442 | 974.3255 | 115305.7217 | 9668.6731
| Week 16 | 94.3714 | 0.32437 | 64.5314 | 107 | 80.7143 | 163 | 29 | 164 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 3452.4286 | 3106.4286 | 3106.4286 | 20746 | 21421 | 43 | 251 | 45 | 170 | 399 | 57 | 678 | -999 | 133 | 95.87% | 143.8512 | 85.85% | 97.83% | 87.65% | 63.919 | 150.77 | 9637.0676 | 172.1851 | 974.8603 | 167856.3716 | 8557.9965
| Week 17 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Date | Plant Status Whether Normal Operation or Tripping (State full detail for trippings/return to normal).
| 2018-05-01 | Normal operation. Plant remained at maximum load from 0000 to 2400 hrs.
| 2018-05-02 | CT-1 de-synch @ 2022 hrs & synch @ 2124 hrs due to suspension of HBTU gas by M/S SNGPL.
| 2018-05-03 | Plant load increased from 126 to 138 MW by taking both duct burners into service at 1100 hrs to achieve maximum export.
| 2018-05-04 | Normal operation. Plant remained at maximum load from 0000 to 2400 hrs.
| 2018-05-05 | Normal operation. Gas turbine CT-2 de-synch @2221hrs for balancing purpose and compressor offline washing.
| 2018-05-06 | Gas turbine CT-2 synch @ 1248 hrs after offline washing and balancing. Gas turbine CT-2 de-synch @ 1951 hrs and again synch @ 2042 hrs.
| 2018-05-07 | Plant load increased from 126 to 138 MW by taking both duct burners into service at 1100 hrs to achieve maximum export.
| 2018-05-08 | Normal operation. Plant remained at maximum load from 0000 to 2400 hrs.
| 2018-05-09 | Normal operation. Plant remained at maximum load from 0000 to 2400 hrs.
| 2018-05-10 | Normal operation. Plant remained at maximum load from 0000 to 2400 hrs.
| 2018-05-11 | Normal operation. “Annual Dependable Capacity (ADC) Test” for the year 2018 carried out successfully.
| 2018-05-12 | Plant load remained 125~128 MW from 1755 hrs to 2400 hrs at "NPCC Demand".
| 2018-05-13 | Plant load remained 125 MW from 00:00 hrs to 08:00 hrs at NPCC demand & 124~126 MW from 08:00 hrs to 24:00 hrs to remain within contractual heat rate.
| 2018-05-14 | Plant load increased from 125 to 137 MW by taking both duct burners into service at 1100 hrs to achieve maximum export. Load reduced from 137 to 127 MW at 2300 hrs by reducing DB firing to remain within contractual heat rate.
| 2018-05-15 | Plant load restricted to 124~129 MW from 0000~2400 hrs, as both duct burners kept at minimum firing to remain within contractual heat rate.
| 2018-05-16 | Plant tripped at 0930hrs due to WAPDA supply failure (WAPDA system blackout). WAPDA supply restored at 1226 hrs, however after heavy jerks in 132KV system voltages supply again failed at 1354hrs during plant startup. After restoration of WAPDA supply CT-2 synch @1527 hrs but ST filed to start due to high vibration at bearing#2. It was decided to shutdown CT2 which desynch at @1802 hrs till rectification of fault at ST.
| 2018-05-17 | After rectification of fault at Steam turbine unit plant started successfully. CT-1 synch at 1706 hrs, STG at 2307 hrs & CT-2 at 2342 hrs.
| 2018-05-18 | Plant load remained 125MW upto 0342hrs at "NPCC Demand" & load remained restricted 125~128MW from 0342~2400hrs to remain within contractual heatrate.
| 2018-05-19 | Plant load restricted 126~130 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-05-20 | Plant load restricted 125~129 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-05-21 | Plant load restricted 125~129 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-05-22 | Plant load restricted 125~129 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate
| 2018-05-23 | Plant tripped @ 1712 hrs due to WAPDA supply failure. After restoration of Wapda supply at 1743hrs, plant started & Gas turbine (CT-2) synch @ 1824 hrs. Plant again tripped at 1839hrs due to WAPDA supply failure. Wapda supply restored at 1843 hrs but remained below our technical limits (110~115KV). WAPDA supply stabilized at 1942 hrs, Gas turbine (CT-2) synch @ 2017 hrs, Steam turbine (STG) synch @ 2105 hrs & Gas turbine (CT-1) synch @ 2123 hrs.
| 2018-05-24 | Plant load restricted 125~129 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-05-25 | Plant load restricted 124~129 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-05-26 | Plant load restricted 123~128 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-05-27 | Plant load restricted 124~129 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-05-28 | Plant load restricted 122~127 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-05-29 | Plant load restricted 122~128 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-05-30 | Plant load restricted 120~126 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-05-31 | FKPCL plant tripped @ 1015 hrs due to WAPDA supply failure. After normalization of system voltages at 1119 hrs, CT-2 synch @ 1206 hrs & STG synch @ 1244 hrs. FKPCL plant again tripped @ 1301 hrs due to WAPDA supply failure. After normalization of system voltages at 1547 hrs, CT-2 synch @ 1617 hrs, STG synch @ 1729 hrs & CT-1 synch @ 1800 hrs.

## June
2018-06-01
| Date | Site Avg. Ambient Temp.F | Site Avg. Relative Humidty % | Site Avg. Ambient Wetbulb Temp.F | Site Ambient Temp |  | Base load hours |  |  |  | Standby hours |  |  |  | Plant ambient corrected Max Load |  | Corrected Plant Capacity | Ambient Corrected Daclared Avail'y (MWH) | Plant WAPDA Dispatch (MWH) | Net Plant Export (MWH) | Gross Generation | CT1 Average Cap (MW) | CT1 Unavail minutes | CT2 Average Cap (MW) | CT2 Unavail minutes | ST Average Cap (MW) | ST Unavail minutes | Plant Aux Load including Colony Load MWH | Differenece (+/-) MW | Maximum Daily Generation | Daily Load Factor | Avg. Corrected Plant Capacity | Plant Capacity Factor | Plant Availability Factor | Equivalent Plant Availability | LBtu gas flow (mmscf/day) | 1 LBtu gas (Average Btu/scf) | LBTU MMBTU | 1 HBtu gas flow (mmscf/day) | 1 HBtu gas (Average Btu/scf) | HBTU MMBTU | HHV Net Heat Rate (Btu/Kwh) | Avg. declared availability | CT1 Derated MW | CT1 derated mintutes | CT-2 derated MW | CT-2 derated mintutes | ST derated MW | ST derated mintutes | WAPDA Backfeed (MWH) | CT-1 Gross Generation (MWH) | CT-2 Gross Generation (MWH) | STG Gross Generation (MWH) | CT-1 & CT-2 MWH difference | Base load Heat Rate | STG load | DB1 | DB2 | CT1 | CT1 Gas flow | CT2 Gas flow |  | Pamb | Freq. Hz | LBTU Gas Specific gravity | CT-1 compressor efficiency(%) | CT-2 compressor efficiency(%) | CT-1 Heat Rate (Btu/Kwh) | CT-2 Heat Rate (Btu/Kwh) |  | DB(1+2) | DB-1 Ops Hours | DB-2 Ops Hours | CT-1 Wetcomprssion Ops Hours | RO Operation Hours | CT1 T/G Brg |  | CT2 T/G Brg
[7 empty] | CT1 |  | CT2 |  | CT1 |  | CT2 | [43 empty] | mmscf/d | mmscf/d | WetC flow | HBTU KPPH | HBTU KPPH | LBTU KPPH | mbar | Hz | [6 empty] | mmscf/d |  |  |  |  | Supply air pressure | Seal air pressure | Supply air pressure | Seal air pressure
[5 empty] | Max | Min | hrs | min | hrs | min | hrs | min | hrs | min | hrs | min | [42 empty] | gpm | [16 empty] | Psi | "WC | Psi | "WC
Week 22 | 2018-05-28 | 97.22 | 34.15% | 66.68 | 108 | 84 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3422 | 3068 | 3068 | 2995 | 3100 | 43 | 0 | 45 | 0 | 57 | 0 | 105 | -73 | 131 | 98.6% | 142.5833 | 87.52% | 100% | 89.66% | 9.323 | 151.62 | 1413.5533 | 24.963 | 974.1 | 24316.4583 | 8590.9888 | 127.8333 | 0 | 0 | 0 | 0 | 15 | 1440 | 0 | 1019 | 1070 | 1011 | 51 | 8590.9888 | 42.125 | 0 | 0 | 27 | 26.66 | 21.85 | 26.14 | 977.2 | 50.08 | 0.9407 | 95.09 | 86.57 | 12287 | 11717 | -570 | 0 | 0 | 0 | 24 | 7.2 | 2.1 | 4.1 | 2.1 | 0
| 2018-05-29 | 96.22 | 34.8% | 66.34 | 108 | 85 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3432 | 3066 | 3066 | 2997 | 3095 | 43 | 0 | 45 | 0 | 57 | 0 | 98 | -69 | 132 | 97.7% | 143 | 87.33% | 100% | 89.66% | 9.32 | 151.25 | 1409.65 | 24.869 | 973.06 | 24199.0291 | 8544.7712 | 127.75 | 0 | 0 | 0 | 0 | 15 | 1440 | 0 | 1019 | 1067 | 1009 | 48 | 8544.7712 | 42.0417 | 0 | 0 | 27 | 26.58 | 21.79 | 26.2 | 972.75 | 50.05 | 0.9408 | 95.3 | 86.62 | 12259 | 11718 | -541 | 0 | 0 | 0 | 24 | 5.7 | 2.1 | 4.1 | 2.1 | 0
| 2018-05-30 | 97 | 37.4% | 70 | 109 | 85 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3425 | 3029 | 3029 | 2953 | 3050 | 42 | 0 | 44 | 0 | 57 | 0 | 97 | -76 | 130 | 97.76% | 142.7083 | 86.22% | 100% | 89.51% | 9.22 | 149.97 | 1382.7234 | 24.597 | 978.8 | 24075.5436 | 8621.1537 | 126.2083 | 0 | 0 | 0 | 0 | 15 | 1440 | 0 | 1005 | 1047 | 998 | 42 | 8621.1537 | 41.5833 | 0 | 0 | 27 | 26.3 | 21.45 | 26.3 | 975.5 | 50.05 | 0.9404 | 95.3 | 86.87 | 12288 | 11768 | -520 | 0 | 0 | 0 | 23.8 | 7.2 | 2.2 | 4.2 | 2 | 0
| 2018-05-31 | 98 | 39% | 71 | 109 | 85 | 15 | 56 | 17 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 3413 | 3019 | 3019 | 2086 | 2163 | 42 | 465 | 44 | 307 | 57 | 417 | 85 | -933 | 129 | 69.86% | 142.2083 | 61.12% | 72.41% | 61.65% | 7.04 | 154.71 | 1089.1584 | 17.768 | 980.3736 | 17419.2781 | 8872.6925 | 125.7917 | 22 | 19 | 16 | 80 | 20 | 1023 | 8 | 672 | 809 | 682 | 137 | 8872.6925 | 28.4167 | 0 | 0 | 27 | 17.8 | 16.88 | 20.25 | 976.9 | 50.05 | 0.9387 | 96.15 | 86.9 | 12251 | 11700 | -551 | 0 | 0 | 0 | 14.8 | 13.1 | 2.1 | 4.2 | 2.1 | 0
| 2018-06-01 | 99 | 35% | 68 | 111 | 86 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3403 | 3041 | 3041 | 2976 | 3075 | 42 | 0 | 44 | 0 | 57 | 0 | 99 | -65 | 130 | 98.56% | 141.7917 | 87.45% | 100% | 89.51% | 9.304 | 154.69 | 1439.2358 | 24.69 | 981.003 | 24220.9641 | 8622.379 | 126.7083 | 0 | 0 | 0 | 0 | 15 | 1440 | 0 | 1013 | 1057 | 1005 | 44 | 8622.379 | 41.875 | 0 | 0 | 27 | 26.33 | 21.52 | 25.81 | 977.6 | 50.13 | 0.9403 | 95.56 | 86.58 | 12209 | 11681 | -528 | 0 | 0 | 0 | 24 | 6.7 | 2.1 | 4.2 | 2.1 | 0
| 2018-06-02 | 97.9 | 38.9% | 71 | 109 | 86 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3416 | 3027 | 3027 | 2952 | 3052 | 42 | 0 | 44 | 0 | 57 | 0 | 100 | -75 | 130 | 97.82% | 142.3333 | 86.42% | 100% | 89.51% | 9.352 | 151.08 | 1412.9002 | 24.444 | 982.2042 | 24009 | 8611.7548 | 126.125 | 0 | 0 | 0 | 0 | 15 | 1440 | 0 | 1006 | 1048 | 998 | 42 | 8611.7548 | 41.5833 | 0 | 0 | 27 | 26.07 | 21.28 | 26.19 | 978.21 | 50.11 | 0.9406 | 95.9 | 86.95 | 12185 | 11696 | -489 | 0 | 0 | 0 | 24 | 7.12 | 2.2 | 4.3 | 2.1 | 0
| 2018-06-03 | 100.1 | 39.7% | 72.1 | 113 | 86 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3393 | 3002 | 3002 | 2928 | 3027 | 42 | 0 | 43 | 0 | 57 | 0 | 99 | -74 | 128 | 98.54% | 141.375 | 86.3% | 100% | 88.73% | 9.307 | 153.58 | 1429.3691 | 24.211 | 986.5 | 23884.1515 | 8645.3281 | 125.0833 | 0 | 0 | 0 | 0 | 16 | 1440 | 0 | 996 | 1037 | 994 | 41 | 8645.3281 | 41.4167 | 0 | 0 | 26.9 | 25.81 | 21.04 | 25.97 | 976.33 | 50.08 | 0.9406 | 95.81 | 87.02 | 12160 | 11695 | -465 | 0 | 0 | 0 | 24 | 6.75 | 2.2 | 4.2 | 2 | 0
Week 23 | 2018-06-04 | 99.8 | 42.8% | 73.7 | 110 | 88 | 21 | 8 | 22 | 7 | 0 | 0 | 0 | 0 | 2 | 9 | 3393 | 3054 | 3054 | 2651 | 2745 | 42 | 157 | 43 | 92 | 57 | 126 | 96 | -403 | 137 | 83.49% | 141.375 | 78.13% | 91.33% | 67.16% | 6.318 | 153.93 | 972.5297 | 22.159 | 986.86 | 21867.8307 | 8615.7527 | 127.25 | 20 | 15 | 25 | 21 | 41 | 1185 | 2 | 874 | 959 | 912 | 85 | 8615.7527 | 38 | 0.219 | 0.215 | 27 | 22.78 | 19.49 | 24.73 | 976 | 50.1 | 0.9404 | 96.17 | 87.08 | 12154 | 11691 | -463 | 0.434 | 2.15 | 2.15 | 21.1 | 6.17 | 2 | 4.3 | 2.2 | 0
| 2018-06-05 | 100.9 | 44.5% | 75.5 | 114 | 87 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3386 | 2955 | 2955 | 2886 | 2985 | 41 | 0 | 43 | 0 | 57 | 0 | 99 | -69 | 129 | 96.41% | 141.0833 | 85.23% | 100% | 88.65% | 9.298 | 154.2 | 1433.7516 | 23.829 | 999.2077 | 23810.1203 | 8747.0104 | 123.125 | 0 | 0 | 0 | 0 | 16 | 1440 | 0 | 984 | 1023 | 978 | 39 | 8747.0104 | 40.75 | 0 | 0 | 27 | 25.38 | 20.58 | 26.48 | 977.42 | 50.11 | 0.9408 | 96.47 | 87.16 | 12105 | 11640 | -465 | 0 | 0 | 0 | 24 | 4.83 | 2.2 | 4.3 | 2 | 0
| 2018-06-06 | 94.9 | 47.2% | 72.7 | 105 | 83 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3447 | 3011 | 3011 | 2942 | 3045 | 42 | 0 | 44 | 0 | 57 | 0 | 103 | -69 | 130 | 97.6% | 143.625 | 85.35% | 100% | 88.81% | 9.293 | 151.67 | 1409.4693 | 24.351 | 994.25 | 24210.9817 | 8708.515 | 125.4583 | 0 | 0 | 0 | 0 | 16 | 1440 | 0 | 1003 | 1048 | 994 | 45 | 8708.515 | 41.4167 | 0 | 0 | 27 | 26 | 21.08 | 26.89 | 981.25 | 50.13 | 0.94 | 96.5 | 87.26 | 12179 | 11656 | -523 | 0 | 0 | 0 | 24 | 6.63 | 2.1 | 4.2 | 2.1 | 0
| 2018-06-07 | 99.4 | 46.5% | 75.7 | 107 | 90 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3402 | 2967 | 2967 | 2894 | 2991 | 41 | 0 | 43 | 0 | 57 | 0 | 97 | -73 | 126 | 98.91% | 141.75 | 85.07% | 100% | 88.65% | 9.284 | 153.65 | 1426.4866 | 24.055 | 987.6112 | 23756.9874 | 8701.9606 | 123.625 | 0 | 0 | 0 | 0 | 16 | 1440 | 0 | 987 | 1024 | 980 | 37 | 8701.9606 | 40.8333 | 0 | 0 | 27 | 25.82 | 20.82 | 26.85 | 976.42 | 50.09 | 0.9415 | 96.65 | 87.45 | 12282 | 11787 | -495 | 0 | 0 | 0 | 24 | 6.9 | 2.2 | 4.3 | 2.1 | 0
| 2018-06-08 | 101.5 | 42.87% | 75.54 | 112 | 92 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3381 | 2960 | 2960 | 2889 | 2990 | 41 | 0 | 43 | 0 | 57 | 0 | 101 | -71 | 127 | 98.1% | 140.875 | 85.45% | 100% | 88.65% | 9.289 | 154.12 | 1431.6207 | 23.826 | 988.1637 | 23543.9882 | 8645.0706 | 123.3333 | 0 | 0 | 0 | 0 | 16 | 1440 | 0 | 984 | 1024 | 982 | 40 | 8645.0706 | 40.9167 | 0 | 0 | 27 | 25.58 | 20.58 | 26.92 | 975.25 | 50.14 | 0.9418 | 96.37 | 87.23 | 12205 | 11695 | -510 | 0 | 0 | 0 | 24 | 7 | 2.1 | 4.2 | 2 | 0
| 2018-06-09 | 92.08 | 57.1% | 74.93 | 99 | 89 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3475 | 2981 | 2981 | 2915 | 3014 | 42 | 0 | 43 | 0 | 57 | 0 | 99 | -66 | 128 | 98.11% | 144.7917 | 83.88% | 100% | 88.73% | 9.254 | 149.78 | 1386.0641 | 24.1604 | 989.5281 | 23907.4156 | 8677.0085 | 124.2083 | 0 | 0 | 0 | 0 | 16 | 1440 | 0 | 996 | 1037 | 981 | 41 | 8677.0085 | 40.875 | 0 | 0 | 27 | 25.89 | 20.82 | 27.22 | 977.42 | 50.15 | 0.9403 | 96.75 | 87.19 | 12244 | 12054 | -190 | 0 | 0 | 0 | 24 | 6.78 | 2.1 | 4.4 | 2.1 | 0
| 2018-06-10 | 90.36 | 63.39% | 76.76 | 100 | 80 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3495 | 2983 | 2983 | 2911 | 3010 | 41 | 0 | 43 | 0 | 57 | 0 | 99 | -72 | 127 | 98.75% | 145.625 | 83.29% | 100% | 88.65% | 9.292 | 148.84 | 1383.0213 | 24.2232 | 981.6703 | 23779.196 | 8643.8397 | 124.2917 | 0 | 0 | 0 | 0 | 16 | 1440 | 0 | 991 | 1034 | 985 | 43 | 8643.8397 | 41.0417 | 0 | 0 | 27 | 25.98 | 20.99 | 27.29 | 979.83 | 50.09 | 0.9397 | 96.95 | 87.32 | 12318 | 11768 | -550 | 0 | 0 | 0 | 24 | 7.77 | 2.1 | 4.2 | 2 | 0
Week 24 | 2018-06-11 | 97 | 54% | 78 | 106 | 88 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3421 | 2952 | 2952 | 2872 | 2975 | 41 | 0 | 43 | 0 | 57 | 0 | 103 | -80 | 125 | 99.17% | 142.5417 | 83.95% | 100% | 88.65% | 9.261 | 153.2 | 1418.7852 | 23.7499 | 987.96 | 23463.9808 | 8663.9158 | 123 | 0 | 0 | 0 | 0 | 16 | 1440 | 0 | 977 | 1023 | 975 | 46 | 8663.9158 | 40.625 | 0 | 0 | 27 | 25.5 | 20.57 | 27.59 | 977.6 | 50.1 | 0.9413 | 96.56 | 87.38 | 12239 | 11733 | -506 | 0 | 0 | 0 | 23.6 | 7.6 | 2.1 | 4.3 | 2.1 | 0
| 2018-06-12 | 100.4 | 45% | 75 | 112 | 89 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3390 | 2959 | 2959 | 2880 | 2984 | 41 | 0 | 42 | 0 | 57 | 0 | 104 | -79 | 126 | 98.68% | 141.25 | 84.96% | 100% | 88.57% | 9.276 | 154.32 | 1431.4723 | 23.6561 | 995.054 | 23539.087 | 8670.3331 | 123.2917 | 0 | 0 | 0 | 0 | 16 | 1440 | 0 | 980 | 1025 | 979 | 45 | 8670.3331 | 40.7917 | 0 | 0 | 27 | 25.37 | 20.51 | 27.6 | 973.8 | 50.06 | 0.9414 | 96 | 87.2 | 12155 | 11683 | -472 | 0 | 0 | 0 | 23.4 | 9 | 2.1 | 4.2 | 2.1 | 0
| 2018-06-13 | 98.2 | 49% | 76 | 108 | 90 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3411 | 2959 | 2959 | 2884 | 2988 | 41 | 0 | 43 | 0 | 57 | 0 | 104 | -75 | 127 | 98.03% | 142.125 | 84.55% | 100% | 88.65% | 9.26 | 152.23 | 1409.6498 | 23.7932 | 991.3 | 23586.2289 | 8667.0869 | 123.2917 | 0 | 0 | 0 | 0 | 16 | 1440 | 0 | 983 | 1027 | 978 | 44 | 8667.0869 | 40.75 | 0 | 0 | 27 | 25.51 | 20.52 | 27.57 | 974.1 | 50.13 | 0.9407 | 96.38 | 87.14 | 12179 | 11658 | -521 | 0 | 0 | 0 | 24 | 4.7 | 2.1 | 4.2 | 2.1 | 0
| 2018-06-14 | 96.8 | 53.3% | 76.4 | 105 | 90 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3431 | 2957 | 2957 | 2887 | 2990 | 41 | 0 | 43 | 0 | 57 | 0 | 103 | -70 | 127 | 98.1% | 142.9583 | 84.14% | 100% | 88.65% | 9.275 | 150.65 | 1397.2788 | 23.8357 | 992.6579 | 23660.7257 | 8679.5997 | 123.2083 | 0 | 0 | 0 | 0 | 16 | 1440 | 0 | 983 | 1029 | 978 | 46 | 8679.5997 | 40.75 | 0 | 0 | 27 | 25.5 | 20.58 | 27.3 | 974.08 | 50.17 | 0.9413 | 96.51 | 87.21 | 12190 | 11661 | -529 | 0 | 0 | 0 | 24 | 7.75 | 2.1 | 4.2 | 2.1 | 0
| 2018-06-15 | 95.8 | 53.9% | 76.2 | 103 | 88 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3444 | 2957 | 2957 | 2889 | 2986 | 41 | 0 | 43 | 0 | 57 | 0 | 97 | -68 | 127 | 97.97% | 143.5 | 83.89% | 100% | 88.65% | 9.086 | 151.62 | 1377.6193 | 23.8049 | 994.78 | 23680.6086 | 8673.6684 | 123.2083 | 0 | 0 | 0 | 0 | 16 | 1440 | 0 | 982 | 1026 | 978 | 44 | 8673.6684 | 40.75 | 0 | 0 | 27 | 25.47 | 20.57 | 27.14 | 976.13 | 50.14 | 0.9409 | 96.61 | 87.23 | 12160 | 11650 | -510 | 0 | 0 | 0 | 24 | 6.92 | 2 | 4.3 | 2.1 | 0
| 2018-06-16 | 96.8 | 58.6% | 78.4 | 104 | 91 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3431 | 2938 | 2938 | 2873 | 2970 | 41 | 0 | 42 | 0 | 57 | 0 | 97 | -65 | 126 | 98.21% | 142.9583 | 83.74% | 100% | 88.57% | 9.1 | 151.86 | 1381.926 | 23.67 | 997.507 | 23610.9907 | 8699.2401 | 122.4167 | 0 | 0 | 0 | 0 | 16 | 1440 | 0 | 976 | 1021 | 973 | 45 | 8699.2401 | 40.5417 | 0 | 0 | 27 | 25.33 | 20.44 | 27.25 | 979.4 | 50.16 | 0.9409 | 96.83 | 87.38 | 12173 | 11664 | -509 | 0 | 0 | 0 | 24 | 7.27 | 2.1 | 4.3 | 2.1 | 0
| 2018-06-17 | 90 | 59.2% | 73.9 | 97 | 81 | 15 | 9 | 24 | 0 | 7 | 59 | 0 | 0 | 0 | 0 | 3371 | 3203 | 2540 | 2261 | 2349 | 41 | 0 | 43 | 0 | 57 | 0 | 88 | -279 | 126 | 77.68% | 140.4583 | 67.07% | 100% | 79.73% | 9.111 | 150.97 | 1375.4877 | 18.906 | 992.91 | 18771.9565 | 8910.8554 | 133.4583 | 20 | 52 | 11 | 243 | 26 | 1440 | 0 | 601 | 994 | 754 | 393 | 8910.8554 | 31.4167 | 0 | 0 | 27 | 16.12 | 19.93 | 27.18 | 982 | 50.21 | 0.9403 | 96.79 | 87.35 | 12049 | 11767 | -282 | 0 | 0 | 0 | 10.25 | 5.55 | 2.1 | 4.2 | 2.1 | 0
Week 25 | 2018-06-18 | 88.4 | 63.2% | 74.8 | 97 | 79 | 2 | 40 | 2 | 40 | 21 | 0 | 21 | 3 | 0 | 0 | 3512 | 3371 | 356 | 350 | 360 | 41 | 0 | 43 | 0 | 57 | 0 | 30 | -6 | 126 | 11.9% | 146.3333 | 9.966% | 100% | 97.46% | 1.128 | 149.36 | 168.4781 | 2.928 | 996.77 | 2918.5426 | 8820.059 | 140.4583 | 18 | 20 | 17 | 17 | 25 | 180 | 20 | 119 | 122 | 119 | 3 | 8820.059 | 4.9583 | 0 | 0 | 27 | 3.27 | 2.5 | 3.09 | 984.21 | 50.09 | 0.9415 | 97.12 | 87.38 | 12047 | 11554 | -493 | 0 | 0 | 0 | 2.66 | 5.02 | 2.1 | 1.3 | 2.1 | 0
| 2018-06-19 | 93.7 | 58.2% | 77 | 103 | 83 | 11 | 30 | 13 | 25 | 11 | 59 | 8 | 38 | 0 | 0 | 3461 | 3157 | 1579 | 1543 | 1604 | 41 | 0 | 43 | 0 | 57 | 0 | 69 | -36 | 125 | 53.47% | 144.2083 | 44.58% | 100% | 90% | 5.673 | 158.96 | 901.7801 | 12.971 | 1006.066 | 13049.6821 | 9041.7772 | 131.5417 | 24 | 31 | 15 | 117 | 22 | 809 | 8 | 472 | 633 | 499 | 161 | 9041.7772 | 20.7917 | 0 | 0 | 27 | 12.35 | 12.85 | 16.43 | 983.38 | 50.08 | 0.9409 | 96.53 | 87.45 | 11953 | 11395 | -558 | 0 | 0 | 0 | 10.45 | 6.6 | 2.1 | 4.5 | 2.1 | 0
| 2018-06-20 | 93.29 | 53.92% | 74.16 | 107 | 82 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3466 | 3010 | 3010 | 2940 | 3042 | 42 | 0 | 44 | 0 | 57 | 0 | 102 | -70 | 129 | 98.26% | 144.4167 | 84.82% | 100% | 88.81% | 9.115 | 151.51 | 1381.0136 | 23.787 | 1013.87 | 24116.9257 | 8672.7685 | 125.4167 | 0 | 0 | 0 | 0 | 16 | 1440 | 0 | 997 | 1054 | 991 | 57 | 8672.7685 | 41.2917 | 0 | 0 | 27 | 25.1 | 20.56 | 26.12 | 984.83 | 50.15 | 0.9423 | 96.3 | 87.33 | 11826 | 11289 | -537 | 0 | 0 | 0 | 24 | 6.12 | 2.1 | 4.4 | 2.1 | 0
| 2018-06-21 | 92.03 | 57.3% | 74.8 | 105 | 79 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3476 | 3012 | 3012 | 2941 | 3043 | 42 | 0 | 44 | 0 | 57 | 0 | 102 | -71 | 129 | 98.29% | 144.8333 | 84.61% | 100% | 88.81% | 9.087 | 149.84 | 1361.5961 | 24.377 | 996.5952 | 24294.0012 | 8723.4265 | 125.5 | 0 | 0 | 0 | 0 | 16 | 1440 | 0 | 997 | 1054 | 992 | 57 | 8723.4265 | 41.3333 | 0 | 0 | 27 | 25.72 | 21.14 | 25.88 | 984.6 | 50.13 | 0.9413 | 96.3 | 87.41 | 12111 | 11515 | -596 | 0 | 0 | 0 | 24 | 6.23 | 2.2 | 4.3 | 2.1 | 0
| 2018-06-22 | 96.5 | 49.2% | 74.8 | 107 | 86 | 22 | 7 | 24 | 0 | 1 | 27 | 0 | 0 | 0 | 0 | 3430 | 3019 | 2894 | 2825 | 2927 | 41 | 0 | 43 | 0 | 57 | 0 | 102 | -69 | 128 | 95.28% | 142.9167 | 82.36% | 100% | 87.07% | 9.072 | 156.69 | 1421.4917 | 23.453 | 988.767 | 23189.5525 | 8711.874 | 125.7917 | 13 | 26 | 0 | 0 | 18 | 1440 | 0 | 927 | 1047 | 953 | 120 | 8711.874 | 39.7083 | 0 | 0 | 27 | 23.99 | 20.91 | 26.28 | 983.4 | 50.19 | 0.942 | 96.34 | 87.41 | 12124 | 11531 | -593 | 0 | 0 | 0 | 22.12 | 6.62 | 2.1 | 4.3 | 2.1 | 0
| 2018-06-23 | 94 | 50% | 73 | 104 | 82 | 14 | 12 | 24 | 0 | 9 | 10 | 0 | 0 | 0 | 0 | 3458 | 3190 | 2379 | 2338 | 2430 | 41 | 0 | 44 | 0 | 57 | 0 | 92 | -41 | 127 | 79.72% | 144.0833 | 67.61% | 100% | 86.25% | 9.08 | 155.77 | 1414.3916 | 19.351 | 992.93 | 19214.1884 | 8823.1737 | 132.9167 | 20 | 38 | 0 | 0 | 19 | 1440 | 0 | 598 | 1055 | 777 | 457 | 8823.1737 | 32.375 | 0 | 0 | 27 | 15.7 | 21.07 | 26.18 | 984.4 | 50.14 | 0.9412 | 96.2 | 87.28 | 12123 | 11486 | -637 | 0 | 0 | 0 | 13.4 | 6.7 | 2.1 | 4.3 | 2.1 | 0
| 2018-06-24 | 95.5 | 51.6% | 74.7 | 108 | 86 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3441 | 3000 | 3000 | 2925 | 3026 | 41 | 0 | 43 | 0 | 57 | 0 | 101 | -75 | 129 | 97.74% | 143.375 | 85% | 100% | 88.65% | 9.082 | 157.5 | 1430.415 | 24.152 | 993.33 | 23990.9062 | 8691.05 | 125 | 0 | 0 | 0 | 0 | 16 | 1440 | 0 | 992 | 1046 | 988 | 54 | 8691.05 | 41.1667 | 0 | 0 | 27 | 25.6 | 20.95 | 26.42 | 982.2 | 50.14 | 0.9425 | 96.45 | 87.37 | 12126 | 11552 | -574 | 0 | 0 | 0 | 24 | 6.4 | 2.1 | 4.2 | 2.2 | 0
Week 26 | 2018-06-25 | 95.6 | 51.5% | 74.8 | 106 | 84 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 3435 | 3168 | 3168 | 3100 | 3209 | 41 | 0 | 44 | 0 | 57 | 0 | 109 | -68 | 142 | 94.16% | 143.125 | 90.25% | 100% | 94.37% | 9.054 | 155.85 | 1411.0659 | 26.288 | 989.37 | 26008.5586 | 8845.0401 | 132 | 0 | 0 | 0 | 0 | 16 | 720 | 0 | 994 | 1052 | 1163 | 58 | 8845.0401 | 48.4583 | 0.956 | 0.96 | 27 | 25.86 | 21.22 | 26.34 | 979.8 | 50.15 | 0.9427 | 96.43 | 87.42 | 12227 | 11627 | -600 | 1.916 | 12 | 12 | 24 | 6.9 | 2.1 | 4.2 | 2.1 | 0
| 2018-06-26 | 97.9 | 46.8% | 74.3 | 108 | 86 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 3417 | 3158 | 3158 | 3090 | 3200 | 41 | 0 | 44 | 0 | 57 | 0 | 110 | -68 | 142 | 93.9% | 142.375 | 90.43% | 100% | 94.37% | 9.064 | 154 | 1395.856 | 26.193 | 988.253 | 25885.3108 | 8828.8566 | 131.5833 | 0 | 0 | 0 | 0 | 16 | 720 | 0 | 991 | 1049 | 1160 | 58 | 8828.8566 | 48.3333 | 0.998 | 0.954 | 27 | 25.73 | 21.14 | 26.19 | 979.5 | 50.11 | 0.9423 | 96.32 | 87.43 | 12182 | 11601 | -581 | 1.952 | 12 | 12 | 24 | 6.57 | 2.1 | 4.4 | 2.1 | 0
| 2018-06-27 | 89.4 | 60.9% | 74.6 | 97 | 82 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 3502 | 3178 | 3178 | 3113 | 3217 | 41 | 0 | 44 | 0 | 57 | 0 | 104 | -65 | 142 | 94.4% | 145.9167 | 88.89% | 100% | 94.37% | 9.073 | 149.46 | 1356.0506 | 26.358 | 990.38 | 26104.436 | 8821.2292 | 132.4167 | 0 | 0 | 0 | 0 | 16 | 720 | 0 | 999 | 1051 | 1167 | 52 | 8821.2292 | 48.625 | 1.013 | 0.998 | 27 | 25.88 | 21.24 | 26.52 | 982.79 | 50.08 | 0.941 | 96.69 | 87.51 | 12177 | 11624 | -553 | 2.011 | 12 | 12 | 24 | 6.82 | 2.1 | 4.2 | 2.2 | 0
| 2018-06-28 | 86.8 | 66.4% | 74.8 | 92 | 82 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 17 | 46 | 3531 | 3221 | 3101 | 3058 | 3159 | 41 | 0 | 44 | 0 | 57 | 0 | 101 | -43 | 142 | 92.69% | 147.125 | 86.6% | 100% | 92.41% | 9.08 | 149.49 | 1357.3692 | 25.623 | 991.67 | 25409.5604 | 8753.0836 | 134.2083 | 0 | 0 | 0 | 0 | 15 | 1034 | 0 | 1001 | 1057 | 1101 | 56 | 8753.0836 | 45.875 | 0.617 | 0.615 | 27 | 25.87 | 21.26 | 26.38 | 985.88 | 50.13 | 0.94 | 96.68 | 87.51 | 12130 | 11560 | -570 | 1.232 | 13 | 13 | 24 | 6.52 | 2.1 | 4.2 | 2 | 0
| 2018-06-29 | 84.5 | 72.3% | 76.5 | 89 | 82 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 12 | 6 | 3549 | 3426 | 3196 | 3163 | 3270 | 41 | 0 | 44 | 0 | 57 | 0 | 107 | -33 | 144 | 94.62% | 147.875 | 89.12% | 100% | 95.38% | 8.148 | 141.42 | 1152.2902 | 26.992 | 997.36 | 26920.7411 | 8875.4446 | 142.75 | 0 | 0 | 0 | 0 | 13 | 726 | 0 | 1001 | 1051 | 1218 | 50 | 8875.4446 | 50.75 | 1.221 | 1.217 | 27 | 25.76 | 21.4 | 24.48 | 985.46 | 50.14 | 0.9423 | 96.8 | 87.54 | 12102 | 11529 | -573 | 2.438 | 24 | 24 | 24 | 6.62 | 2.1 | 4.3 | 2.1 | 0
| 2018-06-30 | 84.3 | 79.6% | 79.2 | 92 | 78 | 20 | 4 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3552 | 2879 | 2759 | 2719 | 2814 | 41 | 218 | 44 | 0 | 57 | 0 | 95 | -40 | 131 | 89.5% | 148 | 76.55% | 95.63% | 82.76% | 9.06 | 147.07 | 1332.4542 | 23.048 | 985.41 | 22711.7297 | 8843.0246 | 119.9583 | 22 | 18 | 0 | 0 | 18 | 1440 | 0 | 832 | 1051 | 931 | 219 | 8843.0246 | 38.7917 | 0.101 | 0.253 | 27 | 21.98 | 21.57 | 26.04 | 984.67 | 50.13 | 0.9397 | 97.3 | 87.66 | 12327 | 11741 | -586 | 0.354 | 6.1 | 10.12 | 19.1 | 7.13 | 2.1 | 4.3 | 2.1 | 0
| 2018-07-01 | [26 empty] | 0 | 0 |  | no data | no data | no data | no data | no data |  |  | 0 |  |  | 0 | no data | no data | [10 empty] | 0 | no data | 0 | [13 empty] | 0
| Monthly | 94.762 | 53.06% | 74.9097 | 104.3333 | 85.1667 | 658 | 50 | 686 | 12 | 49 | 35 | 29 | 41 | 7 | 1 | 103320 | 91695 | 85033 | 82773.85 | 85477 | 41.2667 | 375 | 43.3333 | 92 | 57 | 126 | 2733.15 | -2438 | 130.4 | 90.93% | 143.5 | 79.99% | 99.57% | 88.64% | 260.076 | 152.2437 | 39600.9196 | 686.8855 | 991.9979 | 681118.3489 | 8707.0889 | 127.3542 | 137 | 200 | 68 | 398 | 531 | 37774 | 30 | 27236 | 29758 | 28483 | 2522 | 8707.0889 | 39.5597 | 5.125 | 5.212 | 26.9967 | 23.575 | 19.971 | 25.411 | 979.932 | 50.1253 | 0.94108 | 96.4757 | 87.2943 | 12154.7 | 11639.4333 |  | 10.337 | 81.25 | 85.27 | 650.08 | 199.69
| Totals | Avg.F | % Avg. |  | M Avg | m Avg | hrs | min | hrs | min | hrs | min | hrs | min | hrs | min | MWhr Total | MWhr Total | MWhr Total | MWhr Total | MWhr Total | MW Avg | Total min | Avg MW | Total min | Avg MW | Total min | MWhr | Total MW | Av Max D/Gen | Av. DailyLF | Avg. | Avg. |  | Avg. | Total | Avg. |  | Total | Avg. |  | Avg. | [7 empty] | Total |  |  |  |  | Avg.
| Weeks data | Site Avg. Amb. Temp F | Site Avg. Relative humidity % |  | M Avg: Site Maximum/Minumum Temperature; hrs: CT-1 Base Load Hours; hrs: CT-2 Base Load Hours; hrs: CT-1 stand by hours / min; hrs: CT-2 standby hours / min; hrs: Plant ambient Corrected maximum Load hours/min | Average Corrected Plant Capacity | Ambient Corrected Declared Avail'y (MWH) | Av Plant WAPDA Dispatch | Net Plant Export (MWH) | Gross Generation | CT1 Av Cap (MW) | CT1 Unavail minutes | CT2 Av Cap (MW) | CT2 Unavail minutes | ST Unavail minutes | ST Average Cap (MW) | Plant Aux Load including Colony Load MWH | Differenece (+/-) MW | Maximum Daily Generation | Daily Load Factor | Avg. Corrected Plant | Plant Capacity Facto | Plant Availability Factor | Equivalent Plant Availability | LBtu gas flow mmscf | 1 LBtu gas (Average Btu/scf) | LBTU MMBTU | PL gas flow (mscf/week) | 1 PL gas (Average Btu/scf) | HBTU MMBTU | Plant Net Heat Rate (Btu/Kwh) | [11 empty] | 98.75
| Week 22 | 97.92 | 36.9929 | 69.3029 | 109.5714 | 85.2857 | 159 | 56 | 161 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 3414.8571 | 3036 | 3036 | 19887 | 20562 | 42.2857 | 465 | 44.1429 | 307 | 417 | 57 | no data | -1365 | 130 | 94.12% | 142.2857 | 83.19% | 96.06% | 85.46% | 62.866 | 152.4143 | 9581.6765 | 165.542 | 979.4344 | 162137.53 | 8644.1526
| Week 23 | 96.9914 | 49.19% | 74.9757 | 106.7143 | 87 | 165 | 6 | 166 | 7 | 0 | 0 | 0 | 0 | 2 | 9 | 3425.5714 | 2987.2857 | 2987.2857 | 20088 | 20780 | 41.4286 | 157 | 43.1429 | 92 | 126 | 57 | 694 | -823 | 129.1429 | 95.91% | 142.7321 | 83.77% | 98.76% | 85.62% | 62.028 | 152.3129 | 9447.6619 | 166.6036 | 989.613 | 164873.1091 | 8677.0225
| Week 24 | 96.4286 | 53.29% | 76.2714 | 105 | 88.1429 | 159 | 9 | 168 | 0 | 7 | 59 | 0 | 0 | 0 | 0 | 3414.1429 | 2989.2857 | 2894.5714 | 19546 | 20242 | 41 | No outage | 42.7143 | No outage | No outage | 57 | 696 | -716 | 126.2857 | 95.4% | 142.256 | 81.76% | 100% | 87.35% | 64.369 | 152.1214 | 9791.9042 | 142.5099 | 993.2098 | 141542.182 | 8709.2428
| Week 25 | 93.3457 | 0.54774 | 74.7514 | 104.4286 | 82.4286 | 122 | 29 | 136 | 5 | 43 | 36 | 29 | 41 | 0 | 0 | 3463.4286 | 3108.4286 | 2318.5714 | 15862 | 16432 | 41.2857 | No outage | 43.4286 | No outage | 399 | 57 | 598 | -368 | 127.5714 | 76.38% | 144.3095 | 65.57% | 100% | 89.58% | 52.237 | 154.2329 | 8056.6618 | 131.019 | 998.3326 | 130800.5389 | 8783.447
| Week 26 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Date | Plant Status Whether Normal Operation or Tripping (State full detail for trippings/return to normal).
| 2018-06-01 | Plant load restricted 122~126 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-06-02 | Plant load restricted 120~126 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-06-03 | Plant load restricted 120~124 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-06-04 | Complex tripped @ 1329 hrs due to Wapda Supply Failure. Wapda Supply restored @ 1332 hrs, but voltages remained below PPA technical limits. Wapda supply stabilized @ 1435 hrs and plant started, CT-2 synch @ 1501 hrs, STG synch @ 1536 hrs & CT-1 synch @ 1606 hrs.
| 2018-06-05 | Plant load restricted 118~124 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-06-06 | Plant load restricted 120~125 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-06-07 | Plant load restricted 120~122 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-06-08 | Plant load restricted 119~122 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-06-09 | Plant load restricted 120~124 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-06-10 | Plant load restricted 120~123 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-06-11 | Plant load restricted 118~121 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-06-12 | Plant load restricted 116~122 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-06-13 | Plant load restricted 118~123 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-06-14 | Plant load restricted 118~123 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-06-15 | Plant load restricted 118~123 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-06-16 | Plant load restricted 118~122 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-06-17 | Plant load remained 90 MW from 0416~0815 hrs & 62 MW from 0815~1630 hrs at NPCC demand. CT-1 de-synch @ 0825 hrs & synch @ 1624 hrs to meet NPCC load demand.
| 2018-06-18 | NPCC load demand of 0 MW received @ 0240 hrs. CT-2 de-synch @ 0257 hrs, CT-1 de-synch @ 0300 hrs & STG de-synch @ 0300 hrs. CT-2 compressor offline washing carried out.
| 2018-06-19 | NPCC load demand of 141 MW received @ 0752 hrs. CT-2 synch @ 0838 hrs, CT-1 synch @ 1159 hrs & STG de-synch @ 1031 hrs. CT-1 compressor offline washing carried out.
| 2018-06-20 | Plant load restricted 120~125 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-06-21 | Plant load restricted 120~125 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-06-22 | Plant load restricted 120~124 MW from 0000~2207 hrs as both DBs kept off to remain within contractual heatrate. CT-1 de-synch @ 2233 hrs to meet NPCC load demand of 62 MW received @2207 hrs.
| 2018-06-23 | After receiving max load demand from NPCC @ 0840 hrs, CT-1 synch @ 0910 hrs. Both DBs kept off to remain within contractual heatrate.
| 2018-06-24 | Plant load restricted 119~124 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-06-25 | Plant load restricted 122~123 MW from 0000~1100 hrs & 2300~0000 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-06-26 | Plant load restricted 121~125 MW from 0000~1100 hrs & 2300~0000 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-06-27 | Plant load restricted 123~124 MW from 0000~1100 hrs & 2300~0000 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-06-28 | Plant load remained 124 MW from 0000~0632 hrs & 126 MW from 1848~2400 hrs to meet NPCC load demand.
| 2018-06-29 | Plant load remained 126 MW from 0000~0606 hrs to meet NPCC load demand. CT-1 Tripped on inlet vacuum high @ 0606 hrs and Synch @ 0944 hrs.
2018-06-30
0.88333
0.1
0.1

## July
2018-07-01
| Date | Site Avg. Ambient Temp.F | Site Avg. Relative Humidty % | Site Avg. Ambient Wetbulb Temp.F | Site Ambient Temp |  | Base load hours |  |  |  | Standby hours |  |  |  | Plant ambient corrected Max Load |  | Corrected Plant Capacity | Ambient Corrected Daclared Avail'y (MWH) | Plant WAPDA Dispatch (MWH) | Net Plant Export (MWH) | Gross Generation | CT1 Average Cap (MW) | CT1 Unavail minutes | CT2 Average Cap (MW) | CT2 Unavail minutes | ST Average Cap (MW) | ST Unavail minutes | Plant Aux Load including Colony Load MWH | Differenece (+/-) MW | Maximum Daily Generation | Daily Load Factor | Avg. Corrected Plant Capacity | Plant Capacity Factor | Plant Availability Factor | Equivalent Plant Availability | LBtu gas flow (mmscf/day) | 1 LBtu gas (Average Btu/scf) | LBTU MMBTU | 1 HBtu gas flow (mmscf/day) | 1 HBtu gas (Average Btu/scf) | HBTU MMBTU | HHV Net Heat Rate (Btu/Kwh) | Avg. declared availability | CT1 Derated MW | CT1 derated mintutes | CT-2 derated MW | CT-2 derated mintutes | ST derated MW | ST derated mintutes | WAPDA Backfeed (MWH) | CT-1 Gross Generation (MWH) | CT-2 Gross Generation (MWH) | STG Gross Generation (MWH) | CT-1 & CT-2 MWH difference | Base load Heat Rate | STG load | DB1 | DB2 | CT1 | CT1 Gas flow | CT2 Gas flow |  | Pamb | Freq. Hz | LBTU Gas Specific gravity | CT-1 compressor efficiency(%) | CT-2 compressor efficiency(%) | CT-1 Heat Rate (Btu/Kwh) | CT-2 Heat Rate (Btu/Kwh) |  | DB(1+2) | DB-1 Ops Hours | DB-2 Ops Hours | CT-1 Wetcomprssion Ops Hours | RO Operation Hours | CT1 T/G Brg |  | CT2 T/G Brg
[7 empty] | CT1 |  | CT2 |  | CT1 |  | CT2 | [43 empty] | mmscf/d | mmscf/d | WetC flow | HBTU KPPH | HBTU KPPH | LBTU KPPH | mbar | Hz | [6 empty] | mmscf/d |  |  |  |  | Supply air pressure | Seal air pressure | Supply air pressure | Seal air pressure
[5 empty] | Max | Min | hrs | min | hrs | min | hrs | min | hrs | min | hrs | min | [42 empty] | gpm | [16 empty] | Psi | "WC | Psi | "WC
Week 26 | 2018-06-25 | 95.6 | 51.5% | 74.8 | 106 | 84 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 3435 | 3168 | 3168 | 3100 | 3209 | 41 | 0 | 44 | 0 | 57 | 0 | 109 | -68 | 142 | 94.16% | 143.125 | 90.25% | 100% | 94.37% | 9.054 | 155.85 | 1411.0659 | 26.288 | 989.37 | 26008.5586 | 8845.0401 | 132 | 0 | 0 | 0 | 0 | 16 | 720 | 0 | 994 | 1052 | 1163 | 58 | 8845.0401 | 48.4583 | 0.956 | 0.96 | 27 | 25.86 | 21.22 | 26.34 | 979.8 | 50.15 | 0.9427 | 96.43 | 87.42 | 12227 | 11627 | -600 | 1.916 | 12 | 12 | 24 | 6.9 | 2.1 | 4.2 | 2.1 | 0
| 2018-06-26 | 97.9 | 46.8% | 74.3 | 108 | 86 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 3417 | 3158 | 3158 | 3090 | 3200 | 41 | 0 | 44 | 0 | 57 | 0 | 110 | -68 | 142 | 93.9% | 142.375 | 90.43% | 100% | 94.37% | 9.064 | 154 | 1395.856 | 26.193 | 988.253 | 25885.3108 | 8828.8566 | 131.5833 | 0 | 0 | 0 | 0 | 16 | 720 | 0 | 991 | 1049 | 1160 | 58 | 8828.8566 | 48.3333 | 0.998 | 0.954 | 27 | 25.73 | 21.14 | 26.19 | 979.5 | 50.11 | 0.9423 | 96.32 | 87.43 | 12182 | 11601 | -581 | 1.952 | 12 | 12 | 24 | 6.57 | 2.1 | 4.4 | 2.1 | 0
| 2018-06-27 | 89.4 | 60.9% | 74.6 | 97 | 82 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 3502 | 3178 | 3178 | 3113 | 3217 | 41 | 0 | 44 | 0 | 57 | 0 | 104 | -65 | 142 | 94.4% | 145.9167 | 88.89% | 100% | 94.37% | 9.073 | 149.46 | 1356.0506 | 26.358 | 990.38 | 26104.436 | 8821.2292 | 132.4167 | 0 | 0 | 0 | 0 | 16 | 720 | 0 | 999 | 1051 | 1167 | 52 | 8821.2292 | 48.625 | 1.013 | 0.998 | 27 | 25.88 | 21.24 | 26.52 | 982.79 | 50.08 | 0.941 | 96.69 | 87.51 | 12177 | 11624 | -553 | 2.011 | 12 | 12 | 24 | 6.82 | 2.1 | 4.2 | 2.2 | 0
| 2018-06-28 | 86.8 | 66.4% | 74.8 | 92 | 82 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 17 | 46 | 3531 | 3221 | 3101 | 3058 | 3159 | 41 | 0 | 44 | 0 | 57 | 0 | 101 | -43 | 142 | 92.69% | 147.125 | 86.6% | 100% | 92.41% | 9.08 | 149.49 | 1357.3692 | 25.623 | 991.67 | 25409.5604 | 8753.0836 | 134.2083 | 0 | 0 | 0 | 0 | 15 | 1034 | 0 | 1001 | 1057 | 1101 | 56 | 8753.0836 | 45.875 | 0.617 | 0.615 | 27 | 25.87 | 21.26 | 26.38 | 985.88 | 50.13 | 0.94 | 96.68 | 87.51 | 12130 | 11560 | -570 | 1.232 | 13 | 13 | 24 | 6.52 | 2.1 | 4.2 | 2 | 0
| 2018-06-29 | 84.5 | 72.3% | 76.5 | 89 | 82 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 12 | 6 | 3549 | 3426 | 3196 | 3163 | 3270 | 41 | 0 | 44 | 0 | 57 | 0 | 107 | -33 | 144 | 94.62% | 147.875 | 89.12% | 100% | 95.38% | 8.148 | 141.42 | 1152.2902 | 26.992 | 997.36 | 26920.7411 | 8875.4446 | 142.75 | 0 | 0 | 0 | 0 | 13 | 726 | 0 | 1001 | 1051 | 1218 | 50 | 8875.4446 | 50.75 | 1.221 | 1.217 | 27 | 25.76 | 21.4 | 24.48 | 985.46 | 50.14 | 0.9423 | 96.8 | 87.54 | 12102 | 11529 | -573 | 2.438 | 24 | 24 | 24 | 6.62 | 2.1 | 4.3 | 2.1 | 0
| 2018-06-30 | 84.3 | 79.6% | 79.2 | 92 | 78 | 20 | 4 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3552 | 2879 | 2759 | 2719 | 2814 | 41 | 218 | 44 | 0 | 57 | 0 | 95 | -40 | 131 | 89.5% | 148 | 76.55% | 95.63% | 82.76% | 9.06 | 147.07 | 1332.4542 | 23.048 | 985.41 | 22711.7297 | 8843.0246 | 119.9583 | 22 | 18 | 0 | 0 | 18 | 1440 | 0 | 832 | 1051 | 931 | 219 | 8843.0246 | 38.7917 | 0.101 | 0.253 | 27 | 21.98 | 21.57 | 26.04 | 984.67 | 50.13 | 0.9397 | 97.3 | 87.66 | 12327 | 11741 | -586 | 0.354 | 6.1 | 10.12 | 19.1 | 7.13 | 2.1 | 4.3 | 2.1 | 0
| 2018-07-01 | 92.27 | 70.5% | 81.91 | 101 | 84 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3468 | 2956 | 2956 | 2885 | 2982 | 41 | 0 | 43 | 0 | 57 | 0 | 97 | -71 | 126 | 98.61% | 144.5 | 83.19% | 100% | 88.65% | 9.05 | 153.34 | 1387.727 | 24.296 | 982.298 | 23865.9122 | 8753.4278 | 123.1667 | 0 | 0 | 0 | 0 | 16 | 1440 | 0 | 979 | 1030 | 973 | 51 | 8753.4278 | 40.5417 | 0 | 0 | 27 | 25.81 | 21.02 | 26.33 | 982 | 50.14 | 0.9411 | 97.15 | 87.77 | 12373 | 11751 | -622 | 0 | 0 | 0 | 24 | 7.7 | 2.1 | 4.3 | 2.1 | 0
Week 27 | 2018-07-02 | 96.75 | 59.86% | 79.5 | 104 | 89 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3431 | 2952 | 2952 | 2879 | 2975 | 41 | 0 | 43 | 0 | 57 | 0 | 96 | -73 | 126 | 98.38% | 142.9583 | 83.91% | 100% | 88.65% | 9.028 | 154.07 | 1390.944 | 23.804 | 997.269 | 23738.9913 | 8728.7028 | 123 | 0 | 0 | 0 | 0 | 16 | 1440 | 0 | 976 | 1027 | 972 | 51 | 8728.7028 | 40.5 | 0 | 0 | 27 | 25.143 | 20.5 | 26.12 | 977 | 50.16 | 0.9412 | 96.58 | 87.59 | 12089 | 11544 | -545 | 0 | 0 | 0 | 24 | 6.95 | 2.1 | 4.2 | 2 | 0
| 2018-07-03 | 93.17 | 59.4% | 76.41 | 99 | 84 | 17 | 16 | 18 | 36 | 1 | 58 | 0 | 0 | 0 | 0 | 3469 | 2989 | 2657 | 2614 | 2709 | 41 | 0 | 43 | 0 | 57 | 0 | 95 | -43 | 127 | 88.88% | 144.5417 | 75.35% | 100% | 82.39% | 9.025 | 151.68 | 1368.912 | 22.146 | 990.2009 | 21928.9891 | 8912.7395 | 124.5417 | 10 | 340 | 11 | 324 | 20 | 1440 | 0 | 848 | 976 | 885 | 128 | 8912.7395 | 36.875 | 0 | 0 | 27 | 22.52 | 19.93 | 26.06 | 977.42 | 50.17 | 0.9416 | 93.93 | 87.56 | 12485 | 11922 | -563 | 0 | 0 | 0 | 16.48 | 4.25 | 2.1 | 4.2 | 2 | 0
| 2018-07-04 | 82 | 74% | 74 | 89 | 74 | 12 | 33 | 24 | 0 | 10 | 48 | 0 | 0 | 0 | 0 | 3576 | 3040 | 2283 | 2244 | 2334 | 42 | 0 | 44 | 0 | 57 | 0 | 90 | -39 | 128 | 75.98% | 149 | 62.75% | 100% | 81.38% | 9.038 | 147.24 | 1330.7551 | 18.656 | 995.28 | 18567.9437 | 8867.5128 | 126.6667 | 23 | 39 | 0 | 0 | 26 | 1440 | 0 | 534 | 1061 | 739 | 527 | 8867.5128 | 30.7917 | 0 | 0 | 26.91 | 13.97 | 21.17 | 26.09 | 981.3 | 50.11 | 0.9405 | 96.04 | 87.36 | 12136 | 11437 | -699 | 0 | 0 | 0 | 11.72 | 6.27 | 2.1 | 4.3 | 2 | 0
| 2018-07-05 | 86.6 | 71.5% | 77.4 | 92 | 81 | 14 | 19 | 24 | 0 | 8 | 45 | 0 | 0 | 0 | 0 | 3531 | 3008 | 2480 | 2350 | 2441 | 41 | 0 | 44 | 0 | 57 | 0 | 91 | -130 | 127 | 80.09% | 147.125 | 66.55% | 100% | 81.9% | 9.032 | 149.35 | 1348.9292 | 19.718 | 996.1964 | 19643 | 8932.7358 | 125.3333 | 18 | 56 | 0 | 0 | 25 | 1440 | 0 | 611 | 1048 | 782 | 437 | 8932.7358 | 32.5833 | 0 | 0 | 27 | 15.89 | 21 | 25.9 | 983.9 | 50.11 | 0.9406 | 96.33 | 87.4 | 12042 | 11512 | -530 | 0 | 0 | 0 | 13.3 | 7.1 | 2.1 | 4..6 | 2.1 | 0
| 2018-07-06 | 91.5 | 60.2% | 76.4 | 100 | 81 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3481 | 3001 | 3001 | 2933 | 3030 | 41 | 0 | 44 | 0 | 57 | 0 | 97 | -68 | 129 | 97.87% | 145.0417 | 84.26% | 100% | 88.73% | 9.035 | 151.68 | 1370.4288 | 24.495 | 989.6714 | 24242 | 8732.5021 | 125.0417 | 0 | 0 | 0 | 0 | 16 | 1440 | 0 | 995 | 1046 | 989 | 51 | 8732.5021 | 41.2083 | 0 | 0 | 27 | 25.49 | 20.98 | 25.88 | 984.3 | 50.08 |  | 97 | 87.45 | 12030 | 11528 | -502 | 0 | 0 | 0 | 24 | 6.9 | 2.1 | 4.6 | 2.1 | 0
| 2018-07-07 | 95.5 | 60.4% | 79.6 | 105 | 85 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3441 | 2950 | 2950 | 2881 | 2975 | 40 | 0 | 43 | 0 | 57 | 0 | 94 | -69 | 126 | 98.38% | 143.375 | 83.73% | 100% | 88.57% | 9.04 | 150.62 | 1361.6048 | 24.179 | 986.5999 | 23855 | 8752.7264 | 122.9167 | 0 | 0 | 0 | 0 | 16 | 1440 | 0 | 973 | 1026 | 976 | 53 | 8752.7264 | 40.6667 | 0 | 0 | 25.2 | 25.16 | 20.78 | 25.65 | 981.8 | 50.08 |  | 96.28 | 87.56 | 12127 | 11635 | -492 | 0 | 0 | 0 | 24 | 6.5 | 2.1 | 4.6 | 2.1 | 0
| 2018-07-08 | 97.5 | 57.6% | 79.7 | 108 | 87 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3421 | 2937 | 2937 | 2870 | 2969 | 40 | 0 | 43 | 0 | 57 | 0 | 99 | -67 | 125 | 98.97% | 142.5417 | 83.89% | 100% | 88.57% | 9.029 | 151 | 1363.379 | 24.025 | 986.44 | 23699.221 | 8732.6132 | 122.375 | 0 | 0 | 0 | 0 | 16 | 1440 | 0 | 970 | 1026 | 973 | 56 | 8732.6132 | 40.5417 | 0 | 0 | 25 | 25.01 | 20.71 | 25.53 | 979.88 | 50.09 | 0.9424 | 96.06 | 87.54 | 12105 | 11609 | -496 | 0 | 0 | 0 | 24 | 6.62 | 2.1 | 4.6 | 2.2 | 0
Week 28 | 2018-07-09 | 96.9 | 54.1% | 77 | 106 | 88 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3426 | 2964 | 2964 | 2888 | 2986 | 41 | 0 | 43 | 0 | 57 | 0 | 98 | -76 | 126 | 98.74% | 142.75 | 84.3% | 100% | 88.65% | 8.728 | 152.46 | 1330.6709 | 24.184 | 988.7942 | 23912.9989 | 8740.8829 | 123.5 | 0 | 0 | 0 | 0 | 16 | 1440 | 0 | 977 | 1029 | 980 | 52 | 8740.8829 | 40.8333 | 0 | 0 | 25 | 25.13 | 20.8 | 25.26 | 978.92 | 50.09 | 0.9426 | 95.92 | 87.44 | 12067 | 11577 | -490 | 0 | 0 | 0 | 24 | 6.52 | 2.2 | 4.6 | 2.1 | 0
| 2018-07-10 | 97.8 | 55.1% | 77.8 | 108 | 88 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3420 | 2946 | 2946 | 2875 | 2974 | 41 | 0 | 43 | 0 | 57 | 0 | 99 | -71 | 125 | 99.13% | 142.5 | 84.06% | 100% | 88.65% | 8.653 | 155.27 | 1343.5513 | 24.138 | 985.21 | 23780.999 | 8738.974 | 122.75 | 0 | 0 | 0 | 0 | 16 | 1440 | 0 | 973 | 1026 | 975 | 53 | 8738.974 | 40.625 | 0 | 0 | 25 | 25.04 | 20.75 | 24.49 | 979.79 | 50.1 | 0.9417 | 96.04 | 87.51 | 12073 | 11552 | -521 | 0 | 0 | 0 | 24 | 6.9 | 2.2 | 4.5 | 2.1 | 0
| 2018-07-11 | 97 | 54.7% | 77.3 | 106 | 91 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3427 | 2955 | 2955 | 2880 | 2983 | 41 | 0 | 43 | 0 | 57 | 0 | 103 | -75 | 126 | 98.64% | 142.7917 | 84.04% | 100% | 88.65% | 8.622 | 155.72 | 1342.6178 | 24.051 | 989.3144 | 23794 | 8727.9923 | 123.125 | 0 | 0 | 0 | 0 | 16 | 1440 | 0 | 975 | 1031 | 977 | 56 | 8727.9923 | 40.7083 | 0 | 0 | 25 | 25.02 | 20.74 | 24.95 | 978.54 | 50.11 | 0.9417 | 95.9 | 87.48 | 12052 | 11520 | -532 | 0 | 0 | 0 | 24 | 6.47 | 2.2 | 4.6 | 2.1 | 0
| 2018-07-12 | 95.6 | 59.1% | 79.3 | 104 | 89 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3441 | 2933 | 2933 | 2869 | 2970 | 41 | 0 | 43 | 0 | 57 | 0 | 101 | -64 | 125 | 99% | 143.375 | 83.38% | 100% | 87.94% | 8.557 | 156.16 | 1336.2611 | 24.039 | 984.46 | 23665.4339 | 8714.4284 | 122.2083 | 0 | 0 | 0 | 0 | 17 | 1440 | 0 | 969 | 1027 | 974 | 58 | 8714.4284 | 40.5833 | 0 | 0 | 24.9 | 25.08 | 20.75 | 24.76 | 977.8 | 50.12 | 0.9419 | 96 | 87.5 | 12119 | 11565 | -554 | 0 | 0 | 0 | 24 | 6.8 | 2.2 | 4.7 | 2.1 | 0
| 2018-07-13 | 97.2 | 58% | 78.8 | 106 | 89 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3424 | 2930 | 2930 | 2857 | 2961 | 40 | 0 | 43 | 0 | 57 | 0 | 104 | -73 | 125 | 98.7% | 142.6667 | 83.44% | 100% | 88.57% | 8.562 | 155.05 | 1327.5381 | 23.93 | 988.4246 | 23653 | 8743.6255 | 122.0833 | 0 | 0 | 0 | 0 | 16 | 1440 | 0 | 967 | 1022 | 972 | 55 | 8743.6255 | 40.5 | 0 | 0 | 24.5 | 24.89 | 20.66 | 24.5 | 978.58 | 50.07 | 0.9427 | 95.44 | 87.53 | 12105 | 11563 | -542 | 0 | 0 | 0 | 24 | 7 | 2.1 | 4.6 | 2.1 | 0
| 2018-07-14 | 96.4 | 61% | 80.8 | 105 | 88 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3435 | 2908 | 2908 | 2840 | 2940 | 40 | 0 | 42 | 0 | 57 | 0 | 100 | -68 | 124 | 98.79% | 143.125 | 82.68% | 100% | 87.77% | 8.477 | 157.46 | 1334.7884 | 23.872 | 983.302 | 23473.3853 | 8735.2725 | 121.1667 | 0 | 0 | 0 | 0 | 17 | 1440 | 0 | 960 | 1014 | 966 | 54 | 8735.2725 | 40.25 | 0 | 0 | 24.5 | 24.83 | 20.54 | 24.69 | 979.1 | 50.02 | 0.9427 | 95.57 | 87.61 | 12144 | 11607 | -537 | 0 | 0 | 0 | 24 | 6.48 | 2.1 | 4.7 | 2.2 | 0
| 2018-07-15 | 95.93 | 62.1% | 80 | 102 | 88 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3438 | 2907 | 2907 | 2834 | 2935 | 40 | 0 | 42 | 0 | 57 | 0 | 101 | -73 | 123 | 99.42% | 143.25 | 82.43% | 100% | 87.77% | 8 | 157.52 | 1260.16 | 23.875 | 985.005 | 23516.9944 | 8742.8209 | 121.125 | 0 | 0 | 0 | 0 | 17 | 1440 | 0 | 957 | 1013 | 965 | 56 | 8742.8209 | 40.2083 | 0 | 0 | 24.5 | 24.81 | 20.53 | 24.42 | 978.7 | 50.02 | 0.9525 | 95.57 | 87.63 | 12151 | 11604 | -547 | 0 | 0 | 0 | 24 | 6.62 | 2.1 | 4.7 | 2.1 | 0
Week 29 | 2018-07-16 | 94.14 | 64.44% | 80.5 | 105 | 88 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3456 | 2927 | 2927 | 2854 | 2956 | 40 | 0 | 43 | 0 | 57 | 0 | 102 | -73 | 126 | 97.75% | 144 | 82.58% | 100% | 87.86% | 8.38 | 155.56 | 1303.5928 | 23.9942 | 984.12 | 23613.2115 | 8730.485 | 121.9583 | 0 | 0 | 0 | 0 | 17 | 1440 | 0 | 964 | 1022 | 970 | 58 | 8730.485 | 40.4167 | 0 | 0 | 24.5 | 24.94 | 20.71 | 24.39 | 978.8 | 50.11 | 0.9428 | 95.56 | 87.57 | 12142 | 11577 | -565 | 0 | 0 | 0 | 24 | 6.58 | 2.1 | 4.8 | 2.1 | 0
| 2018-07-17 | 91.7 | 67% | 80 | 100 | 85 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3478 | 2947 | 2947 | 2873 | 2974 | 40 | 0 | 43 | 0 | 57 | 0 | 101 | -74 | 126 | 98.35% | 144.9167 | 82.6% | 100% | 87.86% | 8.037 | 152.76 | 1227.7321 | 24.092 | 990.08 | 23852.9786 | 8729.7984 | 122.7917 | 0 | 0 | 0 | 0 | 17 | 1440 | 0 | 970 | 1027 | 977 | 57 | 8729.7984 | 40.7083 | 0 | 0 | 24.5 | 25.01 | 20.77 | 24.54 | 980.8 | 50.15 | 0.918 | 95.53 | 87.55 | 12102 | 11536 | -566 | 0 | 0 | 0 | 24 | 7.3 | 2.2 | 4.8 | 2 | 0
| 2018-07-18 | 93.9 | 64.5% | 81 | 103 | 87 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3459 | 2929 | 2929 | 2855 | 2956 | 40 | 0 | 43 | 0 | 57 | 0 | 101 | -74 | 125 | 98.53% | 144.125 | 82.54% | 100% | 87.86% | 8.023 | 155.46 | 1247.2556 | 24.0853 | 982.354 | 23660.2702 | 8724.1771 | 122.0417 | 0 | 0 | 0 | 0 | 17 | 1440 | 0 | 964 | 1020 | 972 | 56 | 8724.1771 | 40.5 | 0 | 0 | 24.4 | 25.07 | 20.83 | 24.22 | 981.6 | 50.12 | 0.9429 | 95.47 | 87.56 | 12203 | 11647 | -556 | 0 | 0 | 0 | 24 | 6.6 | 2.1 | 4.7 | 2.1 | 0
| 2018-07-19 | 90.8 | 68.8% | 80.4 | 103 | 81 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3490 | 2941 | 2941 | 2867 | 2969 | 40 | 0 | 43 | 0 | 57 | 0 | 102 | -74 | 126 | 98.18% | 145.4167 | 82.15% | 100% | 88.57% | 7.899 | 152.31 | 1203.0967 | 24.1453 | 984.18 | 23763.282 | 8708.1893 | 122.5417 | 0 | 0 | 0 | 0 | 16 | 1440 | 0 | 968 | 1026 | 975 | 58 | 8708.1893 | 40.625 | 0 | 0 | 24 | 25.06 | 20.83 | 24.68 | 980.8 | 50.11 | 0.9428 | 95.48 | 87.55 | 12150 | 11586 | -564 | 0 | 0 | 0 | 24 | 7.2 | 2.1 | 4.7 | 2.1 | 0
| 2018-07-20 | 90.6 | 71.7% | 81.9 | 101 | 85 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3492 | 2931 | 2931 | 2860 | 2961 | 40 | 0 | 43 | 0 | 57 | 0 | 101 | -71 | 125 | 98.7% | 145.5 | 81.9% | 100% | 88.57% | 7.801 | 152.66 | 1190.9007 | 24.0336 | 984.5629 | 23662.6311 | 8690.0461 | 122.125 | 0 | 0 | 0 | 0 | 16 | 1440 | 0 | 965 | 1024 | 972 | 59 | 8690.0461 | 40.5 | 0 | 0 | 24 | 24.96 | 20.75 | 24.3 | 980 | 50.11 | 0.9418 | 95.62 | 87.6 | 12149 | 11576 | -573 | 0 | 0 | 0 | 24 | 6.43 | 2.1 | 4.7 | 2.1 | 0
| 2018-07-21 | 94 | 66% | 81 | 103 | 85 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3460 | 2915 | 2915 | 2845 | 2944 | 40 | 0 | 42 | 0 | 57 | 0 | 99 | -70 | 125 | 98.13% | 144.1667 | 82.23% | 100% | 87.77% | 7.829 | 160.25 | 1254.5973 | 23.9018 | 987.7411 | 23608.7507 | 8739.3139 | 121.4583 | 0 | 0 | 0 | 0 | 17 | 1440 | 0 | 959 | 1016 | 969 | 57 | 8739.3139 | 40.375 | 0 | 0 | 24 | 24.78 | 20.6 | 24.16 | 980 | 50.09 | 0.9419 | 95.56 | 87.59 | 12122 | 11575 | -547 | 0 | 0 | 0 | 24 | 6.48 | 2 | 4.7 | 2.1 | 0
| 2018-07-22 | 93.2 | 65.3% | 79.6 | 101 | 85 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3466 | 2931 | 2931 | 2859 | 2958 | 40 | 0 | 43 | 0 | 57 | 0 | 99 | -72 | 126 | 97.82% | 144.4167 | 82.49% | 100% | 88.57% | 7.858 | 155.28 | 1220.1902 | 24.0777 | 985.422 | 23726.7347 | 8725.752 | 122.125 | 0 | 0 | 0 | 0 | 16 | 1440 | 0 | 964 | 1021 | 973 | 57 | 8725.752 | 40.5417 | 0 | 0 | 24 | 24.98 | 20.86 | 24.32 | 980.33 | 50.1 | 0.9421 | 95.41 | 87.53 | 12169 | 11631 | -538 | 0 | 0 | 0 | 24 | 6.47 | 2.1 | 4.7 | 2.1 | 0
Week 30 | 2018-07-23 | 92.4 | 67.8% | 80.7 | 99 | 84 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3472 | 2919 | 2919 | 2849 | 2952 | 40 | 0 | 42 | 0 | 57 | 0 | 103 | -70 | 125 | 98.4% | 144.6667 | 82.06% | 100% | 87.77% | 7.821 | 157 | 1227.897 | 24.1357 | 981.97 | 23700.5628 | 8749.8981 | 121.625 | 0 | 0 | 0 | 0 | 17 | 1440 | 0 | 960 | 1022 | 970 | 62 | 8749.8981 | 40.4167 | 0 | 0 | 24 | 24.89 | 20.73 | 24.56 | 980.9 | 50.11 | 0.9427 | 95.39 | 87.57 | 12163 | 11613 | -550 | 0 | 0 | 0 | 24 | 6.4 | 2.2 | 4.7 | 2.1 | 0
| 2018-07-24 | 95.7 | 62.6% | 80.8 | 104 | 87 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3442 | 2910 | 2910 | 2837 | 2941 | 40 | 0 | 42 | 0 | 57 | 0 | 104 | -73 | 124 | 98.82% | 143.4167 | 82.42% | 100% | 87.77% | 7.784 | 155.77 | 1212.5137 | 24.0186 | 981.4588 | 23573.286 | 8736.6231 | 121.25 | 0 | 0 | 0 | 0 | 17 | 1440 | 0 | 956 | 1016 | 969 | 60 | 8736.6231 | 40.375 | 0 | 0 | 24 | 24.77 | 20.64 | 24.54 | 981.67 | 50.07 | 0.9434 | 95.19 | 87.55 | 12159 | 11617 | -542 | 0 | 0 | 0 | 24 | 6.4 | 2.1 | 4.8 | 2.1 | 0
| 2018-07-25 | 96.2 | 63.5% | 81.3 | 103 | 91 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3433 | 2909 | 2909 | 2839 | 2939 | 40 | 0 | 42 | 0 | 57 | 0 | 100 | -70 | 124 | 98.76% | 143.0417 | 82.7% | 100% | 87.77% | 7.808 | 156.76 | 1223.9821 | 23.9861 | 984.0833 | 23604.33 | 8745.4428 | 121.2083 | 0 | 0 | 0 | 0 | 17 | 1440 | 0 | 954 | 1018 | 967 | 64 | 8745.4428 | 40.2917 | 0 | 0 | 24 | 24.82 | 20.72 | 24.34 | 979.21 | 50.16 | 0.9303 | 95.11 | 87.55 | 12198 | 11629 | -569 | 0 | 0 | 0 | 24 | 6.53 | 2.1 | 4.7 | 2.1 | 0
| 2018-07-26 | 94.1 | 59.9% | 77.3 | 100 | 90 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3454 | 2943 | 2943 | 2872 | 2975 | 40 | 0 | 43 | 0 | 57 | 0 | 103 | -71 | 125 | 99.17% | 143.9167 | 83.15% | 100% | 88.57% | 7.765 | 154.18 | 1197.2077 | 24.2404 | 979.9933 | 23755.47 | 8688.2583 | 122.625 | 0 | 0 | 0 | 0 | 16 | 1440 | 0 | 967 | 1029 | 979 | 62 | 8688.2583 | 40.7917 | 0 | 0 | 24 | 25.1 | 21.03 | 24.09 | 980.46 | 50.18 | 0.9428 | 94.83 | 87.39 | 12189 | 11608 | -581 | 0 | 0 | 0 | 24 | 6.67 | 2.1 | 4.7 | 2.1 | 0
| 2018-07-27 | 94.07 | 61.96% | 78.12 | 102 | 88 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3450 | 2933 | 2933 | 2862 | 2964 | 40 | 0 | 43 | 0 | 57 | 0 | 102 | -71 | 125 | 98.8% | 143.75 | 82.96% | 100% | 88.57% | 7.78 | 157.52 | 1225.5056 | 24.2259 | 981.0912 | 23767.8279 | 8732.8209 | 122.2083 | 0 | 0 | 0 | 0 | 16 | 1440 | 0 | 963 | 1026 | 975 | 63 | 8732.8209 | 40.625 | 0 | 0 | 24 | 25.07 | 20.95 | 24.065 | 981.46 | 50.14 | 0.9426 | 94.93 | 87.4 | 12218 | 11625 | -593 | 0 | 0 | 0 | 24 | 6.47 | 2.1 | 4.7 | 2.1 | 0
| 2018-07-28 | 92.4 | 65.83% | 80.5 | 98 | 87 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3475 | 2934 | 2934 | 2861 | 2961 | 40 | 0 | 43 | 0 | 57 | 0 | 100 | -73 | 125 | 98.7% | 144.7917 | 82.33% | 100% | 88.57% | 7.777 | 154.27 | 1199.7578 | 24.2813 | 976.3944 | 23708.0864 | 8705.9924 | 122.25 | 0 | 0 | 0 | 0 | 16 | 1440 | 0 | 962 | 1024 | 975 | 62 | 8705.9924 | 40.625 | 0 | 0 | 24 | 25.16 | 24.04 | 24.24 | 981.8 | 50.14 | 0.943 | 95.04 | 87.45 | 12270 | 11684 | -586 | 0 | 0 | 0 | 24 | 6.4 | 2.1 | 4.65 | 2.1 | 0
| 2018-07-29 | 93.6 | 66.6% | 81 | 101 | 88 | 24 | 0 | 24 | 0 |  | 0 | 0 | 0 | 0 | 0 | 3463 | 2918 | 2918 | 2843 | 2944 | 40 | 0 | 42 | 0 | 57 | 0 | 101 | -75 | 125 | 98.13% | 144.2917 | 82.1% | 100% | 87.77% | 7.773 | 156.73 | 1218.2623 | 24.1265 | 977.2495 | 23577.56 | 8721.7103 | 121.5833 | 0 | 0 | 0 | 0 | 17 | 1440 | 0 | 956 | 1018 | 970 | 62 | 8721.7103 | 40.4167 | 0 | 0 | 24 | 25.01 | 20.92 | 24.19 | 982.6 | 50.11 | 0.9434 | 95.2 | 87.46 | 12276 | 11708 | -568 | 0 | 0 | 0 | 24 | 6.8 | 2.2 | 4.7 | 2.1 | 0
Week 31 | 2018-07-30 | 94.5 | 65.5% | 80.6 | 104 | 86 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3449 | 2917 | 2917 | 2843 | 2945 | 40 | 0 | 42 | 0 | 57 | 0 | 102 | -74 | 124 | 98.96% | 143.7083 | 82.43% | 100% | 87.77% | 6.155 | 159.41 | 981.1685 | 24.0249 | 981.5146 | 23580.75 | 8639.4367 | 121.5417 | 0 | 0 | 0 | 0 | 17 | 1440 | 0 | 957 | 1017 | 971 | 60 | 8639.4367 | 40.4583 | 0 | 0 | 24 | 24.88 | 20.82 | 24.3 | 981.9 | 50.11 | 0.9447 | 95.1 | 87.4 | 12208 | 11651 | -557 | 0 | 0 | 0 | 24 | 6.6 | 2.1 | 4.6 | 2.1 | 0
| 2018-07-31 | 94.1 | 63.7% | 79.8 | 102 | 87 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3459 | 2919 | 2919 | 2853 | 2955 | 40 | 0 | 43 | 0 | 57 | 0 | 102 | -66 | 125 | 98.5% | 144.125 | 82.48% | 100% | 88.57% | 7.781 | 159.35 | 1239.9023 | 23.8551 | 984.968 | 23496.52 | 8670.3198 | 121.625 | 0 | 0 | 0 | 0 | 16 | 1440 | 0 | 957 | 1025 | 973 | 68 | 8670.3198 | 40.5417 | 0 | 0 | 24 | 24.76 | 20.54 | 26.17 | 980.6 | 50.12 | 0.9418 | 94.96 | 87.36 | 12130 | 11596 | -534 | 0 | 0 | 0 | 24 | 6.1 | 2.1 | 4.7 | 2.1 | 0
2018-08-01
2018-08-02
2018-08-03
2018-08-04
| 2018-08-05 |  |  |  | CT2 min: 0 | [15 empty] | no data | no data | no data | no data | [6 empty] | no data | no data | [10 empty] | 0 | no data | [14 empty] | 0
| Monthly | 93.7913 | 63.31% | 7937% | 102.0645 | 86.129 | 716 | 8 | 738 | 36 | 19 | 31 | 0 | 0 | 0 | 0 | 107227 | 91199 | 89582 | 87564.37 | 90458 | 40.4333 | 218 | 42.9667 | 0 | 57 | 0 | 2893.63 | -2069 | 126.3333 | 96.46% | 144.3847 | 81.52% | 99.85% | 87.7% | 256.147 | 154.6416 | 39571.8299 | 734.6324 | 985.6661 | 723990.1207 | 8720.0074 | 122.5793 | 73 | 453 | 11 | 324 | 512 | 42486 | 0 | 28013 | 30795 | 28890 | 2782 | 8720.0074 | 40.125 | 1.322 | 1.47 | 25.097 | 24.2048 | 20.9097 | 24.9198 | 980.5663 | 50.111 | 0.94115 | 95.7677 | 87.533 | 12158.7 | 11603.3333 |  | 0 | 0 | 0 | 713.5 | 204.51
| Totals | Avg.F | % Avg. |  | M Avg | m Avg | hrs | min | hrs | min | hrs | min | hrs | min | hrs | min | MWhr Total | MWhr Total | MWhr Total | MWhr Total | MWhr Total | MW Avg | Total min | Avg MW | Total min | Avg MW | Total min | MWhr | Total MW | Av Max D/Gen | Av. DailyLF | Avg. | Avg. |  | Avg. | Total | Avg. |  | Total | Avg. |  | Avg. | [7 empty] | Total |  |  |  |  | Avg.
| Weeks data | Site Avg. Amb. Temp F | Site Avg. Relative humidity % |  | M Avg: Site Maximum/Minumum Temperature; hrs: CT-1 Base Load Hours; hrs: CT-2 Base Load Hours; hrs: CT-1 stand by hours / min; hrs: CT-2 standby hours / min; hrs: Plant ambient Corrected maximum Load hours/min | Average Corrected Plant Capacity | Ambient Corrected Declared Avail'y (MWH) | Av Plant WAPDA Dispatch | Net Plant Export (MWH) | Gross Generation | CT1 Av Cap (MW) | CT1 Unavail minutes | CT2 Av Cap (MW) | CT2 Unavail minutes | ST Unavail minutes | ST Average Cap (MW) | Plant Aux Load including Colony Load MWH | Differenece (+/-) MW | Maximum Daily Generation | Daily Load Factor | Avg. Corrected Plant | Plant Capacity Facto | Plant Availability Factor | Equivalent Plant Availability | LBtu gas flow mmscf | 1 LBtu gas (Average Btu/scf) | LBTU MMBTU | PL gas flow (mscf/week) | 1 PL gas (Average Btu/scf) | HBTU MMBTU | Plant Net Heat Rate (Btu/Kwh) | [11 empty] | 57.5
| Week 26 | 90.11 | 64 | 76.5871 | 97.8571 | 82.5714 | 164 | 4 | 168 | 0 | 0 | 0 | 0 | 0 | 65 | 52 | 3493.4286 | 3140.8571 | 3073.7143 | 21128 | 21851 | 41 | 218 | 43.8571 | No outage | No outage | 57 | no data | -388 | 138.4286 | 93.98% | 145.5595 | 86.43% | 99.38% | 91.76% | 62.529 | 150.09 | 9384.9776 | 178.798 | 989.2487 | 176875.6916 | 8817.1581
| Week 27 | 91.86 | 63.28% | 77.5729 | 99.5714 | 83 | 140 | 66 | 162 | 36 | 21 | 151 | 0 | 0 | 0 | 52 | 3478.5714 | 2982.4286 | 2751.4286 | 18771 | 19433 | 40.8571 | No outage | 43.4286 | No outage | No outage | 57 | 662 | -489 | 126.8571 | 91.22% | 144.9405 | 77.21% | 100% | 85.74% | 63.227 | 150.8057 | 9534.9929 | 157.023 | 991.6654 | 155714.271 | 8808.5047
| Week 28 | 96.69 | 57.73% | 78.7143 | 105.2857 | 88.7143 | 168 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3430.1429 | 2934.7143 | 2934.7143 | 20043 | 20749 | 40.5714 | No outage | 42.7143 | No outage | No outage | 57 | 706 | -500 | 124.8571 | 98.92% | 142.9226 | 83.48% | 100% | 88.29% | 59.599 | 155.6629 | 9277.3506 | 144.214 | 986.5842 | 142279.2525 | 8734.8566
| Week 29 | 92.62 | 0.6682 | 80.6286 | 102.2857 | 85.1429 | 168 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3471.5714 | 2931.5714 | 2931.5714 | 20013 | 20718 | 40 | No outage | 42.8571 | No outage | 399 | 57 | 705 | -508 | 125.5714 | 98.21% | 144.6488 | 82.36% | 100% | 88.15% | 55.827 | 154.8971 | 8647.4428 | 168.3299 | 985.4943 | 165888.1455 | 8721.1088
| Week 30 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Date | Plant Status Whether Normal Operation or Tripping (State full detail for trippings/return to normal).
| 2018-07-01 | Plant load restricted 118~122 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-07-02 | Plant load restricted 118~122 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-07-03 | Plant load remained 90 MW from 0230~0757 hrs at NPCC demand. Plant load restricted 119~123 MW from 0757~2146 hrs to remain within contractual heatrate. CT-1 desynch at 2202 hrs to meet NPCC load demand of 61 MW.
| 2018-07-04 | Plant load remained 61 MW from 0000~1010 hrs at NPCC demand. CT-1 synch at 1048 hrs after receiving NPCC maximum load demand. Plant load increased but restricted to 119~123 MW from 1135~2400 hrs to remain within contractual heatrate.
| 2018-07-05 | CT-1 de-synch at 0109 hrs and again synch at 0954 hrs after receiving NPCC maximum load demand. Plant load restricted 119~123 MW from 1100~2400 hrs as both DBs kept off to remain within contractual heatrate
| 2018-07-06 | Plant load restricted 121~125 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-07-07 | Plant load restricted 118~122 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-07-08 | Plant load restricted 118~121 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-07-09 | Plant load restricted 118~121 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-07-10 | Plant load restricted 118~121 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-07-11 | Plant load restricted 119~121 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-07-12 | Plant load restricted 118~121 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-07-13 | Plant load restricted 117~120 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-07-14 | Plant load restricted 117~120 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-07-15 | Plant load restricted 117~120 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-07-16 | Plant load restricted 117~120 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-07-17 | Plant load restricted 118~121 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-07-18 | Plant load restricted 118~121 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-07-19 | Plant load restricted 117~121 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-07-20 | Plant load restricted 117~121 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-07-21 | Plant load restricted 117~120 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-07-22 | Plant load restricted 117~122 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-07-23 | Plant load restricted 117~121 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-07-24 | Plant load restricted 117~120 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-07-25 | Plant load restricted 117~120 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-07-26 | Plant load restricted 119~121 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-07-27 | Plant load restricted 118~121 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-07-28 | Plant load restricted 118~121 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-07-29 | Plant load restricted 117~120 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-07-30 | Plant load restricted 117~120 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-07-31 | Plant load restricted 118~120 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate. LBTU well NP-1 injected by OGDCL and flow increased from 7.8 to 10 mmscfd.
0.88333
0.1
0.1

## Aug
2018-08-01
| Date | Site Avg. Ambient Temp.F | Site Avg. Relative Humidty % | Site Avg. Ambient Wetbulb Temp.F | Site Ambient Temp |  | Base load hours |  |  |  | Standby hours |  |  |  | Plant ambient corrected Max Load |  | Corrected Plant Capacity | Ambient Corrected Daclared Avail'y (MWH) | Plant WAPDA Dispatch (MWH) | Net Plant Export (MWH) | Gross Generation | CT1 Average Cap (MW) | CT1 Unavail minutes | CT2 Average Cap (MW) | CT2 Unavail minutes | ST Average Cap (MW) | ST Unavail minutes | Plant Aux Load including Colony Load MWH | Differenece (+/-) MW | Maximum Daily Generation | Daily Load Factor | Avg. Corrected Plant Capacity | Plant Capacity Factor | Plant Availability Factor | Equivalent Plant Availability | LBtu gas flow (mmscf/day) | 1 LBtu gas (Average Btu/scf) | LBTU MMBTU | 1 HBtu gas flow (mmscf/day) | 1 HBtu gas (Average Btu/scf) | HBTU MMBTU | HHV Net Heat Rate (Btu/Kwh) | Avg. declared availability | CT1 Derated MW | CT1 derated mintutes | CT-2 derated MW | CT-2 derated mintutes | ST derated MW | ST derated mintutes | WAPDA Backfeed (MWH) |  | CT-1 Gross Generation (MWH) | CT-2 Gross Generation (MWH) | STG Gross Generation (MWH) | CT-1 & CT-2 MWH difference | Base load Heat Rate | STG load | DB1 | DB2 | CT1 | CT1 Gas flow | CT2 Gas flow |  | Pamb | Freq. Hz | LBTU Gas Specific gravity | CT-1 compressor efficiency(%) | CT-2 compressor efficiency(%) | CT-1 Heat Rate (Btu/Kwh) | CT-2 Heat Rate (Btu/Kwh) |  | DB(1+2) | DB-1 Ops Hours | DB-2 Ops Hours | CT-1 Wetcomprssion Ops Hours | RO Operation Hours | CT1 T/G Brg |  | CT2 T/G Brg
[7 empty] | CT1 |  | CT2 |  | CT1 |  | CT2 | [44 empty] | mmscf/d | mmscf/d | WetC flow | HBTU KPPH | HBTU KPPH | LBTU KPPH | mbar | Hz | [6 empty] | mmscf/d |  |  |  |  | Supply air pressure | Seal air pressure | Supply air pressure | Seal air pressure
[5 empty] | Max | Min | hrs | min | hrs | min | hrs | min | hrs | min | hrs | min | [43 empty] | gpm | [16 empty] | Psi | "WC | Psi | "WC
Week 31 | 2018-07-30 | 94.5 | 65.5% | 80.6 | 104 | 86 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3449 | 2917 | 2917 | 2843 | 2945 | 40 | 0 | 42 | 0 | 57 | 0 | 102 | -74 | 124 | 98.96% | 143.7083 | 82.43% | 100% | 87.77% | 7.781 | 159.41 | 1240.3692 | 24.024 | 981.52 | 23580.0365 | 8730.3573 | 121.5417 | 0 | 0 | 0 | 0 | 17 | 1440 | 0 |  | 957 | 1017 | 971 | 60 | 8730.3573 | 40.4583 | 0 | 0 | 24 | 24.88 | 20.82 | 24.3 | 981.9 | 50.11 | 0.9447 | 95.1 | 87.4 | 12208 | 11651 | -557 | 0 | 0 | 0 | 24 | 6.6 | 2.1 | 4.6 | 2.1 | 0
| 2018-07-31 | 94.1 | 63.7% | 79.8 | 102 | 87 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3459 | 2919 | 2919 | 2853 | 2955 | 40 | 0 | 43 | 0 | 57 | 0 | 102 | -66 | 125 | 98.5% | 144.125 | 82.48% | 100% | 88.57% | 8.46 | 159.35 | 1348.101 | 23.85 | 984.2 | 23473.17 | 8700.0599 | 121.625 | 0 | 0 | 0 | 0 | 16 | 1440 | 0 |  | 957 | 1025 | 973 | 68 | 8700.0599 | 40.5417 | 0 | 0 | 24 | 24.76 | 20.54 | 26.17 | 980.6 | 50.12 | 0.9418 | 94.96 | 87.36 | 12130 | 11596 | -534 | 0 | 0 | 0 | 24 | 6.1 | 2.1 | 4.7 | 2.1 | 0
| 2018-08-01 | 93.2 | 65.1% | 78.3 | 100 | 88 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3467 | 2944 | 2944 | 2873 | 2975 | 40 | 0 | 43 | 0 | 57 | 0 | 102 | -71 | 125 | 99.17% | 144.4583 | 82.87% | 100% | 88.57% | 9.852 | 170.14 | 1676.2193 | 23.5388 | 990.5726 | 23316.92 | 8699.3175 | 122.6667 | 0 | 0 | 0 | 0 | 16 | 1440 | 0 |  | 962 | 1038 | 975 | 76 | 8699.3175 | 40.625 | 0 | 0 | 24 | 24.68 | 19.88 | 30.59 | 980.42 | 50.16 | 0.9348 | 94.88 | 87.34 | 12031 | 11459 | -572 | 0 | 0 | 0 | 24 | 6.48 | 2.1 | 4.7 | 2.1 | 0
| 2018-08-02 | 93.1 | 64.1% | 78 | 100 | 88 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3464 | 2955 | 2955 | 2882 | 2986 | 40 | 0 | 43 | 0 | 57 | 0 | 104 | -73 | 126 | 98.74% | 144.3333 | 83.2% | 100% | 88.57% | 9.872 | 173.54 | 1713.1869 | 23.6515 | 989.0907 | 23393.449 | 8711.5322 | 123.125 | 0 | 0 | 0 | 0 | 16 | 1440 | 0 |  | 965 | 1041 | 980 | 76 | 8711.5322 | 40.8333 | 0 | 0 | 24 | 24.83 | 20.08 | 30.38 | 982.6 | 50.18 | 0.9328 | 94.85 | 87.32 | 12074 | 11499 | -575 | 0 | 0 | 0 | 24 | 6.65 | 2.1 | 4.5 | 2.1 | 0
| 2018-08-03 | 92.1 | 65.7% | 78.5 | 99 | 85 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3479 | 2956 | 2956 | 2886 | 2986 | 40 | 0 | 43 | 0 | 57 | 0 | 100 | -70 | 126 | 98.74% | 144.9583 | 82.95% | 100% | 88.57% | 9.859 | 175.22 | 1727.494 | 23.5826 | 990.6741 | 23362.67 | 8693.7505 | 123.1667 | 0 | 0 | 0 | 0 | 16 | 1440 | 0 |  | 966 | 1040 | 980 | 74 | 8693.7505 | 40.8333 | 0 | 0 | 24 | 24.77 | 20.48 | 30.4 | 983 | 50.16 | 0.9319 | 94.89 | 87.31 | 12045 | 11649 | -396 | 0 | 0 | 0 | 24 | 6.4 | 2.1 | 4.5 | 2.2 | 0
| 2018-08-04 | 92.1 | 64.8% | 77.9 | 98 | 87 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3476 | 2957 | 2957 | 2887 | 2985 | 40 | 0 | 43 | 0 | 57 | 0 | 98 | -70 | 126 | 98.71% | 144.8333 | 83.06% | 100% | 88.57% | 9.989 | 179.51 | 1793.1254 | 23.6341 | 988.3347 | 23358.4 | 8711.9936 | 123.2083 | 0 | 0 | 0 | 0 | 16 | 1440 | 0 |  | 965 | 1040 | 980 | 75 | 8711.9936 | 40.8333 | 0 | 0 | 24 | 24.91 | 20.61 | 30.64 | 982.17 | 50.13 | 0.9311 | 94.98 | 87.31 | 12119 | 11722 | -397 | 0 | 0 | 0 | 23.95 | 6.63 | 2.1 | 4.6 | 2.1 | 0
| 2018-08-05 | 93.2 | 64.7% | 79.1 | 100 | 87 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3467 | 2944 | 2944 | 2873 | 2970 | 40 | 0 | 43 | 0 | 57 | 0 | 97 | -71 | 126 | 98.21% | 144.4583 | 82.87% | 100% | 88.57% | 9.98 | 181.1 | 1807.378 | 23.4798 | 988.1736 | 23202.08 | 8704.9976 | 122.6667 | 0 | 0 | 0 | 0 | 16 | 1440 | 0 |  | 961 | 1033 | 976 | 72 | 8704.9976 | 40.6667 | 0 | 0 | 24 | 24.8 | 20.54 | 30.47 | 981.29 | 50.09 | 0.9313 | 95.22 | 87.33 | 12113 | 11762 | -351 | 0 | 0 | 0 | 24 | 6.35 | 2.1 | 4.6 | 2.1 | 0
Week 32 | 2018-08-06 | 92.4 | 64.5% | 77.5 | 100 | 87 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3476 | 2949 | 2949 | 2877 | 2977 | 40 | 0 | 43 | 0 | 57 | 0 | 100 | -72 | 126 | 98.45% | 144.8333 | 82.77% | 100% | 88.57% | 9.972 | 183.24 | 1827.2693 | 23.6339 | 985.5251 | 23291.811 | 8730.9977 | 122.875 | 0 | 0 | 0 | 0 | 16 | 1440 | 0 |  | 962 | 1036 | 979 | 74 | 8730.9977 | 40.7917 | 0 | 0 | 24 | 24.98 | 20.81 | 30.35 | 982.88 | 50.09 | 0.931 | 94.9 | 87.29 | 12190 | 11840 | -350 | 0 | 0 | 0 | 24 | 6.47 | 2.1 | 4.6 | 2 | 0
| 2018-08-07 | 93.1 | 62% | 78.23 | 102 | 86 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3465 | 2949 | 2949 | 2879 | 2977 | 40 | 0 | 43 | 0 | 57 | 0 | 98 | -70 | 126 | 98.45% | 144.375 | 83.09% | 100% | 88.57% | 9.999 | 184.94 | 1849.2151 | 23.7046 | 980.4122 | 23240.23 | 8714.6388 | 122.875 | 0 | 0 | 0 | 0 | 16 | 1440 | 0 |  | 962 | 1036 | 979 | 74 | 8714.6388 | 40.7917 | 0 | 0 | 24 | 25.14 | 20.97 | 30.25 | 984.9 | 50.1 | 0.9305 | 94.82 | 87.3 | 12252 | 11897 | -355 | 0 | 0 | 0 | 24 | 7.25 | 2.2 | 4.8 | 2.1 | 0
| 2018-08-08 | 90.16 | 68.79% | 78.93 | 97 | 83 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3496 | 2950 | 2950 | 2875 | 2974 | 40 | 0 | 43 | 0 | 57 | 0 | 99 | -75 | 126 | 98.35% | 145.6667 | 82.24% | 100% | 88.57% | 9.942 | 187.68 | 1865.9146 | 23.5327 | 987.01 | 23227 | 8727.9703 | 122.9167 | 0 | 0 | 0 | 0 | 16 | 1440 | 0 |  | 963 | 1034 | 977 | 71 | 8727.9703 | 40.7083 | 0 | 0 | 24 | 25.04 | 20.94 | 30.19 | 987.25 | 50.07 | 0.9299 | 95.07 | 87.34 | 12200 | 11890 | -310 | 0 | 0 | 0 | 24 | 6.08 | 2.2 | 4.35 | 2.1 | 0
| 2018-08-09 | 88.5 | 75.3% | 81.76 | 95 | 86 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3513 | 2946 | 2946 | 2876 | 2975 | 40 | 0 | 43 | 0 | 57 | 0 | 99 | -70 | 126 | 98.38% | 146.375 | 81.87% | 100% | 88.57% | 9.971 | 187.17 | 1866.2721 | 23.5908 | 985.4253 | 23246.99 | 8732.0105 | 122.75 | 0 | 0 | 0 | 0 | 16 | 1440 | 0 |  | 962 | 1036 | 977 | 74 | 8732.0105 | 40.7083 | 0 | 0 | 24 | 25.07 | 21.09 | 30.25 | 989.9 | 50.14 | 0.9287 | 95.29 | 87.39 | 12235 | 11940 | -295 | 0 | 0 | 0 | 24 | 5.2 | 2.1 | 4.5 | 2.1 | 0
| 2018-08-10 | 93 | 68% | 81 | 101 | 85 | 24 | 0 | 23 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 3466 | 2926 | 2926 | 2852 | 2949 | 40 | 0 | 43 | 0 | 57 | 0 | 97 | -74 | 125 | 98.3% | 144.4167 | 82.29% | 100% | 87.7% | 9.902 | 191.13 | 1892.5693 | 23.4471 | 984.6855 | 23087.97 | 8758.9549 | 121.9167 | 0 | 0 | 13 | 25 | 17 | 1440 | 0 |  | 955 | 1023 | 971 | 68 | 8758.9549 | 40.4583 | 0 | 0 | 24 | 24.95 | 20.93 | 29.95 | 984.2 | 50.1 | 0.93 | 95.17 | 87.43 | 12250 | 12001 | -249 | 0 | 0 | 0 | 24 | 6.6 | 2.1 | 4.5 | 2.1 | 0
| 2018-08-11 | 94 | 65% | 80 | 101 | 88 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3460 | 2932 | 2932 | 2863 | 2960 | 40 | 0 | 43 | 0 | 57 | 0 | 97 | -69 | 125 | 98.67% | 144.1667 | 82.75% | 100% | 87.86% | 9.83 | 190.04 | 1868.0932 | 23.7114 | 977.4766 | 23177.29 | 8747.9508 | 122.1667 | 0 | 0 | 0 | 0 | 17 | 1440 | 0 |  | 956 | 1031 | 973 | 75 | 8747.9508 | 40.5417 | 0 | 0 | 24 | 25.22 | 21.34 | 29.98 | 983.4 | 50.14 | 0.9302 | 95.02 | 87.36 | 12373 | 12090 | -283 | 0 | 0 | 0 | 24 | 5.5 | 2.1 | 4.6 | 2 | 0
| 2018-08-12 | 93.1 | 65% | 79 | 101 | 88 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3467 | 2932 | 2932 | 2863 | 2958 | 40 | 0 | 43 | 0 | 57 | 0 | 95 | -69 | 125 | 98.6% | 144.4583 | 82.58% | 100% | 87.86% | 9.753 | 194.23 | 1894.3252 | 23.6852 | 974.7108 | 23086.21 | 8725.3005 | 122.1667 | 0 | 0 | 0 | 0 | 17 | 1440 | 0 |  | 956 | 1029 | 973 | 73 | 8725.3005 | 40.5417 | 0 | 0 | 24 | 25.24 | 21.42 | 29.73 | 980.8 | 50.07 | 0.9263 | 95.09 | 87.26 | 12388 | 12125 | -263 | 0 | 0 | 0 | 24 | 6.4 | 2.1 | 4.5 | 2.1 | 0
Week 33 | 2018-08-13 | 92.7 | 63% | 78.2 | 99 | 87 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3471 | 2948 | 2948 | 2877 | 2975 | 40 | 0 | 43 | 0 | 57 | 0 | 98 | -71 | 127 | 97.6% | 144.625 | 82.89% | 100% | 88.57% | 9.645 | 191.6 | 1847.982 | 23.7932 | 974.3717 | 23183.41 | 8700.5186 | 122.8333 | 0 | 0 | 0 | 0 | 16 | 1440 | 0 |  | 962 | 1036 | 977 | 74 | 8700.5186 | 40.7083 | 0 | 0 | 24 | 25.34 | 21.64 | 29.6 | 982.21 | 50.09 | 0.9294 | 95 | 87.26 | 12374 | 12137 | -237 | 0 | 0 | 0 | 24 | 6.67 | 2.1 | 4.6 | 2.1 | 0
| 2018-08-14 | 93.7 | 63.1% | 78.1 | 100 | 87 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3461 | 2947 | 2947 | 2872 | 2971 | 40 | 0 | 43 | 0 | 57 | 0 | 99 | -75 | 126 | 98.25% | 144.2083 | 82.98% | 100% | 88.57% | 9.575 | 193.08 | 1848.741 | 23.7356 | 975.8085 | 23161.38 | 8708.2594 | 122.7917 | 0 | 0 | 0 | 0 | 16 | 1440 | 0 |  | 960 | 1033 | 978 | 73 | 8708.2594 | 40.75 | 0 | 0 | 24 | 25.28 | 21.36 | 29.58 | 984.42 | 50.1 | 0.9293 | 94.95 | 87.23 | 12360 | 12044 | -316 | 0 | 0 | 0 | 24 | 6.42 | 2.1 | 4.4 | 2.1 | 0
| 2018-08-15 | 91.9 | 68% | 80.2 | 101 | 87 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3478 | 2940 | 2940 | 2865 | 2964 | 40 | 0 | 43 | 0 | 57 | 0 | 99 | -75 | 125 | 98.8% | 144.9167 | 82.37% | 100% | 88.57% | 9.375 | 197.28 | 1849.5 | 23.629 | 980.3089 | 23163.71 | 8730.6143 | 122.5 | 0 | 0 | 0 | 0 | 16 | 1440 | 0 |  | 958 | 1032 | 974 | 74 | 8730.6143 | 40.5833 | 0 | 0 | 24 | 25.13 | 21.21 | 29.43 | 986.13 | 50.13 | 0.9293 | 95.07 | 87.32 | 12305 | 11987 | -318 | 0 | 0 | 0 | 24 | 5.77 | 2.1 | 4.5 | 2 | 0
| 2018-08-16 | 90.4 | 68.4% | 79.9 | 99 | 84 | 16 | 53 | 21 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 3482 | 2328 | 2328 | 2279 | 2364 | 40 | 409 | 43 | 124 | 57 | 189 | 89 | -49 | 126 | 78.17% | 145.0833 | 65.45% | 83.9% | 68.33% | 5.075 | 197.66 | 1003.1245 | 19.0377 | 982.1702 | 18698.311 | 8644.772 | 97 | 22 | 18 | 19 | 39 | 21 | 1440 | 4 |  | 676 | 931 | 757 | 255 | 8644.772 | 31.5417 | 0 | 0 | 24 | 25.15 | 21.27 | 29.34 | 988.54 | 50.11 | 0.9292 | 94.99 | 87.31 | 12257 | 11963 | -294 | 0 | 0 | 0 | 15.78 | 6.75 | 1.9 | 4.5 | 2.1 | 0
| 2018-08-17 | 93.5 | 66.9% | 81.2 | 100 | 86 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3463 | 2916 | 2916 | 2844 | 2942 | 40 | 0 | 42 | 0 | 57 | 0 | 98 | -72 | 124 | 98.86% | 144.2917 | 82.13% | 100% | 87.77% | 9.394 | 195.93 | 1840.5664 | 23.4738 | 979.4223 | 22990.811 | 8731.1454 | 121.5 | 0 | 0 | 0 | 0 | 17 | 1440 | 0 |  | 956 | 1018 | 968 | 62 | 8731.1454 | 40.3333 | 0 | 0 | 24 | 25.06 | 21.25 | 29.32 | 986.33 | 50.1 | 0.9292 | 95.28 | 87.5 | 12312 | 12142 | -170 | 0 | 0 | 0 | 24 | 4.72 | 2 | 4.2 | 2.1 | 0
| 2018-08-18 | 91.3 | 69.6% | 81 | 102 | 83 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3486 | 2930 | 2930 | 2855 | 2955 | 40 | 0 | 43 | 0 | 57 | 0 | 100 | -75 | 126 | 97.72% | 145.25 | 81.9% | 100% | 87.86% | 9.263 | 197.72 | 1831.4804 | 23.5908 | 978.8773 | 23092.51 | 8729.9441 | 122.0833 | 0 | 0 | 0 | 0 | 17 | 1440 | 0 |  | 957 | 1026 | 972 | 69 | 8729.9441 | 40.5 | 0 | 0 | 24 | 25.12 | 21.3 | 29 | 985.33 | 50.15 | 0.9307 | 95.04 | 87.46 | 12317 | 12068 | -249 | 0 | 0 | 0 | 24 | 6.47 | 2.1 | 4.3 | 2 | 0
| 2018-08-19 | 91.23 | 67.9% | 79.57 | 100 | 82 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3485 | 2938 | 2938 | 2867 | 2965 | 40 | 0 | 43 | 0 | 57 | 0 | 98 | -71 | 126 | 98.05% | 145.2083 | 82.27% | 100% | 88.57% | 9.31 | 200.95 | 1870.8445 | 23.5926 | 980.0891 | 23122.83 | 8717.71 | 122.4167 | 0 | 0 | 0 | 0 | 16 | 1440 | 0 |  | 961 | 1028 | 976 | 67 | 8717.71 | 40.6667 | 0 | 0 | 24 | 25.11 | 20.71 | 29.25 | 985.6 | 50.11 | 0.9308 | 95.07 | 87.37 | 12263 | 11809 | -454 | 0 | 0 | 0 | 24 | 6.66 | 2.1 | 4.3 | 2.1 | 0
Week 34 | 2018-08-20 | 94.8 | 65.9% | 81.558 | 104 | 86 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3449 | 2904 | 2904 | 2838 | 2935 | 40 | 0 | 42 | 0 | 57 | 0 | 97 | -66 | 124 | 98.62% | 143.7083 | 82.28% | 100% | 87.77% | 9.205 | 197.86 | 1821.3013 | 23.3568 | 982.001 | 22936.43 | 8723.6544 | 121 | 0 | 0 | 0 | 0 | 17 | 1440 | 0 |  | 950 | 1018 | 967 | 68 | 8723.6544 | 40.2917 | 0 | 0 | 24 | 24.89 | 20.88 | 29.07 | 986 | 50.13 | 0.9305 | 94.92 | 87.49 | 12295 | 11992 | -303 | 0 | 0 | 0 | 24 | 6.5 | 2.1 | 4.3 | 2.1 | 0
| 2018-08-21 | 95.22 | 64.24% | 81.34 | 104 | 89 | 20 | 3 | 20 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 3446 | 2700 | 2700 | 2595 | 2692 | 38 | 0 | 40 | 0 | 57 | 228 | 97 | -105 | 124 | 90.46% | 143.5833 | 75.3% | 93.31% | 76.77% | 5.822 | 202.7 | 1180.1194 | 22.5412 | 983.7045 | 22173.91 | 8999.626 | 112.5 | 9 | 237 | 9 | 239 | 23 | 1212 | 0 |  | 912 | 970 | 810 | 58 | 8999.626 | 33.75 | 0 | 0 | 24 | 24.14 | 20.31 | 28.88 | 986 | 50.1 | 0.9304 | 94.44 | 87.45 | 12272 | 12072 | -200 | 0 | 0 | 0 | 20.8 | 7.1 | 2.1 | 4.4 | 2.1 | 0
| 2018-08-22 | 95 | 65% | 81 | 104 | 86 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3454 | 2906 | 2906 | 2838 | 2935 | 40 | 0 | 42 | 0 | 57 | 0 | 97 | -68 | 123 | 99.42% | 143.9167 | 82.17% | 100% | 87.77% | 9.399 | 202.86 | 1906.6811 | 23.3605 | 982.9456 | 22962.08 | 8762.777 | 121.0833 | 0 | 0 | 0 | 0 | 17 | 1440 | 0 |  | 949 | 1018 | 968 | 69 | 8762.777 | 40.3333 | 0 | 0 | 24 | 24.81 | 21.15 | 28.59 | 986 | 50.07 | 0.9313 | 94.65 | 87.4 | 12263 | 12072 | -191 | 0 | 0 | 0 | 24 | 6.3 | 2.1 | 4.2 | 2.1 | 0
| 2018-08-23 | 93.4 | 66% | 80 | 99 | 88 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3463 | 2918 | 2918 | 2846 | 2941 | 40 | 0 | 43 | 0 | 57 | 0 | 95 | -72 | 124 | 98.82% | 144.2917 | 82.18% | 100% | 87.86% | 9.402 | 199.9 | 1879.4598 | 23.4269 | 982.3507 | 23013.4 | 8746.6127 | 121.5833 | 0 | 0 | 0 | 0 | 17 | 1440 | 0 |  | 952 | 1020 | 969 | 68 | 8746.6127 | 40.375 | 0 | 0 | 24 | 24.89 | 21.27 | 28.81 | 985.2 | 50.09 | 0.9297 | 94.7 | 87.4 | 12260 | 12090 | -170 | 0 | 0 | 0 | 24 | 6.8 | 2.1 | 4.4 | 2.1 | 0
| 2018-08-24 | 92 | 67% | 78 | 99 | 86 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3477 | 2830 | 2830 | 2761 | 2859 | 36 | 0 | 43 | 0 | 57 | 0 | 98 | -69 | 125 | 95.3% | 144.875 | 79.41% | 100% | 87.5% | 9.226 | 197.01 | 1817.6143 | 22.7776 | 980.1139 | 22324.66 | 8744.0327 | 117.9167 | 0 | 0 | 0 | 0 | 17 | 1440 | 0 |  | 866 | 1031 | 962 | 165 | 8744.0327 | 40.0833 | 0 | 0 | 24 | 23.42 | 21.46 | 28.67 | 984.9 | 50.14 | 0.9292 | 86.43 | 87.3 | 12680 | 12079 | -601 | 0 | 0 | 0 | 2.8 | 5.2 | 2.1 | 4 | 2.1 | 0
| 2018-08-25 | 91.7 | 65.4% | 78.7 | 99 | 86 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3485 | 2837 | 2837 | 2767 | 2863 | 36 | 0 | 43 | 0 | 57 | 0 | 96 | -70 | 123 | 96.99% | 145.2083 | 79.4% | 100% | 87.5% | 9.291 | 197.75 | 1837.2953 | 22.7908 | 979.4022 | 22321.35 | 8730.9885 | 118.2083 | 0 | 0 | 0 | 0 | 17 | 1440 | 0 |  | 868 | 1031 | 964 | 163 | 8730.9885 | 40.1667 | 0 | 0 | 22.4 | 23.45 | 21.48 | 28.73 | 984.75 | 50.15 | 0.9293 | 86.18 | 87.21 | 12670 | 12057 | -613 | 0 | 0 | 0 | 2.32 | 0 | 2.1 | 4 | 2.1 | 0
| 2018-08-26 | 91.3 | 65.5% | 78.2 | 99 | 86 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3485 | 2943 | 2943 | 2872 | 2970 | 40 | 0 | 43 | 0 | 57 | 0 | 98 | -71 | 126 | 98.21% | 145.2083 | 82.41% | 100% | 88.57% | 9.279 | 205.51 | 1906.9273 | 23.6703 | 978.6065 | 23163.881 | 8729.3901 | 122.625 | 0 | 0 | 0 | 0 | 16 | 1440 | 0 |  | 959 | 1033 | 978 | 74 | 8729.3901 | 40.75 | 0 | 0 | 22.04 | 25.13 | 21.56 | 28.7 | 985.21 | 50.1 | 0.9305 | 94.13 | 87.26 | 12296 | 12078 | -218 | 0 | 0 | 0 | 24 | 6.3 | 2.1 | 4.2 | 2.1 | 0
Week 35 | 2018-08-27 | 93.2 | 62.7% | 78.1 | 103 | 85 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3466 | 2937 | 2937 | 2865 | 2963 | 40 | 0 | 43 | 0 | 57 | 0 | 98 | -72 | 126 | 97.98% | 144.4167 | 82.66% | 100% | 88.57% | 9.255 | 203.33 | 1881.8192 | 23.6396 | 978.5817 | 23133.311 | 8731.2845 | 122.375 | 0 | 0 | 0 | 0 | 16 | 1440 | 0 |  | 956 | 1031 | 976 | 75 | 8731.2845 | 40.6667 | 0 | 0 | 22 | 25.1 | 21.8 | 28.5 | 986.9 | 50.06 | 0.931 | 94.07 | 87.24 | 12314 | 12078 | -236 | 0 | 0 | 0 | 24 | 6.3 | 2.1 | 4.2 | 2.1 | 0
| 2018-08-28 | 94 | 60.6% | 78.1 | 103 | 84 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3460 | 2924 | 2924 | 2853 | 2954 | 40 | 0 | 43 | 0 | 57 | 0 | 101 | -71 | 125 | 98.47% | 144.1667 | 82.46% | 100% | 88.57% | 9.243 | 207.04 | 1913.6707 | 23.269 | 980.7014 | 22819.93 | 8669.3308 | 121.8333 | 0 | 0 | 0 | 0 | 16 | 1440 | 0 |  | 951 | 1028 | 975 | 77 | 8669.3308 | 40.625 | 0 | 0 | 22 | 24.62 | 21.23 | 27.94 | 988.17 | 50.08 | 0.9315 | 93.41 | 87.24 | 12162 | 11926 | -236 | 0 | 0 | 0 | 22.28 | 6.17 | 2.1 | 4.3 | 2 | 0
| 2018-08-29 | 94.5 | 59.7% | 77.8 | 104 | 84 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3453 | 2920 | 2920 | 2845 | 2945 | 41 | 0 | 43 | 0 | 57 | 0 | 100 | -75 | 126 | 97.39% | 143.875 | 82.39% | 100% | 87.94% | 9.272 | 204.93 | 1900.111 | 23.0913 | 998.9775 | 23067.74 | 8776.046 | 121.6667 | 0 | 0 | 0 | 0 | 17 | 1440 | 0 |  | 945 | 1027 | 973 | 82 | 8776.046 | 40.5417 | 0 | 0 | 28.9 | 24.31 | 20.97 | 27.9 | 988.1 | 50.09 | 0.9313 | 93.7 | 87.22 | 12073 | 11846 | -227 | 0 | 0 | 0 | 18.13 | 6.72 | 2.1 | 4.3 | 2.1 | 0
| 2018-08-30 | 93.6 | 61.9% | 78.4 | 103 | 84 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3461 | 2947 | 2947 | 2875 | 2974 | 40 | 0 | 43 | 0 | 57 | 0 | 99 | -72 | 125 | 99.13% | 144.2083 | 83.07% | 100% | 88.57% | 9.284 | 206.72 | 1919.1885 | 23.3147 | 1000.4413 | 23324.939 | 8780.5661 | 122.7917 | 0 | 0 | 0 | 0 | 16 | 1440 | 0 |  | 977 | 1023 | 974 | 46 | 8780.5661 | 40.5833 | 0 | 0 | 28.8 | 24.81 | 20.92 | 27.9 | 985.83 | 50.05 | 0.9311 | 96.97 | 87.31 | 11926 | 11856 | -70 | 0 | 0 | 0 | 24 | 6.67 | 2.1 | 4.5 | 2 | 0
| 2018-08-31 | 91.77 | 64.43% | 76.76 | 99.2 | 85.6 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3481 | 2955 | 2955 | 2889 | 2986 | 41 | 0 | 43 | 0 | 57 | 0 | 97 | -66 | 126 | 98.74% | 145.0417 | 82.99% | 100% | 88.65% | 9.252 | 205.73 | 1903.414 | 23.542 | 1001.5993 | 23579.641 | 8820.7182 | 123.125 | 0 | 0 | 0 | 0 | 16 | 1440 | 0 |  | 980 | 1028 | 978 | 48 | 8820.7182 | 40.75 | 0 | 0 | 28.98 | 25.04 | 21.17 | 27.96 | 985.6 | 50.04 | 0.932 | 96.96 | 87.2 | 11977 | 11898 | -79 | 0 | 0 | 0 | 24 | 6.5 | 2.1 | 4.65 | 2.1 | 0
| 2018-09-01 | [26 empty] | 0 | 0 |  | no data | no data | no data | no data | no data |  |  | 0 |  |  | 0 | no data | no data | [11 empty] | 0 | no data | 0 | [13 empty] | 0 | 0
| 2018-09-02 | [26 empty] | 0 | 0 |  | no data | no data | no data | no data | no data |  |  | 0 |  |  | 0 | no data | no data | [11 empty] | 0 | no data | 0 | [13 empty] | 0 | 0
| Monthly | 92.6832 | 65.4277 | 79.1725 | 100.4903 | 85.9226 | 732 | 56 | 736 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 107602 | 90008 | 90008 | 87978.92 | 90825 | 1232 | 409 | 1327 | 124 | 1767 | 417 | 2850.08 | -2219 | 125.3226 | 0.97411 | 144.6263 | 0.81588 | 0.99265 | 0.87253 | 288.488 | 193.6613 | 55740.9026 | 722.8258 | 983.9537 | 711225.254 | 8717.6128 | 120.9785 | 31 | 255 | 41 | 303 | 487 | 41532 | 4 |  | 27303 | 29700 | 27861 | 2397 | 8717.6128 | 38.6958 | 0 | 0 | 24.2455 | 24.8593 | 21.1059 | 29.289 | 985.2072 | 50.1028 | 0.93023 | 94.359 | 87.3272 | 12260.0345 | 11969.3103 |  | 0 | 0 | 0 | 586.11 | 163.87
| Totals | Avg.F | % Avg. |  | M Avg | m Avg | hrs | min | hrs | min | hrs | min | hrs | min | hrs | min | MWhr Total | MWhr Total | MWhr Total | MWhr Total | MWhr Total | MW Avg | Total min | Avg MW | Total min | Avg MW | Total min | MWhr | Total MW | Av Max D/Gen | Av. DailyLF | Avg. | Avg. |  | Avg. | Total | Avg. |  | Total | Avg. |  | Avg. | [7 empty] | Total | [5 empty] | Avg.
| Weeks data | Site Avg. Amb. Temp F | Site Avg. Relative humidity % |  | M Avg: Site Maximum/Minumum Temperature; hrs: CT-1 Base Load Hours; hrs: CT-2 Base Load Hours; hrs: CT-1 stand by hours / min; hrs: CT-2 standby hours / min; hrs: Plant ambient Corrected maximum Load hours/min | Average Corrected Plant Capacity | Ambient Corrected Declared Avail'y (MWH) | Av Plant WAPDA Dispatch | Net Plant Export (MWH) | Gross Generation | CT1 Av Cap (MW) | CT1 Unavail minutes | CT2 Av Cap (MW) | CT2 Unavail minutes | ST Unavail minutes | ST Average Cap (MW) | Plant Aux Load including Colony Load MWH | Differenece (+/-) MW | Maximum Daily Generation | Daily Load Factor | Avg. Corrected Plant | Plant Capacity Facto | Plant Availability Factor | Equivalent Plant Availability | LBtu gas flow mmscf | 1 LBtu gas (Average Btu/scf) | LBTU MMBTU | PL gas flow (mscf/week) | 1 PL gas (Average Btu/scf) | HBTU MMBTU | Plant Net Heat Rate (Btu/Kwh) | [12 empty] | 90
| Week 31 | 92.74 | 0.6488 | 78.36 | 99.4 | 87 | 120 | 2 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 289 | 3470.6 | 2951.2 | 2951.2 | 2880.2 | 2980.4 | 40 | No outage | 43 | No outage | No outage | 57 | no data | 100.2 | -71 | 125.8 | 0.98716 | 144.6083 | 0.82989 | 1 | 49.552 | 175.902 | 8716.2959 | 117.8868 | 989.3691 | 116633.5212 | 8704.3183
| Week 32 | 92.0371 | 66.94% | 79.4886 | 99.5714 | 86.1429 | 168 | -2 | 167 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 3477.5714 | 2940.5714 | 2940.5714 | 20085 | 20770 | 40 | No outage | 43 | No outage | No outage | 57 | 685 | -499 | 125.5714 | 98.45% | 144.8988 | 82.51% | 100% | 88.24% | 69.369 | 188.3471 | 13065.453 | 165.3056 | 982.1779 | 162359.4703 | 8733.9748 | [11 empty] | 355.5
| Week 33 | 92.1043 | 66.7% | 79.7386 | 100.1429 | 85.1429 | 160 | 53 | 165 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 3475.1429 | 2849.5714 | 2849.5714 | 19459 | 20136 | 40 | 409 | 42.8571 | 124 | 189 | 57 | 681 | -488 | 125.7143 | 95.35% | 144.7976 | 80% | 97.7% | 85.46% | 61.637 | 196.3171 | 12100.3997 | 137.2602 | 978.4931 | 134308.136 | 8708.9948
| Week 34 | 93.3457 | 0.65577 | 79.8283 | 101.1429 | 86.7143 | 164 | 5 | 164 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 3465.5714 | 2862.5714 | 2862.5714 | 19517 | 20195 | 38.5714 | No outage | 42.2857 | No outage | 399 | 57 | 678 | -521 | 124.1429 | 96.83% | 144.3988 | 80.45% | 99.04% | 86.25% | 61.624 | 200.5129 | 12356.4043 | 161.9241 | 981.3035 | 158896.6701 | 8776.7259 | [5 empty] | 0.225 |  |  | 0.225
| Week 35 | 93.414 | 0.61866 | 77.832 | 102.44 | 84.52 | 164 | 5 | 164 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 3468 | 2867.2857 | 2867.2857 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0.88875
| Date | Plant Status Whether Normal Operation or Tripping (State full detail for trippings/return to normal).
| 2018-08-01 | Plant load restricted 118~121 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-08-02 | Plant load restricted 118~122 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-08-03 | Plant load restricted 119~122 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-08-04 | Plant load restricted 119~122 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-08-05 | Plant load restricted 118~122 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-08-06 | Plant load restricted 118~122 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-08-07 | Plant load restricted 119~122 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-08-08 | Plant load restricted 118~121 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-08-09 | Plant load restricted 119~121 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-08-10 | Plant load restricted 113~120 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-08-11 | Plant load restricted 118~121 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-08-12 | Plant load restricted 118~121 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-08-13 | Plant load restricted 118~122 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-08-14 | Plant load restricted 118~122 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-08-15 | Plant load restricted 118~121 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-08-16 | Plant tripped @ 1524 hrs due to "Internal Fault". After rectification of fault, CT-2 synch @ 1728, STG synch @ 1833 hrs & CT-1 synch @ 2213 hrs.
| 2018-08-17 | Plant load restricted 117~119 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-08-18 | Plant load restricted 117~121 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-08-19 | Plant load restricted 118~121 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-08-20 | Plant load restricted 117~120 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-08-21 | STG tripped @ 0551 hrs due to "Internal Fault". After rectification of fault, STG synch @ 0939 hrs .
| 2018-08-22 | Plant load restricted 117~120 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-08-23 | Plant load restricted 117~120 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-08-24 | Plant load restricted 113~120 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-08-25 | Plant load restricted 113~119 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-08-26 | Plant load restricted 118~122 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-08-27 | Plant load restricted 118~122 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-08-28 | Plant load restricted 115~121 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-08-29 | Plant load restricted 114~122 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-08-30 | Plant load restricted 117~121 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-08-31 | Plant load restricted 118~123 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
0.88333
0.1
0.1

## Sept
2018-09-01
| Date | Site Avg. Ambient Temp.F | Site Avg. Relative Humidty % | Site Avg. Ambient Wetbulb Temp.F | Site Ambient Temp |  | Base load hours |  |  |  | Standby hours |  |  |  | Plant ambient corrected Max Load |  | Corrected Plant Capacity | Ambient Corrected Daclared Avail'y (MWH) | Plant WAPDA Dispatch (MWH) | Net Plant Export (MWH) | Gross Generation | CT1 Average Cap (MW) | CT1 Unavail minutes | CT2 Average Cap (MW) | CT2 Unavail minutes | ST Average Cap (MW) | ST Unavail minutes | Plant Aux Load including Colony Load MWH | Differenece (+/-) MW | Maximum Daily Generation | Daily Load Factor | Avg. Corrected Plant Capacity | Plant Capacity Factor | Plant Availability Factor | Equivalent Plant Availability | LBtu gas flow (mmscf/day) | 1 LBtu gas (Average Btu/scf) | LBTU MMBTU | 1 HBtu gas flow (mmscf/day) | 1 HBtu gas (Average Btu/scf) | HBTU MMBTU | HHV Net Heat Rate (Btu/Kwh) | Avg. declared availability | CT1 Derated MW | CT1 derated mintutes | CT-2 derated MW | CT-2 derated mintutes | ST derated MW | ST derated mintutes | WAPDA Backfeed (MWH) | CT-1 Gross Generation (MWH) | CT-2 Gross Generation (MWH) | STG Gross Generation (MWH) | CT-1 & CT-2 MWH difference | Base load Heat Rate | STG load | DB1 | DB2 | CT1 | CT1 Gas flow | CT2 Gas flow |  | Pamb | Freq. Hz | LBTU Gas Specific gravity | CT-1 compressor efficiency(%) | CT-2 compressor efficiency(%) | CT-1 Heat Rate (Btu/Kwh) | CT-2 Heat Rate (Btu/Kwh) |  | DB(1+2) | DB-1 Ops Hours | DB-2 Ops Hours | CT-1 Wetcomprssion Ops Hours | RO Operation Hours | CT1 T/G Brg |  | CT2 T/G Brg
[7 empty] | CT1 |  | CT2 |  | CT1 |  | CT2 | [43 empty] | mmscf/d | mmscf/d | WetC flow | HBTU KPPH | HBTU KPPH | LBTU KPPH | mbar | Hz | [6 empty] | mmscf/d |  |  |  |  | Supply air pressure | Seal air pressure | Supply air pressure | Seal air pressure
[5 empty] | Max | Min | hrs | min | hrs | min | hrs | min | hrs | min | hrs | min | [42 empty] | gpm | [16 empty] | Psi | "WC | Psi | "WC
Week 35 | 2018-08-27 | 93.2 | 62.7% | 78.1 | 103 | 85 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3466 | 2937 | 2937 | 2865 | 2963 | 40 | 0 | 43 | 0 | 57 | 0 | 98 | -72 | 126 | 97.98% | 144.4167 | 82.66% | 100% | 88.57% | 9.255 | 203.33 | 1881.8192 | 23.6396 | 978.5817 | 23133.311 | 8731.2845 | 122.375 | 0 | 0 | 0 | 0 | 16 | 1440 | 0 | 956 | 1031 | 976 | 75 | 8731.2845 | 40.6667 | 0 | 0 | 22 | 25.1 | 21.8 | 28.5 | 986.9 | 50.06 | 0.931 | 94.07 | 87.24 | 12314 | 12078 | -236 | 0 | 0 | 0 | 24 | 6.3 | 2.1 | 4.2 | 2.1 | 0
| 2018-08-28 | 94 | 60.6% | 78.1 | 103 | 84 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3460 | 2924 | 2924 | 2853 | 2954 | 40 | 0 | 43 | 0 | 57 | 0 | 101 | -71 | 125 | 98.47% | 144.1667 | 82.46% | 100% | 88.57% | 9.243 | 207.04 | 1913.6707 | 23.269 | 980.7014 | 22819.93 | 8669.3308 | 121.8333 | 0 | 0 | 0 | 0 | 16 | 1440 | 0 | 951 | 1028 | 975 | 77 | 8669.3308 | 40.625 | 0 | 0 | 22 | 24.62 | 21.23 | 27.94 | 988.17 | 50.08 | 0.9315 | 93.41 | 87.24 | 12162 | 11926 | -236 | 0 | 0 | 0 | 22.28 | 6.17 | 2.1 | 4.3 | 2 | 0
| 2018-08-29 | 94.5 | 59.7% | 77.8 | 104 | 84 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3453 | 2920 | 2920 | 2845 | 2945 | 41 | 0 | 43 | 0 | 57 | 0 | 100 | -75 | 126 | 97.39% | 143.875 | 82.39% | 100% | 87.94% | 9.272 | 204.93 | 1900.111 | 23.0913 | 998.9775 | 23067.74 | 8776.046 | 121.6667 | 0 | 0 | 0 | 0 | 17 | 1440 | 0 | 945 | 1027 | 973 | 82 | 8776.046 | 40.5417 | 0 | 0 | 28.9 | 24.31 | 20.97 | 27.9 | 988.1 | 50.09 | 0.9313 | 93.7 | 87.22 | 12073 | 11846 | -227 | 0 | 0 | 0 | 18.13 | 6.72 | 2.1 | 4.3 | 2.1 | 0
| 2018-08-30 | 93.6 | 61.9% | 78.4 | 103 | 84 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3461 | 2947 | 2947 | 2875 | 2974 | 40 | 0 | 43 | 0 | 57 | 0 | 99 | -72 | 125 | 99.13% | 144.2083 | 83.07% | 100% | 88.57% | 9.284 | 206.72 | 1919.1885 | 23.3147 | 1000.4413 | 23324.939 | 8780.5661 | 122.7917 | 0 | 0 | 0 | 0 | 16 | 1440 | 0 | 977 | 1023 | 974 | 46 | 8780.5661 | 40.5833 | 0 | 0 | 28.8 | 24.81 | 20.92 | 27.9 | 985.83 | 50.05 | 0.9311 | 96.97 | 87.31 | 11926 | 11856 | -70 | 0 | 0 | 0 | 24 | 6.67 | 2.1 | 4.5 | 2 | 0
| 2018-08-31 | 91.77 | 64.43% | 76.76 | 99.2 | 85.6 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3481 | 2955 | 2955 | 2889 | 2986 | 41 | 0 | 43 | 0 | 57 | 0 | 97 | -66 | 126 | 98.74% | 145.0417 | 82.99% | 100% | 88.65% | 9.252 | 205.73 | 1903.414 | 23.542 | 993.1039 | 23379.641 | 8751.4901 | 123.125 | 0 | 0 | 0 | 0 | 16 | 1440 | 0 | 980 | 1028 | 978 | 48 | 8751.4901 | 40.75 | 0 | 0 | 28.98 | 25.04 | 21.17 | 27.96 | 985.6 | 50.04 | 0.932 | 96.96 | 87.2 | 11977 | 11898 | -79 | 0 | 0 | 0 | 24 | 6.5 | 2.1 | 4.65 | 2.1 | 0
| 2018-09-01 | 90.75 | 65.14% | 77.1 | 99 | 84 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3488 | 2977 | 2977 | 2906 | 3002 | 41 | 0 | 43 | 0 | 57 | 0 | 96 | -71 | 127 | 98.49% | 145.3333 | 83.31% | 100% | 88.65% | 8.942 | 200.59 | 1793.6758 | 23.8647 | 983.0273 | 23459.69 | 8690.0777 | 124.0417 | 0 | 0 | 0 | 0 | 16 | 1440 | 0 | 986 | 1034 | 982 | 48 | 8690.0777 | 40.9167 | 0 | 0 | 29.1 | 25.5 | 21.6 | 28.02 | 988.7 | 50.01 | 0.9328 | 97 | 87.2 | 12144 | 12024 | -120 | 0 | 0 | 0 | 24 | 6.67 | 2.1 | 4.4 | 2.1 | 0
| 2018-09-02 | 90.21 | 66.48% | 77.83 | 99 | 83 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3497 | 2973 | 2973 | 2902 | 3001 | 41 | 0 | 43 | 0 | 57 | 0 | 99 | -71 | 127 | 98.46% | 145.7083 | 82.99% | 100% | 88.65% | 8.922 | 202.96 | 1810.8091 | 23.8188 | 988.1489 | 23536.53 | 8734.438 | 123.875 | 0 | 0 | 0 | 0 | 16 | 1440 | 0 | 986 | 1034 | 981 | 48 | 8734.438 | 40.875 | 0 | 0 | 29.2 | 25.4 | 21.49 | 27.85 | 988.4 | 50.06 | 0.9317 | 97.03 | 87.2 | 12092 | 11978 | -114 | 0 | 0 | 0 | 24 | 6.67 | 2.1 | 4.55 | 2.1 | 0
Week 36 | 2018-09-03 | 91 | 64% | 77 | 99 | 84 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3485 | 2976 | 2976 | 2905 | 3002 | 41 | 0 | 43 | 0 | 57 | 0 | 97 | -71 | 128 | 97.72% | 145.2083 | 83.36% | 100% | 88.65% | 8.884 | 200.79 | 1783.8184 | 23.9432 | 985.1052 | 23586.6 | 8733.3626 | 124 | 0 | 0 | 0 | 0 | 16 | 1440 | 0 | 987 | 1033 | 982 | 46 | 8733.3626 | 40.9167 | 0 | 0 | 29.07 | 25.5 | 21.6 | 27.8 | 988.9 | 50.08 | 0.9317 | 96.99 | 87.22 | 12147 | 12039 | -108 | 0 | 0 | 0 | 24 | 7.1 | 2.1 | 4.6 | 2.1 | 0
| 2018-09-04 | 92 | 64.9% | 78 | 100 | 83 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3475 | 2972 | 2972 | 2902 | 2999 | 41 | 0 | 43 | 0 | 57 | 0 | 97 | -70 | 127 | 98.39% | 144.7917 | 83.51% | 100% | 88.65% | 8.831 | 204.63 | 1807.0875 | 24.0487 | 979.0741 | 23545.46 | 8736.2328 | 123.8333 | 0 | 0 | 0 | 0 | 16 | 1440 | 0 | 986 | 1032 | 981 | 46 | 8736.2328 | 40.875 | 0 | 0 | 28.99 | 25.7 | 22.28 | 27.8 | 989.5 | 50.12 | 0.9323 | 96.88 | 87.2 | 12234 | 12307 | 73 | 0 | 0 | 0 | 24 | 7.1 | 2.1 | 5 | 2.1 | 0
| 2018-09-05 | 91.4 | 66% | 78.1 | 100 | 83 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3484 | 2966 | 2966 | 2893 | 2993 | 41 | 0 | 43 | 0 | 57 | 0 | 100 | -73 | 126 | 98.97% | 145.1667 | 83.04% | 100% | 88.65% | 8.896 | 206.56 | 1837.5578 | 23.9963 | 979.5302 | 23505.09 | 8759.9889 | 123.5833 | 0 | 0 | 0 | 0 | 16 | 1440 | 0 | 984 | 1030 | 979 | 46 | 8759.9889 | 40.7917 | 0 | 0 | 28.94 | 25.64 | 22.57 | 27.8 | 988.6 | 50.09 | 0.9324 | 96.93 | 87.21 | 12243 | 12423 | 180 | 0 | 0 | 0 | 24 | 7.1 | 2.1 | 5 | 2 | 0
| 2018-09-06 | 91.8 | 62.6% | 76.9 | 102 | 83 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3479 | 2981 | 2981 | 2908 | 3006 | 41 | 0 | 43 | 0 | 57 | 0 | 98 | -73 | 127 | 98.62% | 144.9583 | 83.59% | 100% | 88.65% | 8.862 | 214.23 | 1898.5063 | 24.0392 | 979.4822 | 23545.93 | 8749.8061 | 124.2083 | 0 | 0 | 0 | 0 | 16 | 1440 | 0 | 988 | 1034 | 984 | 46 | 8749.8061 | 41 | 0 | 0 | 28.9 | 25.7 | 22.61 | 28.06 | 988.17 | 50.12 | 0.9351 | 96.83 | 87.18 | 12209 | 12409 | 200 | 0 | 0 | 0 | 24 | 7.58 | 2.1 | 5 | 2.1 | 0
| 2018-09-07 | 91.7 | 60.6% | 76 | 103 | 81 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3482 | 2998 | 2998 | 2921 | 3016 | 41 | 0 | 43 | 0 | 57 | 0 | 95 | -77 | 128 | 98.18% | 145.0833 | 83.89% | 100% | 88.65% | 8.883 | 214.78 | 1907.8907 | 24.0931 | 981.0547 | 23636.61 | 8745.1218 | 124.9167 | 0 | 0 | 0 | 0 | 16 | 1440 | 0 | 991 | 1036 | 989 | 45 | 8745.1218 | 41.2083 | 0 | 0 | 29 | 25.74 | 22.65 | 27.9 | 990 | 50.12 | 0.9336 | 96.75 | 87.11 | 12184 | 12365 | 181 | 0 | 0 | 0 | 24 | 8.5 | 2.1 | 5 | 2.1 | 0
| 2018-09-08 | 90.6 | 68.12% | 78.8 | 99 | 82 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3493 | 2965 | 2965 | 2892 | 2990 | 41 | 0 | 43 | 0 | 57 | 0 | 98 | -73 | 128 | 97.33% | 145.5417 | 82.79% | 100% | 88.65% | 8.806 | 208.65 | 1837.3719 | 23.737 | 984.9346 | 23379.3924 | 8719.4897 | 123.5417 | 0 | 0 | 0 | 0 | 16 | 1440 | 0 | 982 | 1027 | 981 | 45 | 8719.4897 | 40.875 | 0 | 0 | 29 | 25.5 | 22.43 | 27.83 | 991 | 50.08 | 0.9317 | 97.15 | 87.26 | 12187 | 12413 | 226 | 0 | 0 | 0 | 24 | 7.1 | 2.1 | 5 | 2 | 0
| 2018-09-09 | 90.4 | 70% | 80 | 98 | 84 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3494 | 2962 | 2962 | 2893 | 2990 | 41 | 0 | 43 | 0 | 57 | 0 | 97 | -69 | 126 | 98.88% | 145.5833 | 82.8% | 100% | 88.65% | 8.78 | 205.1 | 1800.778 | 23.7993 | 987.9538 | 23512.57 | 8749.861 | 123.4167 | 0 | 0 | 0 | 0 | 16 | 1440 | 0 | 981 | 1026 | 983 | 45 | 8749.861 | 40.9583 | 0 | 0 | 29.15 | 25.36 | 22.34 | 27.62 | 991.79 | 50.13 | 0.9312 | 97.15 | 87.32 | 12134 | 12354 | 220 | 0 | 0 | 0 | 24 | 7.58 | 2.1 | 5 | 2.1 | 0
Week 37 | 2018-09-10 | 90.8 | 66.9% | 78.5 | 99 | 81 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3493 | 2974 | 2974 | 2904 | 3000 | 41 | 0 | 43 | 0 | 57 | 0 | 96 | -70 | 126 | 99.21% | 145.5417 | 83.14% | 100% | 88.65% | 8.731 | 204.6 | 1786.3626 | 23.8204 | 990.1992 | 23586.97 | 8737.3735 | 123.9167 | 0 | 0 | 0 | 0 | 16 | 1440 | 0 | 984 | 1028 | 988 | 44 | 8737.3735 | 41.1667 | 0 | 0 | 29.1 | 25.38 | 21.53 | 28.22 | 993.5 | 50.09 | 0.9327 | 96.99 | 87.22 | 12100 | 12022 | -78 | 0 | 0 | 0 | 24 | 6.65 | 2.1 | 5 | 2 | 0
| 2018-09-11 | 92.1 | 65.2% | 79 | 103 | 83 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3477 | 2966 | 2966 | 2897 | 2996 | 41 | 0 | 43 | 0 | 57 | 0 | 99 | -69 | 127 | 98.29% | 144.875 | 83.32% | 100% | 88.65% | 8.748 | 202.56 | 1771.9949 | 23.8469 | 988.5377 | 23573.51 | 8748.8798 | 123.5833 | 0 | 0 | 0 | 0 | 16 | 1440 | 0 | 982 | 1028 | 986 | 46 | 8748.8798 | 41.0833 | 0 | 0 | 28.95 | 25.4 | 20.23 | 28.88 | 991.79 | 50.13 | 0.9306 | 96.85 | 87.24 | 12150 | 11564 | -586 | 0 | 0 | 0 | 24 | 6.55 | 2.1 | 5 | 2.1 | 0
| 2018-09-12 | 90.31 | 67.27% | 77.72 | 98 | 85 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3494 | 2982 | 2982 | 2911 | 3006 | 41 | 0 | 43 | 0 | 57 | 0 | 95 | -71 | 127 | 98.62% | 145.5833 | 83.31% | 100% | 88.65% | 8.609 | 200.99 | 1730.3229 | 23.8919 | 989.0009 | 23629.12 | 8711.5915 | 124.25 | 0 | 0 | 0 | 0 | 16 | 1440 | 0 | 985 | 1031 | 990 | 46 | 8711.5915 | 41.25 | 0 | 0 | 29.17 | 25.41 | 20.25 | 28.62 | 989.38 | 50.13 | 0.9308 | 96.9 | 87.17 | 12100 | 11496 | -604 | 0 | 0 | 0 | 24 | 7.42 | 2.1 | 5 | 2 | 0
| 2018-09-13 | 88.74 | 66.46% | 76.05 | 97 | 83 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3514 | 2999 | 2999 | 2924 | 3023 | 41 | 0 | 43 | 0 | 57 | 0 | 99 | -75 | 128 | 98.4% | 146.4167 | 83.21% | 100% | 88.65% | 8.618 | 200.35 | 1726.6163 | 24.0299 | 988.8543 | 23762.06 | 8717.0576 | 124.9583 | 0 | 0 | 0 | 0 | 16 | 1440 | 0 | 991 | 1038 | 994 | 47 | 8717.0576 | 41.4167 | 0 | 0 | 29.2 | 25.55 | 20.44 | 28.86 | 988.92 | 50.12 | 0.9305 | 96.86 | 87.1 | 12112 | 11526 | -586 | 0 | 0 | 0 | 24 | 7.1 | 2.1 | 5.05 | 2.1 | 0
| 2018-09-14 | 88.4 | 63.98% | 74.85 | 97 | 82 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3515 | 3018 | 3018 | 2943 | 3043 | 42 | 0 | 44 | 0 | 57 | 0 | 100 | -75 | 128 | 99.06% | 146.4583 | 83.73% | 100% | 89.51% | 8.601 | 201.56 | 1733.6176 | 24.1606 | 985.6837 | 23814.69 | 8681.0423 | 125.75 | 0 | 0 | 0 | 0 | 15 | 1440 | 0 | 998 | 1045 | 1000 | 47 | 8681.0423 | 41.6667 | 0 | 0 | 29.37 | 25.74 | 20.68 | 28.83 | 991.38 | 50.18 | 0.9312 | 96.76 | 87.06 | 12107 | 11541 | -566 | 0 | 0 | 0 | 24 | 7.18 | 2.1 | 5 | 2.1 | 0
| 2018-09-15 | 83 | 70% | 73 | 93 | 77 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3568 | 3042 | 3042 | 2968 | 3068 | 42 | 0 | 44 | 0 | 57 | 0 | 100 | -74 | 130 | 98.33% | 148.6667 | 83.18% | 100% | 89.51% | 8.625 | 205.58 | 1773.1275 | 23.989 | 999.8138 | 23984.5339 | 8678.4573 | 126.75 | 0 | 0 | 0 | 0 | 15 | 1440 | 0 | 1007 | 1054 | 1007 | 47 | 8678.4573 | 41.9583 | 0 | 0 | 29.95 | 25.03 | 20.18 | 29.29 | 995.21 | 50.13 | 0.9331 | 96.93 | 87 | 11660 | 11193 | -467 | 0 | 0 | 0 | 24 | 6.67 | 2 | 5 | 2.1 | 0
| 2018-09-16 | 87 | 64% | 74 | 94 | 78 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3526 | 3024 | 3024 | 2956 | 3057 | 42 | 0 | 44 | 0 | 58 | 0 | 101 | -68 | 129 | 98.74% | 146.9167 | 83.83% | 100% | 88.89% | 8.603 | 204.14 | 1756.2164 | 23.612 | 1012.5949 | 23909.3904 | 8682.5463 | 126 | 0 | 0 | 0 | 0 | 16 | 1440 | 0 | 1002 | 1050 | 1005 | 48 | 8682.5463 | 41.875 | 0 | 0 | 29.53 | 25.02 | 20.24 | 28.92 | 994.8 | 50.12 | 0.9325 | 96.77 | 86.99 | 11736 | 11278 | -458 | 0 | 0 | 0 | 24 | 6.6 | 2.1 | 5 | 2.1 | -0.5
Week 38 | 2018-09-17 | 90 | 60% | 74 | 99 | 81 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3499 | 3022 | 3022 | 2946 | 3044 | 42 | 0 | 44 | 0 | 57 | 0 | 98 | -76 | 128 | 99.09% | 145.7917 | 84.2% | 100% | 89.51% | 8.621 | 205.07 | 1767.9085 | 23.623 | 1003.4428 | 23704.3292 | 8646.3807 | 125.9167 | 0 | 0 | 0 | 0 | 15 | 1440 | 0 | 996 | 1046 | 1002 | 50 | 8646.3807 | 41.75 | 0 | 0 | 29.2 | 24.98 | 20.27 | 28.86 | 993.2 | 50.13 | 0.931 | 96.56 | 87 | 11769 | 11318 | -451 | 0 | 0 | 0 | 24 | 6.4 | 2 | 4.9 | 2.1 | -0.3
| 2018-09-18 | 89.9 | 60.7% | 74 | 102 | 79 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3501 | 3019 | 3019 | 2945 | 3043 | 42 | 0 | 44 | 0 | 57 | 0 | 98 | -74 | 129 | 98.29% | 145.875 | 84.12% | 100% | 89.51% | 8.624 | 204.23 | 1761.2795 | 23.771 | 1001.934 | 23816.9723 | 8685.3147 | 125.7917 | 0 | 0 | 0 | 0 | 15 | 1440 | 0 | 997 | 1045 | 1001 | 48 | 8685.3147 | 41.7083 | 0 | 0 | 29.2 | 25.14 | 20.52 | 28.56 | 993 | 50.21 | 0.9311 | 96.52 | 87 | 11838 | 11423 | -415 | 0 | 0 | 0 | 24 | 7.16 | 2 | 4.9 | 2.1 | -0.4
| 2018-09-19 | 88.8 | 63.1% | 74.8 | 102 | 79 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3509 | 3002 | 3002 | 2933 | 3033 | 41 | 0 | 43 | 0 | 57 | 0 | 100 | -69 | 130 | 97.21% | 146.2083 | 83.59% | 100% | 89.36% | 8.598 | 189.09 | 1625.7958 | 23.858 | 997.8442 | 23806.5679 | 8671.1094 | 125.0833 | 0 | 0 | 0 | 0 | 15 | 1440 | 0 | 993 | 1042 | 998 | 49 | 8671.1094 | 41.5833 | 0 | 0 | 28.8 | 25.09 | 20.47 | 28.67 | 991.92 | 50.15 | 0.9276 | 96.45 | 87.16 | 11860 | 11430 | -430 | 0 | 0 | 0 | 24 | 7.33 | 2 | 4.9 | 2.1 | -0.3
| 2018-09-20 | 88.9 | 61.5% | 74.3 | 100 | 79 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3511 | 3009 | 3009 | 2937 | 3035 | 41 | 0 | 43 | 0 | 57 | 0 | 98 | -72 | 130 | 97.28% | 146.2917 | 83.65% | 100% | 89.36% | 8.585 | 183.69 | 1576.9787 | 23.879 | 999.1528 | 23858.7707 | 8660.4526 | 125.375 | 0 | 0 | 0 | 0 | 15 | 1440 | 0 | 994 | 1041 | 1000 | 47 | 8660.4526 | 41.6667 | 0 | 0 | 28.5 | 25.03 | 20.48 | 28.37 | 992.5 | 50.12 | 0.9246 | 96.26 | 87.24 | 11830 | 11451 | -379 | 0 | 0 | 0 | 24 | 7.12 | 2 | 4.9 | 2.1 | -0.3
| 2018-09-21 | 88.2 | 65.2% | 75.51 | 98 | 79 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3516 | 2999 | 2999 | 2929 | 3025 | 41 | 0 | 43 | 0 | 57 | 0 | 96 | -70 | 129 | 97.71% | 146.5 | 83.3% | 100% | 88.65% | 8.577 | 179.22 | 1537.1699 | 24.091 | 994.6898 | 23963.0711 | 8706.1253 | 124.9583 | 0 | 0 | 0 | 0 | 16 | 1440 | 0 | 992 | 1038 | 995 | 46 | 8706.1253 | 41.4583 | 0 | 0 | 28.46 | 25.23 | 20.68 | 28.43 | 994.83 | 50.13 | 0.9234 | 96.34 | 87.34 | 11949 | 11555 | -394 | 0 | 0 | 0 | 24 | 7.38 | 2.1 | 5 | 2 | 0
| 2018-09-22 | 85.4 | 67.3% | 74.1 | 96 | 77 | 22 | 42 | 24 | 0 | 0 | 57 | 0 | 0 | 0 | 0 | 3546 | 3021 | 2945 | 2887 | 2981 | 42 | 0 | 43 | 0 | 57 | 0 | 94 | -58 | 130 | 95.54% | 147.75 | 81.42% | 100% | 87.86% | 8.565 | 171.4 | 1468.041 | 23.715 | 992.4124 | 23535.0607 | 8660.5825 | 125.875 | 16 | 21 | 0 | 0 | 17 | 1440 | 0 | 952 | 1048 | 981 | 96 | 8660.5825 | 40.875 | 0 | 0 | 29.14 | 24.18 | 20.87 | 28.4 | 996.63 | 50.12 | 0.9233 | 96.53 | 87.23 | 11895 | 11502 | -393 | 0 | 0 | 0 | 22.42 | 6.6 | 2.1 | 4.8 | 2.1 | 0
| 2018-09-23 | 81.5 | 70.4% | 72.5 | 92 | 73 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 3581 | 3024 | 1459 | 1455 | 1532 | 42 | 0 | 44 | 0 | 57 | 0 | 77 | -4 | 66 | 96.72% | 149.2083 | 40.63% | 100% | 81.12% | 8.518 | 170.56 | 1452.8301 | 11.327 | 993.3437 | 11251.6037 | 8731.5696 | 126 | 0 | 0 | 0 | 0 | 27 | 1440 | 0 | 0 | 1062 | 470 | 1062 | 8731.5696 | 19.5833 | 0 | 0 | 0 | 0 | 21.2 | 28.5 | 996.88 | 50.11 | 0.9221 | - | 87.13 | - | 11504 | - | 0 | 0 | 0 | 0 | 2.78 | - | - | 2.1 | 0
Week 39 | 2018-09-24 | 82.5 | 72.9% | 74.2 | 93 | 74 | 15 | 30 | 24 | 0 | 7 | 31 | 0 | 0 | 15 | 20 | 3569 | 3448 | 2731 | 2678 | 2782 | 42 | 0 | 44 | 0 | 57 | 0 | 104 | -53 | 145 | 79.94% | 148.7083 | 75.04% | 100% | 90.05% | 8.474 | 167.56 | 1419.9034 | 22.118 | 992.8255 | 21959.3146 | 8730.1038 | 143.6667 | 21 | 59 | 0 | 0 | 37 | 520 | 0 | 659 | 1054 | 1069 | 395 | 8730.1038 | 44.5417 | 1.415 | 1.415 | 14 | 17.04 | 21.13 | 28.34 | 996 | 50.09 | 0.9225 | 95.71 | 86.99 | 11947 | 11563 | -384 | 2.83 | 15.98 | 8.58 | 14 | 4.93 | 2.1 | 4.9 | 2.1 | -0.4
| 2018-09-25 | 83.54 | 69.52% | 73.23 | 94 | 75 | 22 | 3 | 24 | 0 | 1 | 41 | 0 | 0 | 11 | 2 | 3566 | 3278 | 3127 | 3055 | 3159 | 42 | 0 | 44 | 0 | 57 | 0 | 104 | -72 | 146 | 90.15% | 148.5833 | 85.67% | 100% | 93.83% | 8.512 | 167.66 | 1427.1219 | 25.133 | 1001.0743 | 25160 | 8702.8222 | 136.5833 | 16 | 16 | 0 | 0 | 16 | 778 | 0 | 928 | 1056 | 1175 | 128 | 8702.8222 | 48.9583 | 1.103 | 1.093 | 29.46 | 23.39 | 20.98 | 28.32 | 995.4 | 50.09 | 0.9219 | 96.89 | 86.99 | 11806 | 11475 | -331 | 2.196 | 22.08 | 24 | 22.07 | 7.58 | 2.1 | 4.9 | 2 | 0
| 2018-09-26 | 85.37 | 69.4% | 74.75 | 98 | 75 | 4 | 58 | 24 | 0 | 18 | 6 | 0 | 0 | 0 | 0 | 3545 | 3331 | 1873 | 1867 | 1952 | 42 | 0 | 44 | 0 | 57 | 0 | 85 | -6 | 131 | 62.09% | 147.7083 | 52.67% | 100% | 79.85% | 8.492 | 172.45 | 1464.4454 | 14.775 | 1005.9876 | 14863.4672 | 8745.5343 | 138.7917 | 21 | 56 | 0 | 0 | 28 | 1440 | 0 | 220 | 1047 | 685 | 827 | 8745.5343 | 28.5417 | 0.078 | 1.002 | 29.27 | 6 | 20.74 | 27.8 | 999.5 | 50.09 | 0.9203 | 95.31 | 87.02 | 11844 | 11443 | -401 | 1.08 | 3.33 | 24 | 4.2 | 4.47 | 2 | 4.25 | 2.1 | 0
| 2018-09-27 | 88.2 | 60.4% | 73.5 | 102 | 77 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 3517 | 3093 | 1608 | 1608 | 1687 | 42 | 0 | 44 | 0 | 57 | 0 | 79 | 0 | 72 | 97.63% | 146.5417 | 45.72% | 100% | 79.02% | 8.51 | 168.8 | 1436.488 | 12.541 | 999.6087 | 12536.0931 | 8689.4161 | 128.875 | 0 | 0 | 0 | 0 | 30 | 1440 | 0 | 0 | 1045 | 642 | 1045 | 8689.4161 | 26.75 | 0 | 1.661 | 0 | 0 | 21.05 | 29.9 | 994.5 | 50.09 | 0.9217 | 0 | 86.98 | 0 | 11585 | 11585 | 1.661 | 0 | 24 | 0 | 0 | 0 | 0 | 2 | 0
| 2018-09-28 | 87 | 53% | 68 | 102 | 79 | 0 | 0 | 21 | 38 | 24 | 0 | 1 | 15 | 0 | 0 | 3527 | 3488 | 1542 | 1550 | 1625 | 42 | 0 | 44 | 0 | 57 | 0 | 77 | 8 | 73 | 92.75% | 146.9583 | 43.95% | 100% | 79.97% | 8.185 | 170.16 | 1392.7596 | 12.104 | 996.331 | 12059.5907 | 8678.9357 | 145.3333 | 0 | 0 | 5 | 67 | 30 | 1364 | 2 | 0 | 1004 | 621 | 1004 | 8678.9357 | 25.875 | 0 | 1.594 | 0 | 0 | 20.09 | 26.3 | 995.1 | 50.11 | 0.9216 | 0 | 86.8 | 0 | 11503 | 11503 | 1.594 | 0 | 21.7 | 0 | 0 | 0 | 0 | 2.1 | -0.4
| 2018-09-29 | 83 | 62% | 72 | 93 | 72 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3567 | 3571 | 0 | 0 | 0 | 42 | 0 | 44 | 0 | 57 | 0 | 19 | 0 | 0 | no data | 148.625 | no data | no data | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 148.7917 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 997 | 50.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7 | 0 | 0 | 0 | 0
| 2018-09-30 | 85.8 | 61.2% | 71.2 | 96 | 78 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3536 | 3540 | 0 | 0 | 0 | 42 | 0 | 44 | 0 | 57 | 0 | 16 | 0 | 0 | no data | 147.3333 | no data | no data | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 147.5 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 996.04 | 50.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Monthly | 88.2773 | 64.9423 | 75.298 | 98.2333 | 79.7667 | 569 | 13 | 669 | 38 | 26 | 15 | 49 | 15 | 26 | 22 | 105454 | 92620 | 78111 | 76581.82 | 79090 | 1244 | 0 | 1303 | 0 | 1711 | 0 | 2545.18 | -1696 | 114.9333 | 95.72% | 146.4639 | 72.62% | 100% | 87.8% | 242.602 | 180.932 | 47086.4755 | 623.6259 | 926.0547 | 618482.9877 | 8690.9591 | 128.6389 | 74 | 152 | 5 | 67 | 515 | 38662 | 37 | 23551 | 29088 | 26451 | 5537 | 8690.9591 | 36.7375 | 2.596 | 6.765 | 23.755 | 20.1217 | 19.72 | 26.425 | 992.7513 | 50.11 | 0.86683 | 83.3566 | 81.3187 | 10354.3793 | 10956.1333 |  | 9.361 | 41.39 | 102.28 | 566.69 | 178.02 | 1.7897 | 4.2086 | 1.9367 | -0.086667
| Totals | Avg.F | % Avg. |  | M Avg | m Avg | hrs | min | hrs | min | hrs | min | hrs | min | hrs | min | MWhr Total | MWhr Total | MWhr Total | MWhr Total | MWhr Total | MW Avg | Total min | Avg MW | Total min | Avg MW | Total min | MWhr | Total MW | Av Max D/Gen | Av. DailyLF | Avg. | Avg. |  | Avg. | Total | Avg. |  | Total | Avg. |  | Avg. | [7 empty] | Total |  |  |  |  | Avg.
[47 empty] | 520 |  | 480
| Weeks data | Site Avg. Amb. Temp F | Site Avg. Relative humidity % |  | M Avg: Site Maximum/Minumum Temperature; hrs: CT-1 Base Load Hours; hrs: CT-2 Base Load Hours; hrs: CT-1 stand by hours / min; hrs: CT-2 standby hours / min; hrs: Plant ambient Corrected maximum Load hours/min | Average Corrected Plant Capacity | Ambient Corrected Declared Avail'y (MWH) | Av Plant WAPDA Dispatch | Net Plant Export (MWH) | Gross Generation | CT1 Av Cap (MW) | CT1 Unavail minutes | CT2 Av Cap (MW) | CT2 Unavail minutes | ST Unavail minutes | ST Average Cap (MW) | Plant Aux Load including Colony Load MWH | Differenece (+/-) MW | Maximum Daily Generation | Daily Load Factor | Avg. Corrected Plant | Plant Capacity Facto | Plant Availability Factor | Equivalent Plant Availability | LBtu gas flow mmscf | 1 LBtu gas (Average Btu/scf) | LBTU MMBTU | PL gas flow (mscf/week) | 1 PL gas (Average Btu/scf) | HBTU MMBTU | Plant Net Heat Rate (Btu/Kwh) | [28 empty] | 1825~2145
| Week 35 | 92.166 | 0.6353 | 77.578 | 100.84 | 84.12 | 120 | 2 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 289 | 3476 | 2954.4 | 2954.4 | 2883.4 | 2981.6 | 40.8 | No outage | 43 | No outage | No outage | 57 | no data | 98.2 | -71 | 126.2 | 0.98443 | 144.8333 | 0.82951 | 1 | 45.672 | 204.186 | 9325.583 | 117.6315 | 992.7398 | 116777.5074 | 8746.5236
| Week 36 | 91.2714 | 65.17% | 77.8286 | 100.1429 | 82.8571 | 168 | -2 | 168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3484.5714 | 2974.2857 | 2974.2857 | 20314 | 20996 | 41 | No outage | 43 | No outage | No outage | 57 | 682 | -506 | 127.1429 | 98.3% | 145.1905 | 83.28% | 100% | 88.65% | 61.942 | 207.82 | 12872.7864 | 167.6567 | 982.4478 | 164713.9618 | 8741.9804 | [27 empty] | 0.41667 | 18.4167
| Week 37 | 88.6214 | 66.26% | 76.16 | 97.2857 | 81.2857 | 168 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3512.4286 | 3000.7143 | 3000.7143 | 20503 | 21193 | 41.4286 | No outage | 43.4286 | No outage | No outage | 57.1429 | 690 | -502 | 127.8571 | 98.67% | 146.3512 | 83.39% | 100% | 88.93% | 60.535 | 202.8257 | 12278.0546 | 143.7387 | 990.3483 | 142351.332 | 8708.1355 | [27 empty] | 0.75 | 21.75 | 3.3333
| Week 38 | 87.5286 | 0.64029 | #REF! | 98.4286 | 78.1429 | 142 | 44 | 168 | 0 | 24 | 57 | 0 | 0 | 0 | 0 | 3523.2857 | 3013.7143 | 2779.2857 | 19032 | 19693 | 41.5714 | No outage | 43.4286 | No outage | 399 | 57 | 661 | -423 | 120.2857 | 97.4% | 146.8036 | 77.27% | 100% | 87.91% | 60.088 | 186.18 | 11187.1838 | 154.264 | 997.5457 | 153885.3853 | 8680.2193
| Week 39 | 85.322 | 0.65044 | 72.736 | 97.8 | 76 | 134 | 74 | 168 | 0 | 32 | 88 | 0 | 0 | 15 | 20 | 3533.2857 | 3074.5714 | 2737.7143 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Date | Plant Status Whether Normal Operation or Tripping (State full detail for trippings/return to normal).
| 2018-09-01 | Plant load restricted 119~123 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-09-02 | Plant load restricted 119~123 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-09-03 | Plant load restricted 119~124 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-09-04 | Plant load restricted 119~123 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-09-05 | Plant load restricted 119~122 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-09-06 | Plant load restricted 119~123 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-09-07 | Plant load restricted 120~124 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2018-09-08 | Plant load restricted 118~123 MW from 0000~2400 hrs; both DBs kept off to remain within contractual heatrate.
| 2018-09-09 | Plant load restricted 119~122 MW from 0000~2400 hrs; both DBs kept off to remain within contractual heatrate.
| 2018-09-10 | Plant load restricted 119~122 MW from 0000~2400 hrs; both DBs kept off to remain within contractual heatrate.
| 2018-09-11 | Plant load restricted 118~123 MW from 0000~2400 hrs; both DBs kept off to remain within contractual heatrate.
| 2018-09-12 | Plant load restricted 119~123 MW from 0000~2400 hrs; both DBs kept off to remain within contractual heatrate.
| 2018-09-13 | Plant load restricted 120~124 MW from 0000~2400 hrs; both DBs kept off to remain within contractual heatrate.
| 2018-09-14 | Plant load restricted 121~124 MW from 0000~2400 hrs; both DBs kept off to remain within contractual heatrate.
| 2018-09-15 | Plant load restricted 122~125 MW from 0000~2400 hrs; both DBs kept off to remain within contractual heatrate.
| 2018-09-16 | Plant load restricted 122~125 MW from 0000~2400 hrs; both DBs kept off to remain within contractual heatrate.
| 2018-09-17 | Plant load restricted 121~124 MW from 0000~2400 hrs; both DBs kept off to remain within contractual heatrate.
| 2018-09-18 | Plant load restricted 120~125 MW from 0000~2400 hrs; both DBs kept off to remain within contractual heatrate.
| 2018-09-19 | Plant load restricted 120~125 MW from 0000~2400 hrs; both DBs kept off to remain within contractual heatrate.
| 2018-09-20 | Plant load restricted 120~126 MW from 0000~2400 hrs; both DBs kept off to remain within contractual heatrate.
| 2018-09-21 | Plant load restricted 120~125 MW from 0000~2400 hrs; both DBs kept off to remain within contractual heatrate.
| 2018-09-22 | CT-1 de-synch @ 2303 hrs to achieve NPCC demand of 45% of complex export.
| 2018-09-23 | CT-1 remained shutdown and at standby mode at NPCC demand.
| 2018-09-24 | CT-1 synch @ 0731 hrs to achieve maximum load as per NPCC demand.
| 2018-09-25 | Plant load increased from 125 to 138 MW by increasing duct burners firing at 1100 hrs to achieve maximum export. CT-1 de-synch @ 2219 hrs to achieve NPCC demand of 45% of complex export.
| 2018-09-26 | CT-1 synch @ 1606 hrs after receiving NPCC maximum load demand. CT-1 de-synch @ 2200 hrs to achieve NPCC demand of 45% of complex export.
| 2018-09-27 | CT-1 remained shutdown and in standby mode throughout the day as per NPCC demand.
| 2018-09-28 | Plant load reduced to 0 MW as per NPCC demand. STG de-synch @ 2244 hrs and CT-2 de-synch @ 2245 hrs and put in standby mode (CT-1 already shutdown and in standby mode).
| 2018-09-29 | Plant remained shutdown and in standby mode throughout the day as per NPCC demand.
| 2018-09-30 | Plant remained shutdown and in standby mode throughout the day as per NPCC demand.
0.88333
0.1
0.1

## Oct
Monthly Operational Returns Kabirwala
2018-10-01
| Date | Site Avg. Ambient Temp.F | Site Avg. Relative Humidty % | Site Avg. Ambient Wetbulb Temp.F | Site Ambient Temp |  | Base load hours |  |  |  | Standby hours |  |  |  | Plant ambient corrected Max Load |  | Corrected Plant Capacity | Ambient Corrected Daclared Avail'y (MWH) | Plant WAPDA Dispatch (MWH) | Net Plant Export (MWH) | Gross Generation | CT1 Average Cap (MW) | CT1 Unavail minutes | CT2 Average Cap (MW) | CT2 Unavail minutes | ST Average Cap (MW) | ST Unavail minutes | Plant Aux Load including Colony Load MWH | Differenece (+/-) MW | Maximum Daily Generation | Daily Load Factor | Avg. Corrected Plant Capacity | Plant Capacity Factor | Plant Availability Factor | Equivalent Plant Availability | LBtu gas flow (mmscf/day) | 1 LBtu gas (Average Btu/scf) | LBTU MMBTU | 1 HBtu gas flow (mmscf/day) | 1 HBtu gas (Average Btu/scf) | HBTU MMBTU | HHV Net Heat Rate (Btu/Kwh) | Avg. declared availability | CT1 Derated MW | CT1 derated mintutes | CT-2 derated MW | CT-2 derated mintutes | ST derated MW | ST derated mintutes | WAPDA Backfeed (MWH) | CT-1 Gross Generation (MWH) | CT-2 Gross Generation (MWH) | STG Gross Generation (MWH) | CT-1 & CT-2 MWH difference | Base load Heat Rate | STG load | DB1 | DB2 | CT1 | CT1 Gas flow | CT2 Gas flow |  | Pamb | Freq. Hz | LBTU Gas Specific gravity | CT-1 compressor efficiency(%) | CT-2 compressor efficiency(%) |  | CT-1 Heat Rate (Btu/Kwh) | CT-2 Heat Rate (Btu/Kwh) |  | DB(1+2) | DB-1 Ops Hours | DB-2 Ops Hours | CT-1 Wetcomprssion Ops Hours | RO Operation Hours | CT1 T/G Brg |  | CT2 T/G Brg
[7 empty] | CT1 |  | CT2 |  | CT1 |  | CT2 | [43 empty] | mmscf/d | mmscf/d | WetC flow | HBTU KPPH | HBTU KPPH | LBTU KPPH | mbar | Hz | [7 empty] | mmscf/d |  |  |  |  | Supply air pressure | Seal air pressure | Supply air pressure | Seal air pressure
[5 empty] | Max | Min | hrs | min | hrs | min | hrs | min | hrs | min | hrs | min | [42 empty] | gpm | [17 empty] | Psi | "WC | Psi | "WC
Week 40 | 2018-10-01 | 85.7 | 59.9% | 70.7 | 100 | 76 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3539 | 3528 | 0 | 0 | 0 | 42 | 0 | 45 | 0 | 60 | 0 | 17 | 0 | 0 | no data | 147.4583 | no data | 100% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | no data | 147 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 995.13 | 50.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2018-10-02 | 85.4 | 60.3% | 70.5 | 99 | 75 | 3 | 45 | 4 | 9 | 19 | 32 | 16 | 51 | 3 | 0 | 3546 | 3288 | 797 | 686 | 719 | 42 | 0 | 45 | 0 | 60 | 0 | 45 | -111 | 148 | 20.24% | 147.75 | 19.35% | 100% | 96.58% | 2.506 | 174.87 | 438.2242 | 5.778 | 994.83 | 5748.1277 | 9018.0058 | 137 | 24 | 43 | 17 | 180 | 26 | 121 | 12 | 168 | 304 | 247 | 136 | 9018.0058 | 10.2917 | 0.381 | 0.467 | 30.05 | 22.55 | 18.94 | 26.11 | 995.8 | 49.97 | 0.9183 | 96.56 | 87.03 | -9.53 | 11907 | 11231 | -676 | 0.848 | 4.65 | 3.34 | 2.8 | 2.85 | 2.1 | 5 | 2.1 | -2.3
| 2018-10-03 | 84.8 | 58.4% | 69.1 | 98 | 73 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3544 | 3473 | 3473 | 3410 | 3521 | 42 | 0 | 45 | 0 | 60 | 0 | 111 | -63 | 148 | 99.13% | 147.6667 | 96.22% | 100% | 100% | 8.294 | 152.34 | 1263.508 | 29.278 | 988.626 | 28944.992 | 8858.7977 | 144.7083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1017 | 1076 | 1428 | 59 | 8858.7977 | 59.5 | 2.225 | 2.225 | 29.8 | 25.75 | 21.3 | 25.89 | 995.54 | 50.08 | 0.9255 | 96.51 | 86.99 | -9.52 | 12157 | 11283 | -874 | 4.45 | 24 | 24 | 24 | 5.08 | 2.1 | 5 | 2.1 | 0
| 2018-10-04 | 82.5 | 57% | 66.4 | 94 | 73 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3573 | 3457 | 3457 | 3401 | 3513 | 42 | 0 | 45 | 0 | 58 | 0 | 112 | -56 | 151 | 96.94% | 148.875 | 95.19% | 100% | 100% | 8.202 | 146.43 | 1201.0189 | 29.5 | 979.38 | 28891.71 | 8848.2002 | 144.0417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1024 | 1088 | 1401 | 64 | 8848.2002 | 58.375 | 2.027 | 2.027 | 29.18 | 26.38 | 22.15 | 25.87 | 997.38 | 50.11 | 0.927 | 96.05 | 87.03 | -9.02 | 12111 | 11508 | -603 | 4.054 | 24 | 24 | 23.97 | 6.9 | 2.1 | 5 | 2.1 | 0
| 2018-10-05 | 81.8 | 54.9% | 65 | 91 | 73 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 13 | 16 | 3578 | 3459 | 3228 | 3212 | 3315 | 42 | 0 | 45 | 0 | 58 | 0 | 103 | -16 | 148 | 93.33% | 149.0833 | 89.77% | 100% | 95.68% | 8.535 | 167.85 | 1432.5998 | 26.933 | 976.9799 | 26313 | 8638.107 | 144.125 | 0 | 0 | 0 | 0 | 14 | 644 | 0 | 967 | 1094 | 1254 | 127 | 8638.107 | 52.25 | 1.331 | 1.335 | 29.23 | 25.27 | 21.71 | 28.53 | 1000.1 | 50.1 | 0.9198 | 90.33 | 87.04 | -3.29 | 12283 | 11426 | -857 | 2.666 | 24 | 24 | 12.17 | 7.05 | 2.1 | 4.9 | 2.1 | 0
| 2018-10-06 | 83.3 | 55.2% | 66.3 | 94 | 73 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 7 | 17 | 3562 | 3381 | 3152 | 3125 | 3223 | 42 | 0 | 45 | 0 | 58 | 0 | 98 | -27 | 149 | 90.13% | 148.4167 | 87.73% | 100% | 93.27% | 8.501 | 171.51 | 1458.0065 | 25.835 | 987.416 | 25509.8924 | 8629.7276 | 140.875 | 0 | 0 | 0 | 0 | 14 | 1003 | 0 | 973 | 1090 | 1160 | 117 | 8629.7276 | 48.3333 | 0.857 | 0.773 | 28.6 | 25 | 21.37 | 28.18 | 999.08 | 50.08 | 0.9188 | 91.33 | 87.09 | -4.24 | 12084 | 11299 | -785 | 1.63 | 17.25 | 17.25 | 15.55 | 4.83 | 2.1 | 5 | 2.1 | 0
| 2018-10-07 | 82.84 | 59.78% | 67.9 | 94.8 | 72.76 | 22 | 16 | 24 | 0 | 1 | 26 | 0 | 0 | 2 | 50 | 3566 | 3184 | 3031 | 2983 | 3079 | 42 | 0 | 45 | 0 | 58 | 0 | 96 | -48 | 149 | 86.1% | 148.5833 | 83.65% | 100% | 90.14% | 8.482 | 166.19 | 1409.6236 | 24.481 | 991.63 | 24276.094 | 8610.6998 | 132.6667 | 15 | 18 | 0 | 0 | 16 | 1270 | 0 | 940 | 1087 | 1052 | 147 | 8610.6998 | 43.8333 | 0.177 | 0.309 | 26.21 | 25.28 | 21.3 | 27.67 | 997.5 | 50.12 | 0.9207 | 94.6 | 87.15 | -7.45 | 12121 | 11259 | -862 | 0.486 | 2.92 | 4.633 | 19.87 | 4.83 | 2.1 | 4.9 | 2.1 | 0
Week 41 | 2018-10-08 | 82.4 | 62.4% | 68.7 | 94 | 73 | 12 | 47 | 24 | 0 | 10 | 27 | 0 | 0 | 12 | 32 | 3571 | 3377 | 2609 | 2583 | 2679 | 42 | 0 | 45 | 0 | 58 | 0 | 96 | -26 | 147 | 75.94% | 148.7917 | 72.33% | 100% | 89.3% | 8.483 | 166.63 | 1413.5223 | 21.205 | 1006.178 | 21336.0045 | 8807.4049 | 140.7083 | 22 | 46 | 0 | 0 | 31 | 688 | 0 | 544 | 1081 | 1054 | 537 | 8807.4049 | 43.9167 | 1.12 | 1.787 | 28.41 | 13.74 | 21.07 | 27.56 | 994.96 | 50.12 | 0.9206 | 95.83 | 87.21 | -8.62 | 11580 | 11203 | -377 | 2.907 | 12.7 | 24 | 11.8 | 5.62 | 2.1 | 5 | 2 | 0
| 2018-10-09 | 77.4 | 58.7% | 63.5 | 88 | 69 | 0 | 38 | 12 | 1 | 22 | 21 | 6 | 50 | 0 | 25 | 3617 | 3169 | 998 | 998 | 1046 | 42 | 0 | 45 | 0 | 58 | 0 | 55 | 0 | 131 | 33.27% | 150.7083 | 27.59% | 100% | 85.9% | 5.872 | 170.21 | 999.4731 | 8.151 | 1011.657 | 8246.0162 | 9264.0174 | 132.0417 | 20 | 61 | 17 | 309 | 32 | 718 | 7 | 46 | 711 | 289 | 665 | 9264.0174 | 12.0417 | 0.09 | 0.4 | 0 | 1.54 | 14.2 | 19.93 | 996.7 | 50.06 | 0.9193 | 87.8 | 86.9 | -0.9 | 12451 | 11212 | -1239 | 0.49 | 0.6 | 3.8 | 0 | 0 | 2 | 3.7 | 2 | -0.7
| 2018-10-10 | 79 | 53% | 63 | 92 | 69 | 7 | 41 | 24 | 0 | 15 | 35 | 0 | 0 | 7 | 29 | 3604 | 3528 | 2254 | 2235 | 2322 | 43 | 0 | 46 | 0 | 58 | 0 | 87 | -19 | 148 | 65.37% | 150.1667 | 62.01% | 100% | 84.52% | 8.409 | 169.97 | 1429.2777 | 17.825 | 1016.662 | 18122.0001 | 8747.7753 | 147 | 24 | 44 | 0 | 0 | 32 | 991 | 0 | 343 | 1108 | 871 | 765 | 8747.7753 | 36.2917 | 0.6 | 1.52 | 30.3 | 8.76 | 21.33 | 27.65 | 997.1 | 50.08 | 0.9203 | 96.28 | 86.85 | -9.43 | 11523 | 11045 | -478 | 2.12 | 7.8 | 24 | 6.8 | 6.1 | 2 | 5 | 2.1 | -0.7
| 2018-10-11 | 80 | 53% | 63 | 91 | 69 | 16 | 52 | 16 | 52 | 0 | 0 | 0 | 0 | 16 | 36 | 3596 | 3506 | 3175 | 3141 | 3244 | 43 | 0 | 46 | 0 | 58 | 0 | 103 | -34 | 149 | 90.72% | 149.8333 | 87.35% | 100% | 89.45% | 8.354 | 170.24 | 1422.185 | 25.512 | 1017.874 | 25968.0015 | 8720.2122 | 146.0833 | 10 | 428 | 9 | 428 | 32 | 444 | 0 | 968 | 1043 | 1233 | 75 | 8720.2122 | 51.375 | 1.187 | 1.246 | 29.3 | 24.2 | 20.3 | 27.57 | 997.7 | 50.11 | 0.9197 | 92.8 | 86.9 | -5.9 | 11800 | 11296 | -504 | 2.433 | 17 | 17.1 | 17.5 | 6 | 2.1 | 4.8 | 2.1 | -0.5
| 2018-10-12 | 79.2 | 64.5% | 67.1 | 90 | 71 | 10 | 4 | 15 | 39 | 12 | 48 | 7 | 14 | 2 | 15 | 3605 | 3410 | 1752 | 1747 | 1810 | 43 | 0 | 46 | 0 | 58 | 0 | 63 | -5 | 144 | 52.37% | 150.2083 | 48.46% | 100% | 97.29% | 5.197 | 173.67 | 902.563 | 14.305 | 1016.25 | 14537.4562 | 8838.019 | 142.0833 | 22 | 68 | 18 | 67 | 37 | 82 | 0 | 444 | 742 | 624 | 298 | 8838.019 | 26 | 0.291 | 0.48 | 29.7 | 24.44 | 20.8 | 26.9 | 1000.2 | 50.1 | 0.9184 | 94.67 | 87.16 | -7.51 | 11673 | 11191 | -482 | 0.771 | 10.15 | 12.93 | 9 | 5.88 | 2.1 | 4.6 | 2 | -0.7
| 2018-10-13 | 79.3 | 63.2% | 66.5 | 90 | 71 | 17 | 34 | 24 | 0 | 5 | 57 | 0 | 0 | 3 | 30 | 3602 | 3313 | 2814 | 2763 | 2852 | 43 | 0 | 46 | 0 | 58 | 0 | 89 | -51 | 146 | 81.39% | 150.0833 | 76.71% | 100% | 93.01% | 8.308 | 164.46 | 1366.3337 | 22.218 | 1007.91 | 22393.7444 | 8599.3768 | 138.0417 | 18 | 30 | 0 | 0 | 19 | 750 | 0 | 761 | 1092 | 999 | 331 | 8599.3768 | 41.625 | 0.469 | 0.703 | 30.1 | 25.44 | 21.35 | 27.65 | 1000.54 | 50.04 | 0.9211 | 95.73 | 87.1 | -8.63 | 11695 | 11200 | -495 | 1.172 | 17.73 | 24 | 16.73 | 6.9 | 2.1 | 4.6 | 2 | -1
| 2018-10-14 | 79.3 | 56.9% | 63.7 | 91 | 69 | 23 | 29 | 24 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 3601 | 3210 | 3188 | 3119 | 3214 | 43 | 0 | 46 | 0 | 58 | 0 | 95 | -69 | 137 | 97.75% | 150.0417 | 86.61% | 100% | 91.03% | 8.305 | 165.91 | 1377.8826 | 25.264 | 1001.519 | 25302.376 | 8554.1066 | 133.75 | 17 | 16 | 0 | 0 | 13 | 1440 | 0 | 1023 | 1101 | 1090 | 78 | 8554.1066 | 45.4167 | 0.291 | 0.288 | 30 | 25.74 | 21.63 | 27.3 | 999.04 | 50.1 | 0.9208 | 96.03 | 86.97 | -9.06 | 11635 | 11215 | -420 | 0.579 | 23.5 | 24 | 23.5 | 8 | 2.1 | 4.5 | 2.1 | -1
Week 42 | 2018-10-15 | 79.47 | 57.14% | 63.95 | 92 | 69 | 14 | 10 | 24 | 0 | 9 | 15 | 0 | 0 | 13 | 46 | 3598 | 3503 | 2852 | 2677 | 2765 | 43 | 0 | 46 | 0 | 58 | 0 | 88 | -175 | 148 | 77.84% | 149.9167 | 74.4% | 100% | 90.3% | 8.285 | 165.98 | 1375.1443 | 21.961 | 1002.368 | 22013.0036 | 8736.7008 | 145.9583 | 25 | 35 | 0 | 0 | 32 | 614 | 0 | 612 | 1097 | 1056 | 485 | 8736.7008 | 44 | 1.12 | 1.512 | 29.4 | 15.52 | 21.6 | 27.31 | 999 | 50.1 | 0.9208 | 95.99 | 87.01 | -8.98 | 11674 | 11245 | -429 | 2.632 | 14.27 | 24 | 13.17 | 6.45 | 2.1 | 4.8 | 2.1 | -0.8
| 2018-10-16 | 78.5 | 57.6% | 63.4 | 90 | 66 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3614 | 3497 | 3497 | 3424 | 3530 | 43 | 0 | 46 | 0 | 58 | 0 | 106 | -73 | 149 | 98.71% | 150.5833 | 94.74% | 100% | 100% | 8.235 | 169.2 | 1393.362 | 28.3679 | 1003.325 | 28462.2433 | 8719.5109 | 145.7083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1041 | 1098 | 1391 | 57 | 8719.5109 | 57.9583 | 1.819 | 1.819 | 30.34 | 25.76 | 21.72 | 27.22 | 998 | 50.06 | 0.9199 | 96.54 | 86.97 | -9.57 | 11627 | 11265 | -362 | 3.638 | 24 | 24 | 24 | 7.93 | 2.1 | 5 | 2.05 | -0.8
| 2018-10-17 | 79.6 | 57.7% | 64.4 | 90 | 70 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3595 | 3490 | 3490 | 3415 | 3521 | 43 | 0 | 46 | 0 | 58 | 0 | 106 | -75 | 149 | 98.46% | 149.7917 | 94.99% | 100% | 100% | 8.133 | 170.01 | 1382.6913 | 28.3352 | 1002.859 | 28416.1606 | 8725.8717 | 145.4167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1037 | 1095 | 1389 | 58 | 8725.8717 | 57.875 | 1.819 | 1.819 | 30.24 | 25.75 | 21.72 | 27.23 | 998.29 | 50.11 | 0.9197 | 96.53 | 87.02 | -9.51 |  |  | 0 | 3.638 | 24 | 24 | 24 | 7.12 | 2.1 | 5 | 2.1 | -0.7
| 2018-10-18 | 79.8 | 55.2% | 63.8 | 91 | 71 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3598 | 3483 | 3483 | 3421 | 3529 | 43 | 0 | 46 | 0 | 58 | 0 | 108 | -62 | 149 | 98.69% | 149.9167 | 95.08% | 100% | 100% | 7.943 | 165.85 | 1317.3465 | 28.5128 | 998.7023 | 28475.749 | 8708.885 | 145.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1038 | 1101 | 1390 | 63 | 8708.885 | 57.9167 | 1.823 | 1.829 | 30.01 | 25.89 | 21.89 | 27.06 | 998.4 | 50.06 | 0.9209 | 96.36 | 87.03 | -9.33 | 11723 | 11309 | -414 | 3.652 | 24 | 24 | 24 | 6.6 | 2.1 | 4.9 | 2 | -0.8
| 2018-10-19 | 79.8 | 50.9% | 61.9 | 91 | 70 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3593 | 3526 | 3526 | 3448 | 3558 | 44 | 0 | 46 | 0 | 59 | 0 | 110 | -78 | 152 | 97.53% | 149.7083 | 95.96% | 100% | 100% | 7.9 | 165.06 | 1303.974 | 28.8796 | 992.7975 | 28671.6263 | 8693.6196 | 146.9167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1043 | 1109 | 1406 | 66 | 8693.6196 | 58.5833 | 1.863 | 1.865 | 29.99 | 26.14 | 22.13 | 27.16 | 1000.4 | 50.12 | 0.9211 | 95.96 | 86.95 | -9.01 | 11780 | 11341 | -439 | 3.728 | 24 | 24 | 24 | 7.58 | 2.1 | 4.89 | 2 | -0.75
| 2018-10-20 | 79.03 | 53.94% | 62.39 | 89 | 68 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3603 | 3532 | 3532 | 3451 | 3559 | 44 | 0 | 46 | 0 | 59 | 0 | 108 | -81 | 152 | 97.56% | 150.125 | 95.78% | 100% | 100% | 7.847 | 165.5 | 1298.6785 | 29.0745 | 986.4828 | 28681.5029 | 8687.3896 | 147.1667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1044 | 1108 | 1407 | 64 | 8687.3896 | 58.625 | 1.912 | 1.912 | 30.29 | 26.25 | 22.23 | 27.14 | 1002.3 | 50.08 | 0.921 | 96.23 | 86.95 | -9.28 | 11824 | 11382 | -442 | 3.824 | 24 | 24 | 24 | 7.72 | 2.1 | 4.75 | 2 | -0.8
| 2018-10-21 | 79 | 55% | 63 | 90 | 68 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3612 | 3531 | 3531 | 3457 | 3564 | 43 | 0 | 46 | 0 | 59 | 0 | 107 | -74 | 152 | 97.7% | 150.5 | 95.71% | 100% | 100% | 7.819 | 164.7 | 1287.7893 | 29.1246 | 986.677 | 28736.6034 | 8685.1006 | 147.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1044 | 1109 | 1411 | 65 | 8685.1006 | 58.7917 | 1.901 | 1.901 | 30.21 | 26.24 | 22.27 | 27.06 | 1003.33 | 50.1 | 0.9212 | 96.11 | 86.91 | -9.2 | 11813 | 11370 | -443 | 3.802 | 24 | 24 | 24 | 7.75 | 2.1 | 4.6 | 2 | -0.9
Week 43 | 2018-10-22 | 78 | 53% | 60 | 92 | 66 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3621 | 3538 | 3538 | 3479 | 3590 | 44 | 0 | 46 | 0 | 59 | 0 | 111 | -59 | 152 | 98.41% | 150.875 | 96.08% | 100% | 100% | 7.789 | 165.76 | 1291.1046 | 29.2243 | 988.879 | 28899.2761 | 8677.8904 | 147.4167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1049 | 1116 | 1425 | 67 | 8677.8904 | 59.375 | 1.956 | 1.956 | 30.3 | 26.21 | 22.25 | 27.08 | 1001.2 | 50.09 | 0.9209 | 95.82 | 86.83 | -8.99 | 11750 | 11317 | -433 | 3.912 | 24 | 24 | 24 | 8.2 | 2.1 | 4.5 | 2.1 | -1
| 2018-10-23 | 76.2 | 50% | 59 | 89 | 64 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3628 | 3570 | 3570 | 3499 | 3608 | 44 | 0 | 46 | 0 | 60 | 0 | 109 | -71 | 154 | 97.62% | 151.1667 | 96.44% | 100% | 100% | 7.792 | 162.58 | 1266.8234 | 29.3418 | 990.1844 | 29053.8417 | 8665.523 | 148.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1057 | 1119 | 1432 | 62 | 8665.523 | 59.6667 | 1.949 | 1.949 | 30.7 | 26.33 | 22.32 | 26.94 | 1000.1 | 50.1 | 0.9218 | 96 | 86.74 | -9.26 | 11710 | 11296 | -414 | 3.898 | 24 | 24 | 24 | 7.8 | 2.1 | 4.6 | 2.1 | -1
| 2018-10-24 | 76.3 | 55.1% | 60.6 | 88 | 65 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3629 | 3564 | 3564 | 3487 | 3597 | 44 | 0 | 46 | 0 | 60 | 0 | 110 | -77 | 153 | 97.96% | 151.2083 | 96.09% | 100% | 100% | 7.745 | 164.43 | 1273.5104 | 29.3629 | 991.4175 | 29110.9028 | 8713.6258 | 148.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1051 | 1110 | 1436 | 59 | 8713.6258 | 59.8333 | 2.008 | 2.008 | 30.7 | 26.2 | 22.24 | 26.77 | 1000.8 | 50.12 | 0.9213 | 96.19 | 86.79 | -9.4 | 11719 | 11327 | -392 | 4.016 | 24 | 24 | 24 | 7.55 | 2.1 | 4.8 | 2 | -1
| 2018-10-25 | 77.5 | 55.3% | 61.7 | 88 | 68 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3623 | 3567 | 3567 | 3495 | 3603 | 44 | 0 | 46 | 0 | 60 | 0 | 108 | -72 | 153 | 98.12% | 150.9583 | 96.47% | 100% | 100% | 7.725 | 165.36 | 1277.406 | 29.3898 | 993.6 | 29201.6953 | 8720.7729 | 148.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1046 | 1105 | 1452 | 59 | 8720.7729 | 60.5 | 2.128 | 2.128 | 30.61 | 26.04 | 22.05 | 27.01 | 1002.33 | 50.07 | 0.9211 | 96.28 | 86.84 | -9.44 | 11705 | 11320 | -385 | 4.256 | 24 | 24 | 24 | 7.63 | 2 | 4.7 | 2.1 | -1
| 2018-10-26 | 77.8 | 55.3% | 61.9 | 89 | 66 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3622 | 3569 | 3569 | 3497 | 3606 | 44 | 0 | 46 | 0 | 60 | 0 | 109 | -72 | 153 | 98.2% | 150.9167 | 96.55% | 100% | 100% | 7.717 | 163.93 | 1265.0478 | 29.4439 | 993.999 | 29267.227 | 8730.9908 | 148.7083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1047 | 1106 | 1453 | 59 | 8730.9908 | 60.5417 | 2.122 | 2.122 | 30.58 | 26.09 | 22.17 | 26.66 | 1004.46 | 50.1 | 0.9314 | 96.17 | 86.76 | -9.41 | 11706 | 11335 | -371 | 4.244 | 24 | 24 | 24 | 8.53 | 2.1 | 4.7 | 2 | -1
| 2018-10-27 | 78.2 | 55.7% | 62.1 | 91 | 68 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3617 | 3563 | 3563 | 3490 | 3599 | 43 | 0 | 46 | 0 | 60 | 0 | 109 | -73 | 153 | 98.01% | 150.7083 | 96.49% | 100% | 100% | 7.7 | 164.8 | 1268.96 | 29.4163 | 993.815 | 29234.3602 | 8740.2064 | 148.4583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1046 | 1102 | 1451 | 56 | 8740.2064 | 60.4583 | 2.122 | 2.122 | 30.45 | 26.09 | 22.1 | 26.8 | 1004.04 | 50.12 | 0.9212 | 96.13 | 86.68 | -9.45 | 11726 | 11365 | -361 | 4.244 | 24 | 24 | 24 | 8.08 | 2.1 | 4.7 | 2.1 | -1
| 2018-10-28 | 78.5 | 54.9% | 62.2 | 91 | 67 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3611 | 3551 | 3551 | 3481 | 3591 | 43 | 0 | 46 | 0 | 60 | 0 | 110 | -70 | 152 | 98.44% | 150.4583 | 96.4% | 100% | 100% | 7.666 | 161.93 | 1241.3554 | 29.3728 | 992.7142 | 29158.8158 | 8733.1718 | 147.9583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1044 | 1098 | 1449 | 54 | 8733.1718 | 60.375 | 2.122 | 2.122 | 30.36 | 26.05 | 22.08 | 26.6 | 1003.7 | 50.04 | 0.922 | 96.08 | 86.63 | -9.45 | 11738 | 11393 | -345 | 4.244 | 24 | 24 | 24 | 8.1 | 2.1 | 4.7 | 2 | -1
Week 44 | 2018-10-29 | 78.29 | 55.78% | 62.17 | 92 | 69 | 18 | 35 | 24 | 0 | 4 | 32 | 0 | 0 | 18 | 24 | 3610 | 3550 | 3159 | 3109 | 3209 | 43 | 0 | 46 | 0 | 60 | 0 | 100 | -50 | 150 | 89.14% | 150.4167 | 86.12% | 100% | 95.01% | 7.614 | 163.53 | 1245.1174 | 26.2288 | 994.014 | 26071.8143 | 8786.4045 | 147.9167 | 18 | 53 | 0 | 0 | 29 | 336 | 0 | 818 | 1095 | 1296 | 277 | 8786.4045 | 54 | 1.627 | 2.152 | 29.95 | 25.83 | 22.05 | 26.55 | 1003.08 | 50.06 | 0.9215 | 96.08 | 86.6 | -9.48 | 11780 | 11399 | -381 | 3.779 | 18.7833 | 24 | 18.43 | 7.48 | 2.1 | 4.8 | 2.1 | -0.8
| 2018-10-30 | 77.8 | 58.2% | 62.9 | 91 | 68 | 14 | 56 | 24 | 0 | 8 | 15 | 0 | 0 | 14 | 52 | 3618 | 3538 | 2873 | 2824 | 2921 | 43 | 0 | 46 | 0 | 60 | 0 | 97 | -49 | 151 | 80.6% | 150.75 | 78.05% | 100% | 92.2% | 7.65 | 165.15 | 1263.3975 | 23.7636 | 990.1107 | 23528.6045 | 8779.0375 | 147.4167 | 18 | 47 | 0 | 0 | 29 | 548 | 0 | 661 | 1091 | 1169 | 430 | 8779.0375 | 48.7083 | 1.295 | 2.067 | 29.85 | 16.88 | 22.06 | 26.52 | 1002.7 | 50.07 | 0.921 | 95.15 | 86.56 | -8.59 | 11826 | 11443 | -383 | 3.362 | 15.25 | 24 | 14.23 | 7.05 | 2 | 4.6 | 2 | -1
| 2018-10-31 | 77.6 | 60.1% | 63.9 | 91 | 67 | 15 | 3 | 22 | 36 | 6 | 58 | 0 | 0 | 13 | 35 | 3621 | 3353 | 2757 | 2707 | 2798 | 43 | 69 | 46 | 35 | 60 | 54 | 91 | -50 | 149 | 78.24% | 150.875 | 74.76% | 96.36% | 87.53% | 7.27 | 164.84 | 1198.3868 | 22.8777 | 991.456 | 22682.2528 | 8821.81 | 139.7083 | 21 | 50 | 27 | 49 | 29 | 571 | 0 | 650 | 1035 | 1113 | 385 | 8821.81 | 46.375 | 1.219 | 1.832 | 29.54 | 16.74 | 21.17 | 25.11 | 1002.79 | 50.07 | 0.9215 | 93.87 | 86.42 | -7.45 | 11876 | 11468 | -408 | 3.051 | 13.6667 | 21.62 | 12.85 | 3.81 | 2.1 | 4.8 | 2.1 | -1
| 2018-11-01 | [26 empty] | 0 | 0 |  | no data | no data | no data | #DIV/0! | no data |  |  | 0 |  |  | 0 | no data | 0 | [10 empty] | 0 | no data | 0 | [11 empty] | 0 |  |  | 0 | 0
| 2018-11-02 | [26 empty] | 0 | 0 |  | no data | no data | no data | #DIV/0! | no data |  |  | 0 |  |  | 0 | no data | 0 | [10 empty] | 0 | no data | 0 | [11 empty] | 0 |  |  | 0 | 0
| 2018-11-03 | [26 empty] | 0 | 0 |  | no data | no data | no data | #DIV/0! | no data |  |  | 0 |  |  | 0 | no data | 0 | [10 empty] | 0 | no data | 0 | [11 empty] | 0 |  |  | 0 | 0
| 2018-11-04 | [26 empty] | 0 | 0 |  | no data | no data | no data | #DIV/0! | no data |  |  | 0 |  |  | 0 | no data | 0 | [10 empty] | 0 | no data | 0 | [11 empty] | 0 |  |  | 0 | 0
| Monthly | 79.8171 | 56.71% | 64.2165 | 91.671 | 69.5729 | 585 | 50 | 671 | 17 | 15 | 21 | 53 | 55 | 3 | 47 | 111517 | 107208 | 91550 | 89954.15 | 92685 | 42.9355 | 2.2258 | 45.7097 | 1.129 | 58.9032 | 1.7419 | 2737.85 | -1786 | 144.0645 | 86.13% | 149.8884 | 80.66% | 99.88% | 95.85% | 230.278 | 160.2868 | 38064.3134 | 748.9626 | 964.2037 | 745255.0948 | 8707.9852 |  | 230 | 896 | 71 | 853 | 331 | 8452 | 7 | 21397 | 26659 | 30338 | 5262 | 8707.9852 | 1264.0833 | 35.03 | 39.848 | 717.54 | 563.15 | 536.03 | 668.45 | 1000.3464 | 50.088 | 0.92117 | 95.4092 | 86.8772 |  | 11773.5 | 11231.75 |  | 88.526 | 466.37 | 540.083 | 554.37 | 168.71
| Totals | Avg.F | % Avg. |  | M Avg | m Avg | hrs | min | hrs | min | hrs | min | hrs | min | Avg Int Avi | Avg Ext Avi | MWhr Total | MWhr Total | MWhr Total | MWhr Total | MWhr Total | MW Avg | Total min | Avg MW | Total min | Avg MW | Total min | MWhr | Total MW | Av Max D/Gen | Av. DailyLF | Avg. | Avg. |  | Avg. | Total | Avg. |  | Total | Avg. |  | Avg. | [7 empty] | Total |  |  |  |  | Avg.
| Weeks data | Site Avg. Amb. Temp F | Site Avg. Relative humidity % | Site Avg. Ambient Wetbulb Temp.F | M Avg: Site Maximum/Minumum Temperature; hrs: CT-1 Base Load Hours; hrs: CT-2 Base Load Hours; hrs: CT-1 stand by hours / min; hrs: CT-2 standby hours / min | Plant ambient Corrected maximum Load hours/min |  | Average Corrected Plant Capacity | Ambient Corrected Declared Avail'y (MWH) | Av Plant WAPDA Dispatch | Net Plant Export (MWH) | Gross Generation | CT1 Av Cap (MW) | CT1 Unavail minutes | CT2 Av Cap (MW) | CT2 Unavail minutes | ST Unavail minutes | ST Average Cap (MW) | Plant Aux Load including Colony Load MWH | Differenece (+/-) MW | Maximum Daily Generation | Daily Load Factor | Avg. Corrected Plant | Plant Capacity Facto | Plant Availability Factor | Equivalent Plant Availability | LBtu gas flow mmscf | 1 LBtu gas (Average Btu/scf) | LBTU MMBTU | PL gas flow (mscf/week) | 1 PL gas (Average Btu/scf) | HBTU MMBTU | Plant Net Heat Rate (Btu/Kwh) | [11 empty] | 59.75
| Week 40 | 83.7629 | 57.93% | 67.9857 | 95.8286 | 73.68 | 122 | 1 | 124 | 9 | 44 | 58 | 40 | 51 | 74 | 23 | 3558.2857 | 3395.7143 | no data | no data | no data | 42 | No outage | 45 | No outage | 412 | no data | no data | no data | no data | 80.98% | 148.2619 | 78.65% | 100% | 96.53% | no data | no data | #VALUE! | no data | no data | #VALUE! | 8767.2564 | [26 empty] | 7 | 56 | 7.9333 | 13.6667
| Week 41 | 79.5143 | 58.81% | 65.0714 | 90.8571 | 70.1429 | 89 | 243 | 140 | 32 | 67 | 203 | 14 | 64 | 42 | -5 | 3599.4286 | 3359 | 2398.5714 | 16586 | 17167 | 42.7143 | No outage | 320 | no data | 406 | no data | 588 | -204 | 143.1429 | 70.97% | 149.9762 | 65.87% | 100% | 90.07% | 52.928 | 168.7271 | 8930.3902 | 134.48 | 1011.15 | 135979.452 | 8790.1303 | [5 empty] | 0.27381 | [20 empty] | 21 | 36 | 21.6
| Week 42 | 79.3143 | 55.35% | 63.2629 | 90.4286 | 68.8571 | 158 | 10 | 168 | 0 | 9 | 15 | 0 | 0 | 157 | 46 | 3601.8571 | 3508.8571 | 3415.8571 | 23293 | 24026 | 43.2857 | No outage | 322 | no data | 409 | no data | 733 | -618 | 150.1429 | 95.21% | 150.0774 | 92.38% | 100% | 98.61% | 56.162 | 166.6143 | 9357.3915 | 165.131 | 997.7558 | 164760.3686 | 8708.154 | [5 empty] | 0.26672
| Week 43 | 77.5 | 54.19% | 61.0714 | 89.7143 | 66.2857 | 168 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 3621.5714 | 3560.2857 | 3560.2857 | 24428 | 25194 | 43.7143 | No outage | 322 | no data | 419 | no data | 766 | -494 | 152.8571 | 98.11% | 150.8988 | 96.36% | 100% | 100% | 54.134 | 164.1129 | 8884.0854 | 205.5519 | 992.087 | 203925.3402 | 8711.7402
| Week 44 | 77.8967 | 0.58027 | 62.99 | 91.3333 | 68 | 48 | 34 | 70 | 36 | 19 | 45 | 0 | 0 | 46 | 51 | 3616.3333 | 3480.3333 | 2929.6667 | 8640 | 8928 | 43 | #REF! | #REF! | no data | #REF! | no data | 288 | -149 | 150 | 82.66% | 150.6806 | 79.64% | #DIV/0! | 91.58% | 22.534 | 164.5067 | 3706.9932 | 72.8701 | 991.8602 | 72277.004 | 8795.7507
| Date | Plant Status Whether Normal Operation or Tripping (State full detail for trippings/return to normal).
| 2018-10-01 | Plant remained shutdown and in standby mode throughout the day as per NPCC demand.
| 2018-10-02 | NPCC demand of maximum load received at 1515 hrs. CT-2 synch at 1609hrs, ST at 1859hrs & CT-1 at 1932hrs.
| 2018-10-03 | Normal operation. Plant remained at maximum load from 0000 to 2400 hrs. | [42 empty] | 17 | 16 | 20 | 53
| 2018-10-04 | Normal operation. Plant remained at maximum load from 0000 to 2400 hrs. | [42 empty] | 49.35
| 2018-10-05 | NPCC load demand of 120 MW received from 0111 to 1155 hrs. | [42 empty] | 24.675
| 2018-10-06 | NPCC load demand of 122 MW received from 0009 to 0954 hrs.
| 2018-10-07 | Plant remained at 122 MW on NPCC load demand from 0250 hrs to 0534 hrs. CT-1 desynch at 2234 hrs to achieve NPCC demand of 45% of complex export.
| 2018-10-08 | Plant remained at 68 MW on NPCC load demand of 45% load from 0000 hrs to 0815 hrs. CT-1 synch at 0855 hrs after receiving maximum load demand from NPCC. CT-1 desynch at 2228 hrs to achieve NPCC demand of 45% of complex export.
| 2018-10-09 | CT-2 de-synch @ 1021 hrs, STG de-synch at 1020hrs to achieve 0 MW load as per NPCC demand. CT-2 synch @ 1711 hrs, STG synch @ 2157hrs and CT-1 synch @ 2221hrs & load increased to maximum as per NPCC demand.
| 2018-10-10 | CT-1 de-synch @ 0003 hrs to achieve 70 MW load as per NPCC demand. CT-1 synch @ 1538 hrs & load increased to maximum as per NPCC demand.
| 2018-10-11 | Plant load rduced to 100 MW at 0542 hrs as per NPCC demand. Plant load increased to maximum at 1238 hrs as per NPCC demand.
| 2018-10-12 | CT-1 @ 0015 hrs, ST @ 0214 hrs & CT-2 @ 0219 hrs de-synch against 0 MW despatch. CT-2 @ 0933 hrs, STG @ 1055 hrs & CT-1 @ 1128 hrs Synch against Max. load despatch. CT-1 Desynch @ 2225 hrs against 68 MW despatch.
| 2018-10-13 | CT-1 Synch @ 0557 hrs against NPCC maximum load demand. From 1000~2400 hrs plant remained at 130 MW to improve plant heat rate
| 2018-10-14 | CT-1 Desynch @ 2345 hrs against 68 MW despatch.
| 2018-10-15 | CT-1 synch @ 0916 hrs against NPCC maximum load demand.
| 2018-10-16 | Normal operation. Plant remained at maximum load from 0000 to 2400 hrs.
| 2018-10-17 | Normal operation. Plant remained at maximum load from 0000 to 2400 hrs.
| 2018-10-18 | Normal operation. Plant remained at maximum load from 0000 to 2400 hrs.
| 2018-10-19 | Normal operation. Plant remained at maximum load from 0000 to 2400 hrs.
| 2018-10-20 | Normal operation. Plant remained at maximum load from 0000 to 2400 hrs.
| 2018-10-21 | Normal operation. Plant remained at maximum load from 0000 to 2400 hrs.
| 2018-10-22 | Normal operation. Plant remained at maximum load from 0000 to 2400 hrs.
| 2018-10-23 | Normal operation. Plant remained at maximum load from 0000 to 2400 hrs.
| 2018-10-24 | Normal operation. Plant remained at maximum load from 0000 to 2400 hrs.
| 2018-10-25 | Normal operation. Plant remained at maximum load from 0000 to 2400 hrs.
| 2018-10-26 | Normal operation. Plant remained at maximum load from 0000 to 2400 hrs.
| 2018-10-27 | Normal operation. Plant remained at maximum load from 0000 to 2400 hrs.
| 2018-10-28 | Normal operation. Plant remained at maximum load from 0000 to 2400 hrs.
| 2018-10-29 | CT-1 desynch @0205hrs at NPCC demand of 73 MW. CT-1 synch @0623 hrs after receiving maximum load demand from NPCC. CT-1 again desynch at 2346 hrs to achieve NPCC load demand of 72 MW.
| 2018-10-30 | CT-1 synch @ 0547 hrs after receiving maximum load demand from NPCC. CT-1 again desynch at 2132 hrs to achieve NPCC load demand of 72 MW.
| 2018-10-31 | CT-1 synch at 0658 hrs to achieve NPCC maximum load demand. At 2138hrs load reduced to 120 MW on NPCC demand. CT-1 de-synch @ 2251 hrs, STG @ 2306 hrs and CT-2 @ 2325 hrs to avail scheduled outage of complex for 2018.
[11 empty] | 15.8833 | 17.4667 | 1048
[8 empty] | 23 | 6 | 23.1 | -1.5833 | -16.5833 | -995 |  |  |  | 0.9
[5 empty] | min: 21; hrs: 31; min: 21.5167; hrs: -14.5833; min: -875 |  |  | 54
[5 empty] | min: 9.52 | 0.52 | 31.2

## Nov
Monthly Operational Returns Kabirwala
2018-11-01
| Date | Site Avg. Ambient Temp.F | Site Avg. Relative Humidty % | Site Avg. Ambient Wetbulb Temp.F | Site Ambient Temp |  | Base load hours |  |  |  | Standby hours |  |  |  | Plant ambient corrected Max Load |  | Corrected Plant Capacity | Ambient Corrected Daclared Avail'y (MWH) | Plant WAPDA Dispatch (MWH) | Net Plant Export (MWH) | Gross Generation | CT1 Average Cap (MW) | CT1 Unavail minutes | CT2 Average Cap (MW) | CT2 Unavail minutes | ST Average Cap (MW) | ST Unavail minutes | Plant Aux Load including Colony Load MWH | Differenece (+/-) MW | Maximum Daily Generation | Daily Load Factor | Avg. Corrected Plant Capacity | Plant Capacity Factor | Plant Availability Factor | Equivalent Plant Availability | LBtu gas flow (mmscf/day) | 1 LBtu gas (Average Btu/scf) | LBTU MMBTU | 1 HBtu gas flow (mmscf/day) | 1 HBtu gas (Average Btu/scf) | HBTU MMBTU | HHV Net Heat Rate (Btu/Kwh) | Avg. declared availability | CT1 Derated MW | CT1 derated mintutes | CT-2 derated MW | CT-2 derated mintutes | ST derated MW | ST derated mintutes | WAPDA Backfeed (MWH) | CT-1 Gross Generation (MWH) | CT-2 Gross Generation (MWH) | STG Gross Generation (MWH) | CT-1 & CT-2 MWH difference | Base load Heat Rate | STG load | DB1 | DB2 | CT1 | CT1 Gas flow | CT2 Gas flow |  | Pamb | Freq. Hz | LBTU Gas Specific gravity | CT-1 compressor efficiency(%) | CT-2 compressor efficiency(%) |  | CT-1 Heat Rate (Btu/Kwh) | CT-2 Heat Rate (Btu/Kwh) |  | DB(1+2) | DB-1 Ops Hours | DB-2 Ops Hours | CT-1 Wetcomprssion Ops Hours | RO Operation Hours | CT1 T/G Brg |  | CT2 T/G Brg
[7 empty] | CT1 |  | CT2 |  | CT1 |  | CT2 | [43 empty] | mmscf/d | mmscf/d | WetC flow | HBTU KPPH | HBTU KPPH | LBTU KPPH | mbar | Hz | [7 empty] | mmscf/d |  |  |  |  | Supply air pressure | Seal air pressure | Supply air pressure | Seal air pressure
[5 empty] | Max | Min | hrs | min | hrs | min | hrs | min | hrs | min | hrs | min | [42 empty] | gpm | [17 empty] | Psi | "WC | Psi | "WC
Week 44 | 2018-10-29 | 78.29 | 55.78% | 62.17 | 92 | 69 | 18 | 35 | 24 | 0 | 4 | 32 | 0 | 0 | 18 | 24 | 3610 | 3550 | 3159 | 3109 | 3209 | 43 | 0 | 46 | 0 | 60 | 0 | 100 | -50 | 150 | 89.14% | 150.4167 | 86.12% | 100% | 95.01% | 7.614 | 163.53 | 1245.1174 | 26.228 | 994.01 | 26070.8943 | 8786.1086 | 147.9167 | 18 | 53 | 0 | 0 | 29 | 336 | 0 | 818 | 1095 | 1296 | 277 | 8786.1086 | 54 | 1.627 | 2.152 | 29.95 | 25.83 | 22.05 | 26.55 | 1003.08 | 50.06 | 0.9215 | 96.08 | 86.6 | -9.48 | 11780 | 11399 | -381 | 3.779 | 18.7833 | 24 | 18.43 | 7.48 | 2.1 | 4.8 | 2.1 | -0.8
| 2018-10-30 | 77.8 | 58.2% | 62.9 | 91 | 68 | 14 | 56 | 24 | 0 | 8 | 15 | 0 | 0 | 14 | 52 | 3618 | 3538 | 2873 | 2824 | 2921 | 43 | 0 | 46 | 0 | 60 | 0 | 97 | -49 | 151 | 80.6% | 150.75 | 78.05% | 100% | 92.2% | 7.65 | 165.15 | 1263.3975 | 23.763 | 990.11 | 23527.9839 | 8778.8178 | 147.4167 | 18 | 47 | 0 | 0 | 29 | 548 | 0 | 661 | 1091 | 1169 | 430 | 8778.8178 | 48.7083 | 1.295 | 2.067 | 29.85 | 16.88 | 22.06 | 26.52 | 1002.7 | 50.07 | 0.921 | 95.15 | 86.56 | -8.59 | 11826 | 11443 | -383 | 3.362 | 15.25 | 24 | 14.23 | 7.05 | 2 | 4.6 | 2 | -1
| 2018-10-31 | 77.6 | 60.1% | 63.9 | 91 | 67 | 15 | 3 | 22 | 36 | 6 | 58 | 0 | 0 | 13 | 35 | 3621 | 3353 | 2757 | 2707 | 2798 | 43 | 69 | 46 | 35 | 60 | 54 | 91 | -50 | 149 | 78.24% | 150.875 | 74.76% | 96.36% | 87.53% | 7.27 | 164.84 | 1198.3868 | 22.878 | 991.46 | 22682.6219 | 8821.9463 | 139.7083 | 21 | 50 | 27 | 49 | 29 | 571 | 0 | 650 | 1035 | 1113 | 385 | 8821.9463 | 46.375 | 1.219 | 1.832 | 29.54 | 16.74 | 21.17 | 25.11 | 1002.79 | 50.07 | 0.9215 | 93.87 | 86.42 | -7.45 | 11876 | 11468 | -408 | 3.051 | 13.6667 | 21.62 | 12.85 | 3.81 | 2.1 | 4.8 | 2.1 | -1
| 2018-11-01 | 76.75 | 62.41% | 64.3 | 89 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3624 | 0 | 0 | 0 | 0 | 43 | 1440 | 46 | 1440 | 60 | 1440 | 6 | 0 | 0 | no data | 151 | no data | 0% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1002.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3 | 0 | 0 | 0 | 0
| 2018-11-02 | 73.6 | 68.5% | 63.8 | 82 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3648 | 0 | 0 | 0 | 0 | 43 | 1440 | 46 | 1440 | 60 | 1440 | 9 | 0 | 0 | no data | 152 | no data | 0% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2018-11-03 | 69.7 | 56.2% | 56.3 | 82 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3696 | 0 | 0 | 0 | 0 | 43 | 1440 | 46 | 1440 | 60 | 1440 | 6 | 0 | 0 | no data | 154 | no data | 0% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2018-11-04 | 67.4 | 47.3% | 50.9 | 87 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 0 | 0 | 0 | 0 | 43 | 1440 | 46 | 1440 | 60 | 1440 | 5 | 0 | 0 | no data | 155 | no data | 0% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Week 45 | 2018-11-05 | 67.1 | 51.6% | 52 | 82.5 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 0 | 0 | 0 | 0 | 43 | 1440 | 46 | 1440 | 60 | 1440 | 6 | 0 | 0 | no data | 155 | no data | 0% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2018-11-06 | 69.3 | 44.9% | 51.5 | 86 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 0 | 0 | 0 | 0 | 43 | 1440 | 46 | 1440 | 60 | 1440 | 0 | 0 | 0 | no data | 155 | no data | 0% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2018-11-07 | 69.6 | 48.1% | 53 | 86 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 0 | 0 | 0 | 0 | 43 | 1440 | 46 | 1440 | 60 | 1440 | 0 | 0 | 0 | no data | 155 | no data | 0% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2018-11-08 | 70.4 | 48.6% | 53.8 | 88 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 0 | 0 | 0 | 0 | 43 | 1440 | 46 | 1440 | 60 | 1440 | 8 | 0 | 0 | no data | 155 | no data | 0% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2018-11-09 | 69.7 | 53.3% | 54.7 | 83 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 0 | 0 | 0 | 0 | 43 | 1440 | 46 | 1440 | 60 | 1440 | 8 | 0 | 0 | no data | 155 | no data | 0% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2018-11-10 | 68.9 | 61.6% | 56.8 | 80 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 0 | 0 | 0 | 0 | 43 | 1440 | 46 | 1440 | 60 | 1440 | 8 | 0 | 0 | no data | 155 | no data | 0% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2018-11-11 | 68.7 | 65.5% | 57.7 | 76 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 0 | 0 | 0 | 0 | 43 | 1440 | 46 | 1440 | 60 | 1440 | 6 | 0 | 0 | no data | 155 | no data | 0% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Week 46 | 2018-11-12 | 67.11 | 66.5% | 57.38 | 75 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 0 | 0 | 0 | 0 | 43 | 1440 | 46 | 1440 | 60 | 1440 | 8 | 0 | 0 | no data | 155 | no data | 0% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2018-11-13 | 69 | 63.99% | 58.07 | 77 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 0 | 0 | 0 | 0 | 43 | 1440 | 46 | 1440 | 60 | 1440 | 7 | 0 | 0 | no data | 155 | no data | 0% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2018-11-14 | 68.2 | 63.4% | 57.2 | 82 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 0 | 0 | 0 | 0 | 43 | 1440 | 46 | 1440 | 60 | 1440 | 8 | 0 | 0 | no data | 155 | no data | 0% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2018-11-15 | 67.3 | 64.9% | 56.9 | 81 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 0 | 0 | 0 | 0 | 43 | 1440 | 46 | 1440 | 60 | 1440 | 6 | 0 | 0 | no data | 155 | no data | 0% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2018-11-16 | 67.2 | 66.1% | 57.2 | 81 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 0 | 0 | 0 | 0 | 43 | 1440 | 46 | 1440 | 60 | 1440 | 7 | 0 | 0 | no data | 155 | no data | 0% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2018-11-17 | 67.86 | 63.81% | 57.1 | 84 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3684 | 0 | 0 | 0 | 0 | 43 | 1440 | 46 | 1440 | 60 | 1440 | 7 | 0 | 0 | no data | 153.5 | no data | 0% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2018-11-18 | 69.8 | 60.5% | 57.02 | 82 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3679 | 0 | 0 | 0 | 0 | 43 | 1440 | 46 | 1440 | 60 | 1440 | 6 | 0 | 0 | no data | 153.2917 | no data | 0% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Week 47 | 2018-11-19 | 67.9 | 63.4% | 56.8 | 80 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3686 | 0 | 0 | 0 | 0 | 43 | 1440 | 46 | 1440 | 60 | 1440 | 6 | 0 | 0 | no data | 153.5833 | no data | 0% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2018-11-20 | 68.6 | 59.5% | 55.8 | 87 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3677 | 0 | 0 | 0 | 0 | 43 | 1440 | 46 | 1440 | 60 | 1440 | 7 | 0 | 0 | no data | 153.2083 | no data | 0% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2018-11-21 | 68.2 | 61% | 56.4 | 84 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3684 | 0 | 0 | 0 | 0 | 43 | 1440 | 46 | 1440 | 60 | 1440 | 7 | 0 | 0 | no data | 153.5 | no data | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2018-11-22 | 68.3 | 58.7% | 55.8 | 84 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3682 | 0 | 0 | 0 | 0 | 43 | 1440 | 46 | 1440 | 60 | 1440 | 6 | 0 | 0 | no data | 153.4167 | no data | 0% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2018-11-23 | 66.9 | 58.9% | 54.2 | 84 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3692 | 0 | 0 | 0 | 0 | 43 | 1440 | 46 | 1440 | 60 | 1440 | 6 | 0 | 0 | no data | 153.8333 | no data | 0% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2018-11-24 | 68.4 | 53.3% | 54.7 | 83 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3678 | 0 | 0 | 0 | 0 | 43 | 1440 | 46 | 1440 | 60 | 1440 | 6 | 0 | 0 | no data | 153.25 | no data | 0% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2018-11-25 | 67.73 | 63.76% | 56.86 | 89.75 | 56.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3680 | 0 | 0 | 0 | 0 | 43 | 1440 | 46 | 1440 | 60 | 1440 | 7 | 0 | 0 | no data | 153.3333 | no data | 0% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Week 48 | 2018-11-26 | 66.9 | 63.6% | 54.2 | 84 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3687 | 0 | 0 | 0 | 0 | 43 | 1440 | 46 | 1440 | 60 | 1440 | 6 | 0 | 0 | no data | 153.625 | no data | 0% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2018-11-27 | 68 | 70% | 59 | 79 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3680 | 0 | 0 | 0 | 0 | 43 | 1440 | 46 | 1440 | 60 | 1440 | 5 | 0 | 0 | no data | 153.3333 | no data | 0% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2018-11-28 | 68 | 65% | 58 | 86 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3680 | 0 | 0 | 0 | 0 | 43 | 1440 | 46 | 1440 | 60 | 1440 | 7 | 0 | 0 | no data | 153.3333 | no data | 0% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2018-11-29 | 67.3 | 67.6% | 57.8 | 82 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3691 | 0 | 0 | 0 | 0 | 43 | 1440 | 46 | 1440 | 60 | 1440 | 4 | 0 | 0 | no data | 153.7917 | no data | 0% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2018-11-30 | 67.3 | 67.6% | 57.8 | 82 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3691 | 0 | 0 | 0 | 0 | 43 | 1440 | 46 | 1440 | 60 | 1440 | 2 | 0 | 0 | no data | 153.7917 | no data | 0% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2018-12-01 | [26 empty] | 0 | 0 |  | no data | no data | no data | #DIV/0! | no data |  |  | 0 |  |  | 0 | no data | 0 | [10 empty] | 0 | no data | 0 | [11 empty] | 0 |  |  | 0 | 0
| 2018-12-02 | [26 empty] | 0 | 0 |  | no data | no data | no data | #DIV/0! | no data |  |  | 0 |  |  | 0 | no data | 0 | [10 empty] | 0 | no data | 0 | [11 empty] | 0 |  |  | 0 | 0
| Monthly | 68.705 | 60.32% | 56.4343 | 82.9417 | 58.1057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110899 | 0 | 0 | 0 | 0 | 43 | 43200 | 46 | 43200 | 60 | 43200 | 154 | 0 | 0 | #DIV/0! | 154.0264 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 154 | 0 | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1003.9533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3 | 0 | 0 | 0 | 0
| Totals | Avg.F | % Avg. |  | M Avg | m Avg | hrs | min | hrs | min | hrs | min | hrs | min | Avg Int Avi | Avg Ext Avi | MWhr Total | MWhr Total | MWhr Total | MWhr Total | MWhr Total | MW Avg | Total min | Avg MW | Total min | Avg MW | Total min | MWhr | Total MW | Av Max D/Gen | Av. DailyLF | Avg. | Avg. |  | Avg. | Total | Avg. |  | Total | Avg. |  | Avg. | [7 empty] | Total |  |  |  |  | Avg.
| Weeks data | Site Avg. Amb. Temp F | Site Avg. Relative humidity % | Site Avg. Ambient Wetbulb Temp.F | M Avg: Site Maximum/Minumum Temperature; hrs: CT-1 Base Load Hours; hrs: CT-2 Base Load Hours; hrs: CT-1 stand by hours / min; hrs: CT-2 standby hours / min | Plant ambient Corrected maximum Load hours/min |  | Average Corrected Plant Capacity | Ambient Corrected Declared Avail'y (MWH) | Av Plant WAPDA Dispatch | Net Plant Export (MWH) | Gross Generation | CT1 Av Cap (MW) | CT1 Unavail minutes | CT2 Av Cap (MW) | CT2 Unavail minutes | ST Unavail minutes | ST Average Cap (MW) | Plant Aux Load including Colony Load MWH | Differenece (+/-) MW | Maximum Daily Generation | Daily Load Factor | Avg. Corrected Plant | Plant Capacity Facto | Plant Availability Factor | Equivalent Plant Availability | LBtu gas flow mmscf | 1 LBtu gas (Average Btu/scf) | LBTU MMBTU | PL gas flow (mscf/week) | 1 PL gas (Average Btu/scf) | HBTU MMBTU | Plant Net Heat Rate (Btu/Kwh) | [11 empty] | 0
| Week 44 | 74.4486 | 58.36% | 60.61 | 87.7143 | 65 | 48 | 34 | 70 | 36 | 19 | 45 | 0 | 0 | 46 | 51 | 3648.1429 | 1491.5714 | 1255.5714 | 1234.2857 | 1275.4286 | 43 | 5829 | 46 | 5795 | 420 | no data | no data | -149 | 64.2857 | 82.66% | 152.006 | 79.64% | 42.34% | 91.58% | 22.534 | 70.5029 | 1588.7114 | 72.869 | 425.0829 | 30975.3627 | 8795.6242
| Week 45 | 69.1 | 53.37% | 54.2143 | 83.0714 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 3720 | no data | no data | no data | no data | 43 | 10080 | 322 | 1440 | 420 | 1440 | 36 | no data | no data | #DIV/0! | 155 | #DIV/0! | no data | #DIV/0! | no data | no data | #VALUE! | no data | no data | #VALUE! | #DIV/0! | [5 empty] | 0.27381
| Week 46 | 68.0671 | 64.17% | 57.2671 | 80.2857 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3709 | no data | no data | no data | no data | 43 | 10080 | 322 | 1440 | 420 | 1440 | 49 | no data | no data | #DIV/0! | 154.5417 | #DIV/0! | no data | #DIV/0! | no data | no data | #VALUE! | no data | no data | #VALUE! | #DIV/0! | [5 empty] | 0.26672
| Week 47 | 68.0043 | 59.79% | 55.7943 | 84.5357 | 58.1671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3682.7143 | no data | no data | no data | no data | 43 | 10080 | 322 | 1440 | 420 | 1440 | 45 | no data | no data | #DIV/0! | 153.4464 | #DIV/0! | no data | 0% | no data | no data | #VALUE! | no data | no data | #VALUE! | #DIV/0!
| Week 48 | 67.5 | 0.6676 | 57.36 | 82.6 | 54.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3685.8 | no data | no data | no data | no data | 43 | #REF! | #REF! | 1440 | #REF! | 1440 | 24 | no data | no data | #DIV/0! | 153.575 | #DIV/0! | no data | #DIV/0! | no data | no data | #VALUE! | no data | no data | #VALUE! | #DIV/0!
| Date | Plant Status Whether Normal Operation or Tripping (State full detail for trippings/return to normal).
| 2018-11-01 | FKPCL complex is shutdown for "Scheduled Outage of 2018".
| 2018-11-02 | FKPCL complex remained shutdown for "Scheduled Outage of 2018".
| 2018-11-03 | FKPCL complex remained shutdown for "Scheduled Outage of 2018". | [42 empty] | 17 | 16 | 20 | 53
| 2018-11-04 | FKPCL complex remained shutdown for "Scheduled Outage of 2018". | [42 empty] | 49.35
| 2018-11-05 | FKPCL complex remained shutdown for "Scheduled Outage of 2018". | [42 empty] | 24.675
| 2018-11-06 | FKPCL complex remained shutdown for "Scheduled Outage of 2018".
| 2018-11-07 | FKPCL complex remained shutdown for "Scheduled Outage of 2018".
| 2018-11-08 | FKPCL complex remained shutdown for "Scheduled Outage of 2018".
| 2018-11-09 | FKPCL complex remained shutdown for "Scheduled Outage of 2018".
| 2018-11-10 | FKPCL complex remained shutdown for "Scheduled Outage of 2018".
| 2018-11-11 | FKPCL complex remained shutdown for "Scheduled Outage of 2018".
| 2018-11-12 | FKPCL complex remained shutdown for "Scheduled Outage of 2018".
| 2018-11-13 | FKPCL complex remained shutdown for "Scheduled Outage of 2018".
| 2018-11-14 | FKPCL complex remained shutdown for "Scheduled Outage of 2018".
| 2018-11-15 | FKPCL complex remained shutdown for "Scheduled Outage of 2018".
| 2018-11-16 | FKPCL complex remained shutdown for "Scheduled Outage of 2018".
| 2018-11-17 | FKPCL complex remained shutdown for "Scheduled Outage of 2018".
| 2018-11-18 | FKPCL complex remained shutdown for "Scheduled Outage of 2018".
| 2018-11-19 | FKPCL complex remained shutdown for "Scheduled Outage of 2018".
| 2018-11-20 | FKPCL complex remained shutdown for "Scheduled Outage of 2018".
| 2018-11-21 | FKPCL complex remained shutdown for "Scheduled Outage of 2018".
| 2018-11-22 | FKPCL complex remained shutdown for "Scheduled Outage of 2018".
| 2018-11-23 | FKPCL complex remained shutdown for "Scheduled Outage of 2018".
| 2018-11-24 | FKPCL complex remained shutdown for "Scheduled Outage of 2018".
| 2018-11-25 | FKPCL complex remained shutdown for "Scheduled Outage of 2018".
| 2018-11-26 | FKPCL complex remained shutdown for "Scheduled Outage of 2018".
| 2018-11-27 | FKPCL complex remained shutdown for "Scheduled Outage of 2018".
| 2018-11-28 | FKPCL complex remained shutdown for "Scheduled Outage of 2018".
| 2018-11-29 | FKPCL complex remained shutdown for "Scheduled Outage of 2018".
| 2018-11-30 | FKPCL complex remained shutdown for "Scheduled Outage of 2018".
[11 empty] | 15.8833 | 17.4667 | 1048
[8 empty] | 23 | 6 | 23.1 | -1.5833 | -16.5833 | -995 |  |  |  | 0.9
[5 empty] | min: 21; hrs: 31; min: 21.5167; hrs: -14.5833; min: -875 |  |  | 54
[5 empty] | min: 9.52 | 0.52 | 31.2
Note on AC10: ops.e: EDG in operation
Note on AC11: ops.e: EDG in opeartion
Note on AC12: ops.e: EDG in operation

## Dec
Monthly Operational Returns Kabirwala
2018-12-01
| Date | Site Avg. Ambient Temp.F | Site Avg. Relative Humidty % | Site Avg. Ambient Wetbulb Temp.F | Site Ambient Temp |  | Base load hours |  |  |  | Standby hours |  |  |  | Plant ambient corrected Max Load |  | Corrected Plant Capacity | Ambient Corrected Daclared Avail'y (MWH) | Plant WAPDA Dispatch (MWH) | Net Plant Export (MWH) | Gross Generation | CT1 Average Cap (MW) | CT1 Unavail minutes | CT2 Average Cap (MW) | CT2 Unavail minutes | ST Average Cap (MW) | ST Unavail minutes | Plant Aux Load including Colony Load MWH | Differenece (+/-) MW | Maximum Daily Generation | Daily Load Factor | Avg. Corrected Plant Capacity | Plant Capacity Factor | Plant Availability Factor | Equivalent Plant Availability | LBtu gas flow (mmscf/day) | 1 LBtu gas (Average Btu/scf) | LBTU MMBTU | 1 HBtu gas flow (mmscf/day) | 1 HBtu gas (Average Btu/scf) | HBTU MMBTU | HHV Net Heat Rate (Btu/Kwh) | Avg. declared availability | CT1 Derated MW | CT1 derated mintutes | CT-2 derated MW | CT-2 derated mintutes | ST derated MW | ST derated mintutes | WAPDA Backfeed (MWH) | CT-1 Gross Generation (MWH) | CT-2 Gross Generation (MWH) | STG Gross Generation (MWH) | CT-1 & CT-2 MWH difference | Base load Heat Rate | STG load | DB1 | DB2 | CT1 | CT1 Gas flow | CT2 Gas flow |  | Pamb | Freq. Hz | LBTU Gas Specific gravity | CT-1 compressor efficiency(%) | CT-2 compressor efficiency(%) |  | CT-1 Heat Rate (Btu/Kwh) | CT-2 Heat Rate (Btu/Kwh) |  | DB(1+2) | DB-1 Ops Hours | DB-2 Ops Hours | CT-1 Wetcomprssion Ops Hours | RO Operation Hours |  | CT1 T/G Brg |  | CT2 T/G Brg
[7 empty] | CT1 |  | CT2 |  | CT1 |  | CT2 | [43 empty] | mmscf/d | mmscf/d | WetC flow | HBTU KPPH | HBTU KPPH | LBTU KPPH | mbar | Hz | [7 empty] | mmscf/d | [5 empty] | Supply air pressure | Seal air pressure | Supply air pressure | Seal air pressure
[5 empty] | Max | Min | hrs | min | hrs | min | hrs | min | hrs | min | hrs | min | [42 empty] | gpm | [18 empty] | Psi | "WC | Psi | "WC
Week 48 | 2018-11-26 | 66.9 | 63.6% | 54.2 | 84 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3687 | 0 | 0 | 0 | 0 | 43 | 1440 | 46 | 1440 | 60 | 1440 | 6 | 0 | 0 | no data | 153.625 | no data | 0% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
| 2018-11-27 | 68 | 70% | 59 | 79 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3680 | 0 | 0 | 0 | 0 | 43 | 1440 | 46 | 1440 | 60 | 1440 | 5 | 0 | 0 | no data | 153.3333 | no data | 0% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
| 2018-11-28 | 68 | 65% | 58 | 86 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3680 | 0 | 0 | 0 | 0 | 43 | 1440 | 46 | 1440 | 60 | 1440 | 7 | 0 | 0 | no data | 153.3333 | no data | 0% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
| 2018-11-29 | 67.3 | 67.6% | 57.8 | 82 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3691 | 0 | 0 | 0 | 0 | 43 | 1440 | 46 | 1440 | 60 | 1440 | 4 | 0 | 0 | no data | 153.7917 | no data | 0% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
| 2018-11-30 | 67.3 | 67.6% | 57.8 | 82 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3691 | 0 | 0 | 0 | 0 | 43 | 1440 | 46 | 1440 | 60 | 1440 | 5 | 0 | 0 | no data | 153.7917 | no data | 0% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
| 2018-12-01 | 65.2 | 66.2% | 54.9 | 89 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3696 | 0 | 0 | 0 | 0 | 43 | 1440 | 46 | 1440 | 60 | 1440 | 5 | 0 | 0 | no data | 154 | no data | 0% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
| 2018-12-02 | 66.1 | 58% | 53.4 | 87 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3691 | 0 | 0 | 0 | 0 | 43 | 1440 | 46 | 1440 | 60 | 1440 | 5 | 0 | 0 | no data | 153.7917 | no data | 0% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
Week 49 | 2018-12-03 | 66 | 60.7% | 54.7 | 86 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3694 | 0 | 0 | 0 | 0 | 43 | 1440 | 46 | 1440 | 60 | 1440 | 8 | 0 | 0 | no data | 153.9167 | no data | 0% | no data | 0 | 0 | 0 | 0 | 990 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
| 2018-12-04 | 65.1 | 62.8% | 54 | 79 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3698 | 0 | 0 | 0 | 0 | 43 | 1440 | 46 | 1440 | 60 | 1440 | 7 | 0 | 0 | no data | 154.0833 | no data | 0% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
| 2018-12-05 | 63.69 | 65.44% | 53.68 | 81.34 | 54.71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3704 | 0 | 0 | 0 | 0 | 43 | 1440 | 46 | 1440 | 60 | 1440 | 7 | 0 | 0 | no data | 154.3333 | no data | 0% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
| 2018-12-06 | 63.5 | 64.2% | 53.4 | 78.5 | 53.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3702 | 0 | 0 | 0 | 0 | 43 | 1440 | 46 | 1440 | 60 | 1440 | 6 | 0 | 0 | no data | 154.25 | no data | 0% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
| 2018-12-07 | 63.08 | 69.83% | 54.89 | 78.34 | 53.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3705 | 0 | 0 | 0 | 0 | 43 | 1440 | 46 | 1440 | 60 | 1440 | 7 | 0 | 0 | no data | 154.375 | no data | 0% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
| 2018-12-08 | 63 | 69% | 55 | 77 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3705 | 0 | 0 | 0 | 0 | 43 | 1440 | 46 | 1440 | 60 | 1440 | 7 | 0 | 0 | no data | 154.375 | no data | 0% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
| 2018-12-09 | 63.4 | 67.5% | 54.5 | 76 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3700 | 0 | 0 | 0 | 0 | 43 | 1440 | 46 | 1440 | 60 | 1440 | 6 | 0 | 0 | no data | 154.1667 | no data | 0% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Week 50 | 2018-12-10 | 63 | 74% | 57 | 72 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3705 | 0 | 0 | 0 | 0 | 43 | 1440 | 46 | 1440 | 60 | 1440 | 7 | 0 | 0 | no data | 154.375 | no data | 0% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
| 2018-12-11 | 59.2 | 73.5% | 53.2 | 69 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3719 | 0 | 0 | 0 | 0 | 43 | 1440 | 46 | 1440 | 60 | 1440 | 3 | 0 | 0 | no data | 154.9583 | no data | 0% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1004 | 50.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
| 2018-12-12 | 58.6 | 70.1% | 51.3 | 75 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3719 | 0 | 0 | 0 | 0 | 43 | 1440 | 46 | 1440 | 60 | 1440 | 2 | 0 | 0 | no data | 154.9583 | no data | 0% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1004 | 50.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
| 2018-12-13 | 57.2 | 76.4% | 51.6 | 72 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3719 | 0 | 0 | 0 | 0 | 43 | 1440 | 46 | 1440 | 60 | 1440 | 7 | 0 | 0 | no data | 154.9583 | no data | 0% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1004 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
| 2018-12-14 | 59 | 68.8% | 50.4 | 75 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3718 | 0 | 0 | 0 | 0 | 43 | 1440 | 46 | 1440 | 60 | 1440 | 9 | 0 | 0 | no data | 154.9167 | no data | 0% | no data | 0 | 0 | 0 | 0 | 989.5 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1004 | 50.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
| 2018-12-15 | 55.8 | 72.3% | 49.7 | 77 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3718 | 0 | 0 | 0 | 0 | 43 | 1440 | 46 | 1440 | 60 | 1440 | 13 | 0 | 0 | no data | 154.9167 | no data | 0% | no data | 0 | 0 | 0 | 0 | 984.5 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1004 | 50.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
| 2018-12-16 | 57.7 | 60.6% | 47.6 | 73 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3716 | 0 | 0 | 299 | 322 | 43 | 1440 | 46 | 1440 | 60 | 1440 | 34 | 0 | 72 | 18.63% | 154.8333 | 8.046% | 0% | 0% | 1.853 | 164.84 | 305.4485 | 3.263 | 990.3445 | 3231.4941 | 11829.2395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 264 | 58 | 264 | 11829.2395 | 2.4167 | 0 | 0 | 0 | 0 | 16.21 | 15.45 | 1008 | 50.08 | 0 | 0 | 86.81 | 86.81 | 0 | 13220 | 13220 | 0 | 0 | 0 | 0 | 5.5 |  | 0 | 0 | 0 | 0
Week 51 | 2018-12-17 | 58 | 60.8% | 47.8 | 75 | 47 | 0 | 0 | 7 | 25 | 0 | 0 | 0 | 56 | 0 | 0 | 3713 | 664 | 569 | 571 | 597 | 43 | 1440 | 48 | 870 | 60 | 1005 | 37 | 2 | 79 | 31.49% | 154.7083 | 15.38% | 24.59% | 16.71% | 2.7 | 164.8412 | 445.0712 | 4.945 | 1013 | 5009.285 | 9552.2876 | 69.8947 | 0 | 0 | 15 | 156 | 34 | 435 | 11 | 0 | 415 | 182 | 415 | 9552.2876 | 7.5833 | 0 | 0.4 | 0 | 0 | 8.68 | 7.63 | 1004 | 50.07 | 0 | 0 | 86.5 | 86.5 | 0 | 10912 | 10912 | 0.4 | 0 | 5 | 0 | 0 |  | 0 | 0 | 0 | 0
| 2018-12-18 | 57.8 | 63.3% | 48.2 | 77.2 | 46.7 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 35 | 0 | 0 | 3715 | 1824 | 1824 | 0 | 0 | 44 | 1440 | 48 | 0 | 30 | 0 | 15 | -1824 | 0 | no data | 154.7917 | no data | 63.93% | no data | 0 | 0 | 0 | 0.00046 | 1002 | 0.46092 | no data | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1003 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
| 2018-12-19 | 57.4 | 61.7% | 47.3 | 77.5 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 3718 | 0 | 0 | 0 | 0 | 44 | 1440 | 48 | 0 | 30 | 0 | 14 | 0 | 0 | no data | 154.9167 | no data | 63.93% | no data | 0 | 0 | 0 | 0.009843 | 1003 | 9.8725 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1001.2 | 50.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
| 2018-12-20 | 56.8 | 64% | 47.6 | 73 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 3718 | 0 | 0 | 0 | 0 | 44 | 1440 | 48 | 0 | 30 | 0 | 12 | 0 | 0 | no data | 154.9167 | no data | 63.93% | no data | 0 | 0 | 0 | 0.009987 | 1003 | 10.017 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1007 | 50.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
| 2018-12-21 | 57 | 68% | 48 | 73 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 3719 | 0 | 0 | 0 | 0 | 44 | 1440 | 48 | 0 | 30 | 0 | 13 | 0 | 0 | no data | 154.9583 | no data | 63.93% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1006 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 |  | 0 | 0 | 0 | 0
| 2018-12-22 | 56 | 69% | 48 | 75 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 3718 | 0 | 0 | 0 | 0 | 44 | 1440 | 48 | 0 | 30 | 0 | 11 | 0 | 0 | no data | 154.9167 | no data | 63.93% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1006 | 49.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
| 2018-12-23 | 56.2 | 69.5% | 48.9 | 69 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 3720 | 0 | 0 | 0 | 0 | 44 | 1440 | 48 | 0 | 30 | 0 | 10 | 0 | 0 | no data | 155 | no data | 63.93% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1006.1 | 50.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
Week 52 | 2018-12-24 | 55.2 | 69.6% | 47.9 | 71 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 3720 | 0 | 0 | 0 | 0 | 44 | 1440 | 48 | 0 | 30 | 0 | 11 | 0 | 0 | no data | 155 | no data | 63.93% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1006.5 | 50.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
| 2018-12-25 | 55 | 72.8% | 48.6 | 70 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 3720 | 0 | 0 | 0 | 0 | 44 | 1440 | 48 | 0 | 30 | 0 | 11 | 0 | 0 | no data | 155 | no data | 63.93% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1006.3 | 49.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
| 2018-12-26 | 53 | 72% | 47 | 65 | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 3720 | 0 | 0 | 0 | 0 | 44 | 1440 | 48 | 0 | 30 | 0 | 13 | 0 | 0 | no data | 155 | no data | 63.93% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1003.6 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
| 2018-12-27 | 55.1 | 67.3% | 47.1 | 72 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 3720 | 0 | 0 | 0 | 0 | 44 | 1440 | 48 | 0 | 30 | 0 | 9 | 0 | 0 | no data | 155 | no data | 63.93% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1006.1 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
| 2018-12-28 | 54.5 | 67.9% | 46.3 | 73 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 3720 | 0 | 0 | 0 | 0 | 44 | 1440 | 48 | 0 | 30 | 0 | 9 | 0 | 0 | no data | 155 | no data | 63.93% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1002.7 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
| 2018-12-29 | 55.08 | 67.58% | 47.25 | 70.4 | 43.9 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 3719 | 0 | 0 | 0 | 0 | 44 | 1440 | 48 | 0 | 30 | 0 | 6 | 0 | 0 | no data | 154.9583 | no data | 63.93% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1002.2 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
| 2018-12-30 | 56 | 70.7% | 48.8 | 70 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 3719 | 0 | 0 | 0 | 0 | 44 | 1440 | 48 | 0 | 30 | 0 | 7 | 0 | 0 | no data | 154.9583 | no data | 63.93% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1002.2 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
| 2018-12-31 | 55.2 | 70.5% | 48.3 | 69.2 | 46.2 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 3720 | 0 | 0 | 0 | 0 | 44 | 1440 | 48 | 0 | 30 | 0 | 8 | 0 | 0 | no data | 155 | no data | 63.93% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1005.6 | 50 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
| Monthly | 59.8723 | 67.35% | 51.2523 | 75.996 | 49.6753 | 0 | 0 | 7 | 25 | 0 | 0 | 6 | 31 | 0 | 0 | 111312 | 2488 | 2393 | 872.53 | 919 | 43.3667 | 43200 | 46.8 | 26790 | 49 | 26925 | 304.47 | -1822 | 5.0333 | 0.25061 | 154.6 | 11.71% | 29.67% | 8.354% | 4.553 | 10.9894 | 750.5198 | 8.2283 | 257.2692 | 8261.1295 | 10328.1827 | 4.8632 | 0 | 0 | 15 | 156 | 34 | 435 | 258 | 0 | 679 | 240 | 679 | 10328.1827 | 10 | 0 | 0.4 | 0 | 0 | 24.89 | 23.08 | 1004.7167 | 29.3228 | 0 | 0 | 5.777 | 5.777 | 0 | 804.4 | 804.4 | 0.4 | 0 | 5 | 0 | 8 |  | 0 | 0 | 0 | 0
| Totals | Avg.F | % Avg. |  | M Avg | m Avg | hrs | min | hrs | min | hrs | min | hrs | min | Avg Int Avi | Avg Ext Avi | MWhr Total | MWhr Total | MWhr Total | MWhr Total | MWhr Total | MW Avg | Total min | Avg MW | Total min | Avg MW | Total min | MWhr | Total MW | Av Max D/Gen | Av. DailyLF | Avg. | Avg. |  | Avg. | Total | Avg. |  | Total | Avg. |  | Avg. | [7 empty] | Total |  |  |  |  | Avg.
| Weeks data | Site Avg. Amb. Temp F | Site Avg. Relative humidity % | Site Avg. Ambient Wetbulb Temp.F | M Avg: Site Maximum/Minumum Temperature; hrs: CT-1 Base Load Hours; hrs: CT-2 Base Load Hours; hrs: CT-1 stand by hours / min; hrs: CT-2 standby hours / min | Plant ambient Corrected maximum Load hours/min |  | Average Corrected Plant Capacity | Ambient Corrected Declared Avail'y (MWH) | Av Plant WAPDA Dispatch | Net Plant Export (MWH) | Gross Generation | CT1 Av Cap (MW) | CT1 Unavail minutes | CT2 Av Cap (MW) | CT2 Unavail minutes | ST Unavail minutes | ST Average Cap (MW) | Plant Aux Load including Colony Load MWH | Differenece (+/-) MW | Maximum Daily Generation | Daily Load Factor | Avg. Corrected Plant | Plant Capacity Facto | Plant Availability Factor | Equivalent Plant Availability | LBtu gas flow mmscf | 1 LBtu gas (Average Btu/scf) | LBTU MMBTU | PL gas flow (mscf/week) | 1 PL gas (Average Btu/scf) | HBTU MMBTU | Plant Net Heat Rate (Btu/Kwh) | [11 empty] | 0
| Week 48 | 66.9714 | 65.43% | 56.4429 | 84.1429 | 54.1429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3688 | no data | no data | no data | no data | 43 | 10080 | 46 | 10080 | 420 | 1440 | 37 | no data | no data | #DIV/0! | 153.6667 | #DIV/0! | no data | #DIV/0! | no data | no data | #VALUE! | no data | no data | #VALUE! | #DIV/0!
| Week 49 | 63.9671 | 65.64% | 54.31 | 79.4543 | 54.7943 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3701.1429 | no data | no data | no data | no data | 43 | 10080 | 322 | 1440 | 420 | 1440 | 48 | no data | no data | #DIV/0! | 154.2143 | #DIV/0! | no data | #DIV/0! | no data | no data | #VALUE! | no data | 141.4286 | #VALUE! | #DIV/0! | [5 empty] | 0.27381
| Week 50 | 58.6429 | 70.81% | 51.5429 | 73.2857 | 50.1429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3716.2857 | no data | no data | no data | no data | 43 | 10080 | 322 | 1440 | 420 | 1440 | 75 | no data | no data | 18.63% | 154.8452 | 8.046% | no data | 0% | no data | no data | #VALUE! | no data | no data | #VALUE! | 11829.2395 | [5 empty] | 0.26672
| Week 51 | 57.0286 | 65.19% | 47.9714 | 74.2429 | 46.6714 | 0 | 0 | 7 | 25 | 0 | 0 | 127 | 31 | 0 | 0 | 3717.2857 | 355.4286 | 341.8571 | 571 | 597 | 43.8571 | 10080 | 336 | 124.2857 | 240 | 143.5714 | 112 | -1822 | 11.2857 | 31.49% | 154.8869 | 15.38% | 58.31% | 16.71% | 2.7 | 23.5487 | 63.5816 | 4.9653 | 574.4286 | 2852.2044 | 9552.2876
| Week 52 | 54.84 | 0.69697 | 47.5643 | 70.2 | 44.9857 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 0 | 0 | 3719.7143 | no data | no data | no data | no data | 44 | #REF! | #REF! | no data | #REF! | no data | 66 | no data | no data | #DIV/0! | 154.9881 | #DIV/0! | 63.93% | #DIV/0! | no data | no data | #VALUE! | no data | no data | #VALUE! | #DIV/0!
| Date | Plant Status Whether Normal Operation or Tripping (State full detail for trippings/return to normal).
| 2018-12-01 | FKPCL complex is shutdown for "Scheduled Outage of 2018".
| 2018-12-02 | FKPCL complex is shutdown for "Scheduled Outage of 2018".
| 2018-12-03 | FKPCL complex is shutdown for "Scheduled Outage of 2018".
| 2018-12-04 | FKPCL complex is shutdown for "Scheduled Outage of 2018". | [42 empty] | 17 | 16 | 20 | 53
| 2018-12-05 | FKPCL complex is shutdown for "Scheduled Outage of 2018". | [42 empty] | 49.35
| 2018-12-06 | FKPCL complex is shutdown for "Scheduled Outage of 2018". | [42 empty] | 24.675
| 2018-12-07 | FKPCL complex is shutdown for "Scheduled Outage of 2018".
| 2018-12-08 | FKPCL complex is shutdown for "Scheduled Outage of 2018".
| 2018-12-09 | FKPCL complex is shutdown for "Scheduled Outage of 2018".
| 2018-12-10 | FKPCL complex remained shutdown due to ongoing major overhauling activities for steam turbine.
| 2018-12-11 | FKPCL complex remained shutdown due to ongoing major overhauling activities for steam turbine.
| 2018-12-12 | FKPCL complex remained shutdown due to ongoing major overhauling activities for steam turbine.
| 2018-12-13 | FKPCL complex remained shutdown due to ongoing major overhauling activities for steam turbine.
| 2018-12-14 | FKPCL complex remained shutdown due to ongoing major overhauling activities for steam turbine. CT-1 started for balancing purpose but M/C tripped on inlet bearing high vibration at 1680 rpm.
| 2018-12-15 | FKPCL complex remained shutdown due to ongoing major overhauling activities for steam turbine. CT-1 started for balancing purpose but M/C tripped on inlet and exhaust bearing high vibration.
| 2018-12-16 | CT-2 & STG started for "Testing & Balancing" Purpose. CT-2 synch @ 1143 hrs & de-synch @ 2000 hrs. STG synch @ 1644 hrs & de-synch @ 1950 hrs.
| 2018-12-17 | CT-2 synch @1334 hrs & ST synch @1538 hrs. Complex is declared commercially available from time of synchronization after completion of scheduled outage activities. ST desynch @ 2253 hrs & CT-2 desynch @ 2304 hrs after receiving NPCC minimum load demand.
| 2018-12-18 | Plant remained shutdown on NPCC demand from 0000~0700 hrs and from 0700~2400 due to suspension of HBTU gas by M/S SNGPL.
| 2018-12-19 | Plant remained shutdown due to suspension of HBTU gas by M/S SNGPL.
| 2018-12-20 | Plant remained shutdown due to suspension of HBTU gas by M/S SNGPL.
| 2018-12-21 | Plant remained shutdown due to suspension of HBTU gas by M/S SNGPL.
| 2018-12-22 | Plant remained shutdown due to suspension of HBTU gas by M/S SNGPL.
| 2018-12-23 | Plant remained shutdown due to suspension of HBTU gas by M/S SNGPL.
| 2018-12-24 | Plant remained shutdown due to suspension of HBTU gas by M/S SNGPL.
| 2018-12-25 | Plant remained shutdown due to suspension of HBTU gas by M/S SNGPL.
| 2018-12-26 | Plant remained shutdown due to suspension of HBTU gas by M/S SNGPL.
| 2018-12-27 | Plant remained shutdown due to suspension of HBTU gas by M/S SNGPL.
| 2018-12-28 | Plant remained shutdown due to suspension of HBTU gas by M/S SNGPL.
| 2018-12-29 | Plant remained shutdown due to suspension of HBTU gas by M/S SNGPL.
| 2018-12-30 | Plant remained shutdown due to suspension of HBTU gas by M/S SNGPL.
| 2018-12-31 | Plant remained shutdown due to suspension of HBTU gas by M/S SNGPL.
[11 empty] | 15.8833 | 17.4667 | 1048
[8 empty] | 23 | 6 | 23.1 | -1.5833 | -16.5833 | -995 |  |  |  | 0.9
[5 empty] | min: 21; hrs: 31; min: 21.5167; hrs: -14.5833; min: -875 |  |  | 54
[5 empty] | min: 9.52 | 0.52 | 31.2
Note on AN13: ops.e: CT-1 started for test run on Siemens demand after completion of major inspection activities.