## Jan
Monthly Operational Returns Kabirwala
2019-01-01
| Date | Site Avg. Ambient Temp.F | Site Avg. Relative Humidty % | Site Avg. Ambient Wetbulb Temp.F | Site Ambient Temp |  | Base load hours |  |  |  | Standby hours |  |  |  | Plant ambient corrected Max Load |  | Corrected Plant Capacity | Ambient Corrected Daclared Avail'y (MWH) | Plant WAPDA Dispatch (MWH) | Net Plant Export (MWH) | Gross Generation | CT1 Average Cap (MW) | CT1 Unavail minutes | CT2 Average Cap (MW) | CT2 Unavail minutes | ST Average Cap (MW) | ST Unavail minutes | Plant Aux Load including Colony Load MWH | Differenece (+/-) MW | Maximum Daily Generation | Daily Load Factor | Avg. Corrected Plant Capacity | Plant Capacity Factor | Plant Availability Factor | Equivalent Plant Availability | LBtu gas flow (mmscf/day) | 1 LBtu gas (Average Btu/scf) | LBTU MMBTU | 1 HBtu gas flow (mmscf/day) | 1 HBtu gas (Average Btu/scf) | HBTU MMBTU | HHV Net Heat Rate (Btu/Kwh) | Avg. declared availability | CT1 Derated MW | CT1 derated mintutes | CT-2 derated MW | CT-2 derated mintutes | ST derated MW | ST derated mintutes | WAPDA Backfeed (MWH) | CT-1 Gross Generation (MWH) | CT-2 Gross Generation (MWH) | STG Gross Generation (MWH) | CT-1 & CT-2 MWH difference | Base load Heat Rate | STG load | DB1 | DB2 | CT1 | CT1 Gas flow | CT2 Gas flow |  | Pamb | Freq. Hz | LBTU Gas Specific gravity | CT-1 compressor efficiency(%) | CT-2 compressor efficiency(%) |  | CT-1 Heat Rate (Btu/Kwh) | CT-2 Heat Rate (Btu/Kwh) |  | DB(1+2) | DB-1 Ops Hours | DB-2 Ops Hours | CT-1 Wetcomprssion Ops Hours | RO Operation Hours | CT1 T/G Brg |  | CT2 T/G Brg
[7 empty] | CT1 |  | CT2 |  | CT1 |  | CT2 | [43 empty] | mmscf/d | mmscf/d | WetC flow | HBTU KPPH | HBTU KPPH | LBTU KPPH | mbar | Hz | [7 empty] | mmscf/d |  |  |  |  | Supply air pressure | Seal air pressure | Supply air pressure | Seal air pressure
[5 empty] | Max | Min | hrs | min | hrs | min | hrs | min | hrs | min | hrs | min | [42 empty] | gpm | [17 empty] | Psi | "WC | Psi | "WC
Week 1 | 2019-01-01 | 56 | 72.4% | 49.5 | 67 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 0 | 0 | 0 | 0 | 44 | 1440 | 48 | 0 | 30 | 0 | 11 | 0 | 0 | no data | 155 | no data | 63.93% | no data | 0 | 0 | 0 | 0.31 | 1010 | 313.1 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | #REF! | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1008 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-01-02 | 55.6 | 77.3% | 50.8 | 67 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 0 | 0 | 0 | 0 | 44 | 1440 | 48 | 0 | 30 | 0 | 13 | 0 | 0 | no data | 155 | no data | 63.93% | no data | 0 | 0 | 0 | 0.19 | 1010 | 191.9 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1008 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-01-03 | 55.6 | 74% | 49 | 72 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 11 | 0 | 0 | no data | 155 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | #REF! | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1007 | 49.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-01-04 | 58 | 73.5% | 51.5 | 68.5 | 51.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 10 | 0 | 0 | no data | 155 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | #REF! | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1003.2 | 49.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-01-05 | 58.4 | 70.8% | 51.6 | 65 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 7 | 0 | 0 | no data | 155 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1002.3 | 49.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-01-06 | 54.8 | 70.2% | 47.8 | 75 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 6 | 0 | 0 | no data | 155 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1004.04 | 49.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-01-07 | 55.5 | 69.04% | 47.9 | 67 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 8 | 0 | 0 | no data | 155 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1005.21 | 49.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Week 2 | 2019-01-08 | 57.2 | 66.8% | 49 | 67 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 6 | 0 | 0 | no data | 155 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | #REF! | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1003 | 50.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-01-09 | 57.8 | 69% | 50.1 | 70 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 7 | 0 | 0 | no data | 155 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | #REF! | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1001.88 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-01-10 | 58.5 | 69.8% | 50.8 | 72 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3719 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 9 | 0 | 0 | no data | 154.9583 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | #REF! | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999.8 | 50.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-01-11 | 60.72 | 67.2% | 52.47 | 70.7 | 55.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 10 | 0 | 0 | no data | 155 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | #REF! | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1002 | 50.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-01-12 | 56.1 | 73.7% | 50.6 | 66.8 | 51.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 8 | 0 | 0 | no data | 155 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | #REF! | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1002 | 50.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-01-13 | 56.2 | 69% | 48.8 | 67 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 10 | 0 | 0 | no data | 155 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1003 | 50.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-01-14 | 54.4 | 62.8% | 44.9 | 66 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 11 | 0 | 0 | no data | 155 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | #REF! | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1005 | 50.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Week 3 | 2019-01-15 | 55.2 | 69.6% | 48.1 | 66 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 11 | 0 | 0 | no data | 155 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1002 | 50.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-01-16 | 56.3 | 69% | 48.9 | 69.4 | 47.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3719 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 9 | 0 | 0 | no data | 154.9583 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | #REF! | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1001 | 50.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-01-17 | 55.6 | 70.5% | 48.3 | 73.8 | 45.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 8 | 0 | 0 | no data | 155 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | #REF! | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1002 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-01-18 | 57.6 | 68.61% | 49.88 | 68 | 48.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 8 | 0 | 0 | no data | 155 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | #REF! | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1002 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-01-19 | 58 | 67% | 52 | 69 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 7 | 0 | 0 | no data | 155 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | #REF! | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1001 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-01-20 | 58 | 71% | 52 | 67 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 7 | 0 | 0 | no data | 155 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1000.1 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-01-21 | 54.8 | 81% | 51.6 | 60 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 9 | 0 | 0 | no data | 155 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | #REF! | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 997.3 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Week 4 | 2019-01-22 | 51.13 | 84.17% | 48.46 | 64 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 8 | 0 | 0 | no data | 155 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1003 | 50.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-01-23 | 50.1 | 87.3% | 48.08 | 56 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 9 | 0 | 0 | no data | 155 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | #REF! | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1004 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-01-24 | 52.6 | 79.9% | 47.9 | 67 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 7 | 0 | 0 | no data | 155 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1004 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
| 2019-01-25 | 52.7 | 79.3% | 48.3 | 65 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 6 | 0 | 0 | no data | 155 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1004.4 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1
| 2019-01-26 | 49.5 | 78.5% | 48 | 63 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 5 | 0 | 0 | no data | 155 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1007 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
| 2019-01-27 | 55 | 69% | 47 | 69 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 6 | 0 | 0 | no data | 155 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1008 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 | 0 | 3.9
| 2019-01-28 | 55.2 | 66.4% | 46.7 | 74 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 7 | 0 | 0 | no data | 155 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1007.1 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1
Week 5 | 2019-01-29 | 56.3 | 65.8% | 47.7 | 71 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 6 | 0 | 0 | 0% | 155 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1004.54 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-01-30 | 55.3 | 69.2% | 48.1 | 59 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 5 | 0 | 0 | 0% | 155 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1003.5 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-01-31 | 51.8 | 83% | 49.7 | 54.7 | 50.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 6 | 0 | 0 | 0% | 155 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1004 | 50.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-02-01 | 54.3 | 76.6% | 49.7 | 67 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 6 | 0 | 0 | 0% | 155 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1003 | 50.08 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-02-02 | 56.2 | 70.9% | 49.5 | 72 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 5 | 0 | 0 | 0% | 155 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1003 | 50.1 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-02-03 | 58.4 | 65.9% | 49.9 | 76 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3715 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 5 | 0 | 0 | 0% | 154.7917 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1004 | 50 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-02-04 | 60.1 | 66.7% | 51 | 73.9 | 48.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3714 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 6 | 0 | 0 | 0% | 154.75 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1003.7 | 50 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Week 6 | 2019-02-05 | 62.87 | 64.6% | 53.27 | 75 | 53.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3712 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 5 | 0 | 0 | 0% | 154.6667 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1000.8 | 50 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-02-06 | 58.1 | 66.6% | 50.1 | 67 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 6 | 0 | 0 | 0% | 155 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 996.1 | 50 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-02-07 | 54.1 | 75.5% | 48.8 | 65 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 5 | 0 | 0 | 0% | 155 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 993.8 | 50 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-02-08 | 52.8 | 67.8% | 45.7 | 63 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 5 | 0 | 0 | 0% | 155 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1001.3 | 50 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-02-09 | 55.8 | 65.4% | 47.2 | 74 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3719 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 4 | 0 | 0 | 0% | 154.9583 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1003.9 | 50 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-02-10 | 57.8 | 64.8% | 48.8 | 72 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 4 | 0 | 0 | 0% | 155 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1004.3 | 50 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-02-11 | 59.9 | 64.9% | 51.1 | 69.9 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3716 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 6 | 0 | 0 | 0% | 154.8333 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1004.9 | 50 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Week 7 | 2019-02-12 | 61.3 | 66.9% | 52.9 | 70 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3717 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 5 | 0 | 0 | 0% | 154.875 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1004 | 50 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-02-13 | 61.2 | 66.6% | 52.5 | 70 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3717 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 4 | 0 | 0 | 0% | 154.875 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1003 | 50 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-02-14 | 61 | 69.5% | 53.6 | 74 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3719 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 5 | 0 | 0 | 0% | 154.9583 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1003 | 50 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-02-15 | 58.44 | 69.79% | 50.53 | 73.5 | 49.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3716 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 5 | 0 | 0 | 0% | 154.8333 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1001 | 50 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-02-16 | 60.36 | 57.65% | 48.65 | 72.85 | 48.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3712 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 5 | 0 | 0 | 0% | 154.6667 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1002 | 50 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-02-17 | 61.52 | 59.92% | 50.87 | 72 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3710 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 5 | 0 | 0 | 0% | 154.5833 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 998 | 50 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-02-18 | 58.17 | 74.33% | 53.12 | 62 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 5 | 0 | 0 | 0% | 155 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 998 | 50 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Week 8 | 2019-02-19 | 57 | 76% | 52 | 66 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 5 | 0 | 0 | 0% | 155 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 998 | 50 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-02-20 | 56 | 82% | 53 | 58 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 5 | 0 | 0 | 0% | 155 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1001 | 50 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-02-21 | 58.5 | 78.8% | 54.2 | 68.5 | 53.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 5 | 0 | 0 | 0% | 155 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1001.3 | 50.05 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
| 2019-02-22 | 59.9 | 70.6% | 52 | 74 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3716 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 4 | 0 | 0 | 0% | 154.8333 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1003.1 | 50.05 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1
| 2019-02-23 | 60.9 | 60.9% | 50.2 | 75 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3709 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 4 | 0 | 0 | 0% | 154.5417 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 50.05 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
| 2019-02-24 | 61.5 | 67.7% | 50.05 | 76 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3709 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 4 | 0 | 0 | 0% | 154.5417 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 995 | 50.05 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9
| 2019-02-25 | 60.7 | 65.5% | 50.08 | 73 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3710 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 5 | 0 | 0 | 0% | 154.5833 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 995 | 50.05 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1
Week 9 | 2019-02-26 | 56.6 | 71% | 50 | 66 | 46 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 6 | 0 | 0 | 0% | 155 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 995.5 | 50.04 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-02-27 | 57.96 | 66.2% | 49.72 | 69 | 49.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 6 | 0 | 0 | 0% | 155 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 995 | 50.05 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-02-28 | 60 | 65.1% | 51 | 70 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3716 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 6 | 0 | 0 | 0% | 154.8333 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999.2 | 50 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-03-01 | 60.9 | 67.04% | 52 | 65 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 5 | 0 | 0 | no data | 155 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-03-02 | 56.3 | 82.1% | 53.8 | 57 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 5 | 0 | 0 | no data | 155 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 50.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-03-03 | 58.5 | 80.1% | 55.2 | 64 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 6 | 0 | 0 | no data | 155 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 998.4 | 50.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-03-04 | 61.5 | 69.8% | 53.4 | 72 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3713 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 5 | 0 | 0 | no data | 154.7083 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 995 | 50.03 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Week 10 | 2019-03-05 | 64 | 62.6% | 53.3 | 84 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3702 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 5 | 0 | 0 | no data | 154.25 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 995.3 | 50.06 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-03-06 | 65.5 | 59.9% | 54 | 84 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3693 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 5 | 0 | 0 | no data | 153.875 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 995.8 | 50.05 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-03-07 | 67.3 | 58.9% | 54.5 | 81 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3687 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 4 | 0 | 0 | no data | 153.625 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 995.5 | 50.1 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-03-08 | 62.5 | 68.7% | 55.5 | 73 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3715 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 4 | 0 | 0 | no data | 154.7917 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 50.1 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-03-09 | 65.4 | 60.5% | 53.8 | 84 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3689 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 4 | 0 | 0 | no data | 153.7083 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 50.08 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-03-10 | 67.1 | 57.8% | 54.7 | 83 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3682 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 4 | 0 | 0 | no data | 153.4167 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 997 | 50.06 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-03-11 | 62.42 | 71.98% | 55.77 | 75 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3714 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 4 | 0 | 0 | no data | 154.75 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 998 | 50.06 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Week 11 | 2019-03-12 | 63.79 | 66.81% | 54.99 | 79 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3706 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 4 | 0 | 0 | no data | 154.4167 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 50.07 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-03-13 | 65.43 | 64.33% | 55.53 | 84 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3694 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 4 | 0 | 0 | no data | 153.9167 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 998 | 50.12 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-03-14 | 65.4 | 64.6% | 55.8 | 79 | 57 | 0 | 0 | 0 | 0 | 4 | 45 | 4 | 45 | 0 | 0 | 3697 | 766 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 6 | 0 | 0 | no data | 154.0417 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 31.9167 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 50.09 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-03-15 | 67 | 59.6% | 55.2 | 81 | 56 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3688 | 3676 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 10 | 0 | 0 | no data | 153.6667 | no data | 100% | no data | 0 | 0 | 0 | 0.283 | 1000 | 283 | no data | 153.1667 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0.6 | 0 | 1003.6 | 50.08 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0
| 2019-03-16 | 68 | 59% | 56 | 80 | 58 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3685 | 3676 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 6 | 0 | 0 | no data | 153.5417 | no data | 100% | no data | 0 | 0 | 0 | 0.25 | 990 | 247.5 | no data | 153.1667 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0.5 | 0 | 0 | 1001 | 50.09 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-03-17 | 71.1 | 57.1% | 57.3 | 83 | 59 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3667 | 3658 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 6 | 0 | 0 | no data | 152.7917 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 152.4167 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 998.5 | 50.1 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-03-18 | 69.6 | 64.2% | 59 | 83 | 60 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3680 | 3658 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 6 | 0 | 0 | no data | 153.3333 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 152.4167 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 997.7 | 50.02 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Week 12 | 2019-03-19 | 71.3 | 62.2% | 59.8 | 88 | 61 | 0 | 0 | 0 | 0 | 8 | 0 | 8 | 0 | 0 | 0 | 3666 | 1240 | 0 | 0 | 0 | 44 | 960 | 48 | 960 | 60 | 960 | 5 | 0 | 0 | no data | 152.75 | no data | 33.33% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 51.6667 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 993 | 50.05 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-03-20 | 68.2 | 67.5% | 59.1 | 82 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3692 | 0 | 0 | 0 | 0 | 44 | 1440 | 48 | 1440 | 60 | 1440 | 3 | 0 | 0 | no data | 153.8333 | no data | 0% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 995 | 50.04 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-03-21 | 71.4 | 58.3% | 58.3 | 91 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3666 | 0 | 0 | 0 | 0 | 44 | 1440 | 48 | 1440 | 60 | 1440 | 3 | 0 | 0 | no data | 152.75 | no data | 0% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 998 | 50 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-03-22 | 74 | 55.9% | 59.4 | 88 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3649 | 0 | 0 | 0 | 0 | 44 | 1440 | 48 | 1440 | 60 | 1440 | 4 | 0 | 0 | no data | 152.0417 | no data | 0% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 50.09 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-03-23 | 72.3 | 63.2% | 61.3 | 87 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3673 | 0 | 0 | 0 | 0 | 44 | 1440 | 48 | 1440 | 60 | 1440 | 4 | 0 | 0 | no data | 153.0417 | no data | 0% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 50.04 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-03-24 | 68.75 | 70.74% | 61.41 | 85.77 | 62.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3695 | 0 | 0 | 0 | 0 | 44 | 1440 | 48 | 1440 | 60 | 1440 | 4 | 0 | 0 | no data | 153.9583 | no data | 0% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 998.24 | 50.05 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-03-25 | 74.6 | 57.9% | 60.8 | 93 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3642 | 0 | 0 | 0 | 0 | 44 | 1440 | 48 | 1440 | 60 | 1440 | 4 | 0 | 0 | no data | 151.75 | no data | 0% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 997.1 | 50.04 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Week 13 | 2019-03-26 | 76.4 | 57.7% | 62 | 90 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3627 | 0 | 0 | 0 | 0 | 43 | 1440 | 47 | 1440 | 60 | 1440 | 5 | 0 | 0 | 0% | 151.125 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 997 | 49.98 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-03-27 | 79.5 | 52.8% | 62.3 | 93 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3600 | 0 | 0 | 0 | 0 | 43 | 1440 | 47 | 1440 | 60 | 1440 | 5 | 0 | 0 | 0% | 150 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 997 | 50.02 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-03-28 | 79.7 | 57.2% | 64 | 91 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3601 | 3638 | 3638 | 0 | 0 | 43 | 0 | 47 | 0 | 60 | 0 | 6 | -3638 | 0 | 0% | 150.0417 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | no data | 151.5833 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 995 | 50.07 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-03-29 | 81.6 | 60.7% | 67.7 | 98 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3581 | 3620 | 3620 | 0 | 0 | 43 | 0 | 47 | 0 | 60 | 0 | 6 | -3620 | 0 | no data | 149.2083 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 150.8333 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 992.7 | 50.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 | 0
| 2019-03-30 | 81.6 | 51.5% | 63.8 | 100 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3582 | 3579 | 3579 | 0 | 0 | 43 | 0 | 47 | 0 | 60 | 0 | 4 | -3579 | 0 | no data | 149.25 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 149.125 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 993.3 | 50.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-03-31 | 77.5 | 44.3% | 57.4 | 93 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3619 | 3567 | 3567 | 0 | 0 | 43 | 0 | 47 | 0 | 60 | 0 | 4 | -3567 | 0 | no data | 150.7917 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 148.625 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 994.8 | 50.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-04-01 | 79 | 47.1% | 59.4 | 93 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3605 | 3550 | 3550 | 0 | 0 | 43 | 0 | 47 | 0 | 60 | 0 | 6 | -3550 | 0 | no data | 150.2083 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 147.9167 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 994 | 50.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Week 14 | 2019-04-02 | 80.9 | 45.4% | 60.4 | 96 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3581 | 2736 | 3526 | 83 | 92 | 43 | 239 | 47 | 337 | 60 | 420 | 9 | -3443 | 29 | 13.22% | 149.2083 | 2.318% | 76.24% | 72.92% | 0.104 | 171.84 | 17.8714 | 1.408 | 1005 | 1415.04 | 17263.9923 | 114 | 25 | 181 | 32 | 83 | 0 | 0 | 9 | 68 | 24 | 0 | 44 | 17263.9923 | 0 | 0 | 0 | 0 | 15.29 | 11.52 | 0 | 993 | 50.02 | 0.9229 | 87.86 | 85.5 | 2.36 | 14848 | 10864 | -3984 | 0 | 0 | 0 | 0 | 1.8 | 2 | 4.5 | 0 | 0
| 2019-04-03 | 82.5 | 62.6% | 48.9 | 98 | 71 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3567 | 1680 | 3514 | 1646 | 1716 | 43 | 0 | 47 | 1440 | 60 | 42 | 70 | -1868 | 76 | 94.08% | 148.625 | 46.15% | 67.5% | 46.92% | 0 | 0 | 0 | 14.747 | 995.9992 | 14688 | 8923.4508 | 70 | 0 | 0 | 0 | 0 | 31.8 | 1398 | 0 | 1040 | 0 | 676 | 0 | 8923.4508 | 28.1667 | 2.432 | 0 | 0 | 24.2 | 0 | 0 | 992 | 50.06 | 0 | 87.35 | 0 | 87.35 | 10946 | 0 | -10946 | 2.432 | 22.1 | 0 | 0 | 3.9 | 2 | 4.5 | 0 | 0
| 2019-04-04 | 83.95 | 50.33% | 64.76 | 96 | 71 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3551 | 1656 | 3519 | 1637 | 1708 | 43 | 0 | 47 | 1440 | 60 | 0 | 71 | -1882 | 75 | 94.89% | 147.9583 | 46.1% | 68.67% | 47.33% | 0 | 0 | 0 | 14.529 | 1008.1905 | 14648 | 8948.0757 | 69 | 0 | 0 | 0 | 0 | 32 | 1440 | 0 | 1031 | 0 | 677 | 0 | 8948.0757 | 28.2083 | 2.147 | 0 | 0 | 24.26 | 0 | 0 | 992.38 | 50.04 | 0 | 87.15 | 0 | 87.15 | 11057 | 0 | -11057 | 2.147 | 24 | 0 | 0 | 0 | 2.1 | 4.5 | 0 | 0
| 2019-04-05 | 85.9 | 51.9% | 66.6 | 99 | 72 | 24 | 0 | 14 | 8 | 0 | 0 | 0 | 0 | 13 | 45 | 3537 | 2707 | 2707 | 2663 | 2758 | 42 | 0 | 42 | 508 | 61 | 0 | 95 | -44 | 149 | 77.13% | 147.375 | 75.29% | 89.78% | 78.47% | 2.42 | 133.02 | 321.9084 | 23.348 | 1006.1247 | 23491 | 8942.1361 | 112.7917 | 0 | 0 | 25 | 84 | 35 | 615 | 0 | 1015 | 615 | 1128 | -400 | 8942.1361 | 47 | 2.179 | 1.44 | 0 | 24.12 | 13.03 | 9.75 | 991.8 | 50.05 | 0.9351 | 87.09 | 86.73 | 0.36 | 11155 | 11160 | 5 | 3.619 | 24 | 14.08 | 0 | 5.62 | 2.2 | 4.5 | 2.1 | 0
| 2019-04-06 | 87.2 | 51.5% | 67.6 | 100 | 75 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3520 | 3467 | 3467 | 3397 | 3506 | 42 | 0 | 42 | 0 | 62 | 0 | 109 | -70 | 148 | 98.7% | 146.6667 | 96.51% | 100% | 100% | 5.1 | 129.38 | 659.838 | 28.935 | 1006.048 | 29110 | 8763.5673 | 144.4583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1005 | 1009 | 1492 | 4 | 8763.5673 | 62.1667 | 2.44 | 2.467 | 0 | 23.93 | 19.96 | 19.77 | 990.67 | 49.99 | 0.9365 | 87.05 | 86.75 | 0.3 | 11172 | 11018 | -154 | 0 | 24 | 24 | 0 | 0 | 2.1 | 4.5 | 2.1 | 0
| 2019-04-07 | 86 | 53% | 67 | 99 | 76 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3542 | 3477 | 3477 | 3409 | 3516 | 42 | 0 | 42 | 0 | 62 | 0 | 107 | -68 | 150 | 97.67% | 147.5833 | 96.25% | 100% | 100% | 5.987 | 135.63 | 812.0168 | 28.818 | 1010.4102 | 29118 | 8779.7057 | 144.875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1008 | 1014 | 1494 | 6 | 8779.7057 | 62.25 | 2.526 | 2.425 | 0 | 23.97 | 19.92 | 20.35 | 989 | 50.07 | 0.9355 | 86.95 | 86.77 | 0.18 | 11174 | 11002 | -172 | 0 | 24 | 24 | 0 | 0 | 2.1 | 4.5 | 2.1 | -0.4
| 2019-04-08 | 83.2 | 52% | 65 | 95 | 70 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3562 | 3518 | 3518 | 3448 | 3557 | 42 | 0 | 43 | 0 | 63 | 0 | 109 | -70 | 151 | 98.15% | 148.4167 | 96.8% | 100% | 100% | 6.92 | 138.81 | 960.5652 | 28.987 | 1007.91 | 29216.2872 | 8751.9873 | 146.5833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1023 | 1027 | 1507 | 4 | 8751.9873 | 62.7917 | 2.507 | 2.4111 | 0 | 24.24 | 20.06 | 20.98 | 990.9 | 50.06 | 0.9342 | 86.86 | 86.61 | 0.25 | 11128 | 10961 | -167 | 0 | 24 | 24 | 0 | 6.4 | 2.1 | 4.5 | 2.1 | -0.6
Week 15 | 2019-04-09 | 85 | 53% | 67 | 98 | 73 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 22 | 42 | 3549 | 3494 | 3464 | 3394 | 3499 | 42 | 0 | 42 | 0 | 62 | 0 | 105 | -70 | 150 | 97.19% | 147.875 | 95.63% | 100% | 99.41% | 7.8 | 139.61 | 1088.958 | 28.5312 | 1007.8675 | 28755.65 | 8793.3435 | 145.5833 | 0 | 0 | 0 | 0 | 16 | 78 | 0 | 1009 | 1016 | 1474 | 7 | 8793.3435 | 61.4167 | 2.297 | 2.219 | 0 | 24.07 | 19.9 | 21.01 | 990.4 | 50.07 | 0.9341 | 86.85 | 86.71 | 0.14 | 11188 | 11013 | -175 | 0 | 24 | 24 | 0 | 0 | 2.2 | 4.7 | 2.1 | -0.5
| 2019-04-10 | 83.3 | 53.8% | 66.6 | 94 | 72 | 18 | 32 | 24 | 0 | 4 | 45 | 0 | 0 | 18 | 25 | 3563 | 3503 | 3088 | 3047 | 3140 | 43 | 0 | 43 | 0 | 63 | 0 | 93 | -41 | 150 | 87.22% | 148.4583 | 85.52% | 100% | 94.35% | 7.79 | 137.11 | 1068.0869 | 25.7489 | 1006.4608 | 25915.3 | 8855.7226 | 145.9583 | 17 | 43 | 0 | 0 | 34 | 335 | 0 | 793 | 1023 | 1324 | 230 | 8855.7226 | 55.1667 | 2 | 2.371 | 0 | 19.28 | 20.06 | 20.9 | 993.54 | 50.06 | 0.9354 | 87.22 | 86.71 | 0.51 | 11351 | 11027 | -324 | 0 | 18.6 | 24 | 0 | 4.3 | 2.1 | 4 | 2.1 | -0.8
| 2019-04-11 | 84.2 | 51.5% | 65.5 | 97 | 73 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3556 | 3479 | 3479 | 3423 | 3524 | 42 | 0 | 43 | 0 | 62 | 0 | 101 | -56 | 150 | 97.89% | 148.1667 | 96.26% | 100% | 100% | 7.795 | 136.14 | 1061.2113 | 28.7611 | 1006.6986 | 28953.78 | 8768.6215 | 144.9583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1004 | 1027 | 1493 | 23 | 8768.6215 | 62.2083 | 2.442 | 2.328 | 0 | 24.21 | 20.1 | 20.67 | 993.33 | 50.11 | 0.9356 | 87.13 | 86.66 | 0.47 | 11344 | 10985 | -359 | 0 | 24 | 24 | 0 | 0 | 2.1 | 3.8 | 2.1 | -0.8
| 2019-04-12 | 81.3 | 58.7% | 67.2 | 92 | 70 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3582 | 3478 | 3478 | 3414 | 3506 | 42 | 0 | 43 | 0 | 62 | 0 | 92 | -64 | 149 | 98.04% | 149.25 | 95.31% | 100% | 100% | 7.84 | 137.29 | 1076.3536 | 29.0033 | 997.0824 | 28918.68 | 8785.8915 | 144.9167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1005 | 1025 | 1476 | 20 | 8785.8915 | 61.5 | 2.358 | 2.318 | 0 | 24.44 | 19.97 | 21.47 | 994.04 | 50.08 | 0.9351 | 87.16 | 86.76 | 0.4 | 11418 | 10978 | -440 | 0 | 24 | 24 | 0 | 6.1 | 2.1 | 3.9 | 2.1 | -0.8
| 2019-04-13 | 80.3 | 61.3% | 67.7 | 91 | 70 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3595 | 3472 | 3472 | 3401 | 3499 | 42 | 0 | 43 | 0 | 61 | 0 | 98 | -71 | 149 | 97.85% | 149.7917 | 94.6% | 100% | 100% | 7.774 | 135.66 | 1054.6208 | 29.0363 | 989.5352 | 28732.48 | 8758.336 | 144.6667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1008 | 1027 | 1464 | 19 | 8758.336 | 61 | 2.293 | 2.234 | 0 | 24.5 | 20.12 | 21.43 | 995 | 50.1 | 0.935 | 87.13 | 86.79 |  | 11420 | 11017 | -403 | 0 | 24 | 24 | 0 | 2.9 | 2.1 | 4 | 2.1 | -0.8
| 2019-04-14 | 82.8 | 58.7% | 69 | 94 | 72 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3570 | 3038 | 3038 | 2973 | 3058 | 42 | 0 | 43 | 0 | 61 | 0 | 85 | -65 | 130 | 98.01% | 148.75 | 83.28% | 100% | 87.67% | 7.856 | 142.43 | 1118.9301 | 24.2906 | 989.4412 | 24034.14 | 8460.5012 | 126.5833 | 0 | 0 | 0 | 0 | 18 | 1440 | 0 | 1000 | 1020 | 1038 | 20 | 8460.5012 | 43.25 | 0 | 0 | 0 | 24.35 | 20.21 | 21.01 | 995 | 50.04 | 0.9334 | 87.14 | 86.76 |  | 11436 | 11109 | -327 | 0 | 0 | 0 | 0 | 0 | 2.1 | 4.5 | 2.1 | -0.8
| 2019-04-15 | 77.22 | 62.42% | 65.27 | 93.3 | 67.9 | 20 | 20 | 24 | 0 | 3 | 19 | 0 | 0 | 9 | 7 | 3622 | 3294 | 3006 | 2956 | 3039 | 42 | 0 | 43 | 0 | 61 | 0 | 83 | -50 | 146 | 86.73% | 150.9167 | 81.61% | 100% | 83.34% | 7.981 | 135.69 | 1082.9419 | 24.5501 | 990.3104 | 24312.19 | 8591.046 | 137.25 | 9 | 21 | 0 | 0 | 39 | 893 | 0 | 872 | 1039 | 1128 | 167 | 8591.046 | 47 | 0.846 | 0.804 | 0 | 24.65 | 20.59 | 21.09 | 993.3 | 50.15 | 0.936 | 87.04 | 86.77 |  | 11375 | 11073 | -302 | 0 | 9.2 | 13 | 0 | 4.1 | 2.1 | 4.9 | 2.1 | 0.9
Week 16 | 2019-04-16 | 71.87 | 74.73% | 65.58 | 85.81 | 65.15 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 3671 | 3506 | 1504 | 1504 | 1565 | 43 | 0 | 44 | 0 | 61 | 0 | 61 | 0 | 66 | 98.8% | 152.9583 | 40.97% | 100% | 73.65% | 7.792 | 138.89 | 1082.2309 | 12.2376 | 990.7614 | 12124.5683 | 8781.1165 | 146.0833 | 0 | 0 | 0 | 0 | 39 | 1440 | 0 | 0 | 1047 | 518 | 1047 | 8781.1165 | 21.5833 | 0 | 0.223 | 0 | 0 | 20.56 | 21.01 | 991.04 | 50.15 | 0.9349 | 0 | 86.89 |  | 0 | 10960 | 10960 | 0.223 | 0 | 24 | 0 | 0.6 | 0 | 0 | 2.1 | -0.9
| 2019-04-17 | 69.06 | 75.5% | 64.11 | 74.4 | 64.2 | 10 | 48 | 24 | 0 | 12 | 20 | 0 | 0 | 10 | 40 | 3693 | 3554 | 2433 | 2403 | 2484 | 44 | 0 | 44 | 0 | 61 | 0 | 81 | -30 | 149 | 69.46% | 153.875 | 65.07% | 100% | 85.27% | 7.726 | 136.47 | 1054.3672 | 20.1664 | 989.2937 | 19950.4849 | 8741.0953 | 148.0833 | 23 | 52 | 0 | 0 | 38 | 800 | 0 | 494 | 1055 | 935 | 561 | 8741.0953 | 38.9583 | 0.869 | 1.044 | 0 | 25.15 | 20.94 | 21.21 | 995.42 | 50.07 | 0.9352 | 87.66 | 86.86 |  | 11229 | 11055 | -174 | 1.913 | 11.0833 | 24 | 0 | 0 | 2.1 | 4.7 | 2.1 | -1
| 2019-04-18 | 73.9 | 65.1% | 63.3 | 84 | 63 | 19 | 6 | 24 | 0 | 3 | 58 | 0 | 0 | 0 | 0 | 3649 | 3226 | 2825 | 2782 | 2861 | 44 | 0 | 44 | 0 | 61 | 0 | 79 | -43 | 134 | 88.96% | 152.0417 | 76.24% | 100% | 85.38% | 7.848 | 133.85 | 1050.4548 | 23.1884 | 984.3747 | 22826.0881 | 8582.51 | 134.4167 | 20 | 56 | 0 | 0 | 21 | 1440 | 0 | 854 | 1055 | 952 | 201 | 8582.51 | 39.6667 | 0 | 0.067 | 0 | 25.5 | 21.35 | 21.1 | 997.7 | 50.1 | 0.936 | 87.64 | 86.8 |  | 11843 | 11494 | -349 | 0.067 | 0 | 8.45 | 0 | 5.97 | 2.1 | 4.8 | 2.1 | -1
| 2019-04-19 | 80 | 54% | 64 | 92 | 66 | 8 | 9 | 13 | 15 | 15 | 13 | 10 | 28 | 0 | 0 | 3597 | 3151 | 1402 | 1377 | 1418 | 43 | 0 | 44 | 0 | 61 | 0 | 50 | -25 | 132 | 44.76% | 149.875 | 38.28% | 100% | 92.15% | 4.321 | 131.09 | 566.4399 | 11.3733 | 982.9985 | 11179.9095 | 8530.3917 | 131.2917 | 19 | 38 | 18 | 17 | 25 | 628 | 9 | 368 | 586 | 464 | 218 | 8530.3917 | 19.3333 | 0 | 0 | 0 | 9 | 11.76 | 11.8 | 993.9 | 50.04 | 0.9369 | 87.37 | 86.78 |  | 11303 | 11134 |  | 0 | 0 | 0 | 0 | 0 | 2.1 | 4.8 | 2.2 | -0.9
| 2019-04-20 | 84 | 49% | 64 | 97 | 72 | 4 | 12 | 4 | 44 | 19 | 2 | 15 | 46 | 0 | 0 | 3553 | 3271 | 674 | 661 | 686 | 42 | 0 | 43 | 0 | 61 | 0 | 35 | -13 | 127 | 22.51% | 148.0417 | 18.6% | 100% | 94.78% | 2.682 | 152.45 | 408.8709 | 5.9445 | 996.6952 | 5924.8224 | 9581.9868 | 136.2917 | 21 | 46 | 18 | 210 | 20 | 311 | 10 | 193 | 298 | 195 | 105 | 9581.9868 | 8.125 | 0 | 0 | 0 | 4.8 | 6.2 | 6.63 | 990.3 | 50.04 | 0.9314 | 87.3 | 86.97 |  | 11194 | 10890 |  | 0 | 0 | 0 | 0 | 7.2 | 2 | 4.8 | 2.1 | -0.8
| 2019-04-21 | 87.1 | 48% | 66 | 99 | 75 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3525 | 3524 | 0 | 0 | 0 | 42 | 0 | 43 | 0 | 60 | 0 | 14 | 0 | 0 | no data | 146.875 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 146.8333 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 989.4 | 50.07 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-04-22 | 91.4 | 43.6% | 67 | 106 | 77 | 12 | 2 | 13 | 25 | 11 | 25 | 9 | 14 | 0 | 0 | 3480 | 3244 | 1615 | 1584 | 1637 | 42 | 0 | 43 | 0 | 60 | 0 | 58 | -31 | 129 | 52.87% | 145 | 45.52% | 100% | 92.27% | 4.616 | 144 | 664.704 | 13.1482 | 1006.5121 | 13233.8336 | 8774.3293 | 135.1667 | 25 | 33 | 17 | 81 | 18 | 774 | 5 | 510 | 605 | 522 | 95 | 8774.3293 | 21.75 | 0 | 0 | 0 | 12.34 | 12.03 | 12.1 | 988.96 | 50.12 | 0.9339 | 87.21 | 87.01 |  | 11187 | 10954 |  | 0 | 0 | 0 | 0 | 0 | 2.2 | 4.9 | 2.1 | -0.8
Week 17 | 2019-04-23 | 92.3 | 45% | 67.6 | 105 | 79 | 14 | 23 | 24 | 0 | 8 | 42 | 0 | 0 | 0 | 0 | 3475 | 3157 | 2393 | 2369 | 2447 | 42 | 0 | 43 | 0 | 60 | 0 | 78 | -24 | 128 | 79.65% | 144.7917 | 68.17% | 100% | 80.85% | 7.969 | 134.89 | 1074.9384 | 19.1917 | 1009.2608 | 19369.465 | 8629.9719 | 131.5417 | 20 | 55 | 0 | 0 | 27 | 1440 | 0 | 613 | 1019 | 815 | 406 | 8629.9719 | 33.9583 | 0 | 0 | 0 | 14.85 | 19.8 | 20.6 | 988.54 | 50.1 | 0.9364 | 86.86 | 86.93 |  | 11245 | 10927 |  | 0 | 0 | 0 | 0 | 4.83 | 2.1 | 4.9 | 2.1 | -0.9
| 2019-04-24 | 84.3 | 51.5% | 66 | 92 | 77 | 15 | 14 | 24 | 0 | 7 | 51 | 0 | 0 | 0 | 0 | 3559 | 3183 | 2459 | 2424 | 2502 | 42 | 0 | 43 | 0 | 60 | 0 | 78 | -35 | 129 | 80.81% | 148.2917 | 68.11% | 100% | 81.84% | 7.919 | 131.33 | 1040.0023 | 19.68 | 1000.662 | 19693.0282 | 8553.2304 | 132.625 | 18 | 26 | 0 | 0 | 26 | 1440 | 0 | 648 | 1027 | 827 | 379 | 8553.2304 | 34.4583 | 0 | 0 | 0 | 15.63 | 20.16 | 20.79 | 993 | 50.07 | 0.9371 | 87.08 | 87.04 |  | 11248 | 11012 |  | 0 | 0 | 0 | 0 | 1.15 | 2.1 | 4.9 | 2.1 | -0.9
| 2019-04-25 | 82.7 | 56% | 66.8 | 96 | 72 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3571 | 3049 | 3049 | 2985 | 3071 | 42 | 0 | 43 | 0 | 60 | 0 | 86 | -64 | 130 | 98.43% | 148.7917 | 83.59% | 100% | 88.28% | 7.904 | 136.78 | 1081.1091 | 24.109 | 1001.42 | 24143.2348 | 8450.3665 | 127.0417 | 0 | 0 | 0 | 0 | 17 | 1440 | 0 | 1011 | 1027 | 1033 | 16 | 8450.3665 | 43.0417 | 0 | 0 | 0 | 24.23 | 20.12 | 20.99 | 993 | 50.04 | 0.9352 | 87.25 | 87.05 |  | 11261 | 10993 |  | 0 | 0 | 0 | 0 | 4 | 2.2 | 4.8 | 2.1 | -0.9
| 2019-04-26 | 86.6 | 51% | 67.7 | 100 | 72 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3530 | 3035 | 3035 | 2978 | 3063 | 42 | 0 | 43 | 0 | 60 | 0 | 85 | -57 | 129 | 98.93% | 147.0833 | 84.36% | 100% | 88.28% | 7.768 | 135.28 | 1050.855 | 23.961 | 1004.8829 | 24078 | 8438.1649 | 126.4583 | 0 | 0 | 0 | 0 | 17 | 1440 | 0 | 1007 | 1025 | 1031 | 18 | 8438.1649 | 42.9583 | 0 | 0 | 0 | 24.12 | 20.07 | 20.49 | 993 | 50.09 | 0.9362 | 87.16 | 86.98 |  | 11254 | 10989 |  | 0 | 0 | 0 | 0 | 3.94 | 2.1 | 4.7 | 2.1 | -0.8
| 2019-04-27 | 90.7 | 43.1% | 66.6 | 103 | 78 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3494 | 3017 | 3017 | 2961 | 3044 | 42 | 0 | 42 | 0 | 60 | 0 | 83 | -56 | 128 | 99.09% | 145.5833 | 84.75% | 100% | 88.19% | 7.805 | 137.59 | 1073.8899 | 23.906 | 1004.392 | 24010.9952 | 8471.7613 | 125.7083 | 0 | 0 | 0 | 0 | 17 | 1440 | 0 | 999 | 1018 | 1027 | 19 | 8471.7613 | 42.7917 | 0 | 0 | 0 | 24.06 | 19.98 | 20.3 | 991.8 | 50.03 | 0.9355 | 86.94 | 86.94 |  | 11317 | 11006 |  | 0 | 0 | 0 | 0 | 0.38 | 2.2 | 4.8 | 2.1 | -0.8
| 2019-04-28 | 91.7 | 39.93% | 65.8 | 104 | 77 | 22 | 7 | 24 | 0 | 1 | 37 | 0 | 0 | 0 | 0 | 3482 | 2912 | 2912 | 2856 | 2936 | 42 | 0 | 43 | 0 | 60 | 0 | 80 | -56 | 129 | 94.83% | 145.0833 | 82.02% | 100% | 86.77% | 7.934 | 134.16 | 1064.4254 | 23.092 | 1002.252 | 23144.0032 | 8476.3406 | 121.3333 | 17 | 16 | 0 | 0 | 19 | 1440 | 0 | 926 | 1019 | 991 | 93 | 8476.3406 | 41.2917 | 0 | 0 | 0 | 22.36 | 20.05 | 20.19 | 990.17 | 50.06 | 0.9367 | 86.82 | 86.88 |  | 11318 | 10998 |  | 0 | 0 | 0 | 0 | 1.05 | 2.2 | 4.8 | 2.1 | -1
| 2019-04-29 | 91.9 | 38.9% | 65.5 | 105 | 77 | 16 | 18 | 24 | 0 | 6 | 58 | 0 | 0 | 0 | 0 | 3479 | 3210 | 2525 | 2480 | 2559 | 42 | 0 | 43 | 0 | 60 | 0 | 79 | -45 | 129 | 82.66% | 144.9583 | 71.28% | 100% | 82.3% | 7.851 | 133.61 | 1048.9721 | 20.179 | 1001.98 | 20218.9544 | 8575.7768 | 133.75 | 22 | 44 | 0 | 0 | 25 | 1440 | 0 | 689 | 1020 | 850 | 331 | 8575.7768 | 35.4167 | 0 | 0 | 0 | 16.78 | 19.971 | 20.33 | 987.5 | 50.08 | 0.9367 | 86.76 | 86.85 |  | 11324 | 10983 |  | 0 | 0 | 0 | 0 | 4.2 | 2.2 | 4.8 | 2.1 | -0.8
Week 18 | 2019-04-30 | 88.9 | 38.6% | 64.3 | 98 | 80 | 0 | 0 | 21 | 3 | 24 | 0 | 2 | 42 | 0 | 0 | 3513 | 3454 | 1284 | 1271 | 1326 | 42 | 0 | 43 | 0 | 60 | 0 | 58 | -13 | 64 | 86.33% | 146.375 | 36.18% | 100% | 75.41% | 7.07 | 137.99 | 975.5893 | 9.98 | 1000.66 | 9986.5868 | 8624.8435 | 143.9167 | 0 | 0 | 18 | 15 | 40 | 1277 | 3 | 0 | 902 | 424 | 902 | 8624.8435 | 17.6667 | 0 | 0 | 0 | 17.71 | 17.96 | 50.09 | 0.935 | 0 | 86.85 | -86.85 | 0 | 10977 | 10977 | 5.22 | 0
| 2019-05-01 | 89 | 39% | 64 | 101 | 75 | 3 | 44 | 10 | 37 | 19 | 7 | 11 | 36 | 0 | 0 | 3506 | 3471 | 968 | 957 | 995 | 42 | 0 | 43 | 0 | 60 | 0 | 47 | -11 | 128 | 32.39% | 146.0833 | 27.3% | 100% | 88.6% | 3.941 | 140.06 | 551.9765 | 8.1314 | 1002.3317 | 8150.318 | 9093.3066 | 144.625 | 22 | 69 | 16 | 107 | 32 | 643 | 9 | 181 | 507 | 307 | 326 | 9093.3066 | 12.7917 | 0 | 0 | 4.6 | 10.47 | 9.76 | 50.1 | 0.9346 | 86.94 | 86.91 | 0.03 | 11271 | 11035 | -236 | 0 | 0
| 2019-05-02 | 87.5 | 38% | 62 | 101 | 75 | 0 | 0 | 6 | 5 | 24 | 0 | 15 | 42 | 0 | 0 | 3522 | 3466 | 434 | 432 | 453 | 42 | 0 | 43 | 0 | 60 | 0 | 37 | -2 | 64 | 29.49% | 146.75 | 12.27% | 100% | 91.24% | 2.517 | 140.82 | 354.4439 | 3.8308 | 1002.227 | 3839.283 | 9707.7013 | 144.4167 | 0 | 0 | 16 | 133 | 40 | 404 | 16 | 0 | 322 | 131 | 322 | 9707.7013 | 5.4583 | 0 | 0 | 0 | 6.8 | 6 | 50.08 | 0.9346 | 0 | 86.55 | -86.55 | 0 | 11024 | 11024 | 4.2 | 0
| 2019-05-03 | 87 | 40% | 63 | 99 | 74 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3526 | 3470 | 0 | 0 | 0 | 42 | 0 | 43 | 0 | 60 | 0 | 17 | 0 | 0 | no data | 146.9167 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 144.5833 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 50.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-05-04 | 90.3 | 38.1% | 64.1 | 102 | 77 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3496 | 3466 | 0 | 0 | 0 | 42 | 0 | 43 | 0 | 60 | 0 | 14 | 0 | 0 | no data | 145.6667 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 144.4167 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 50.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-05-05 | 91.5 | 33.7% | 62.8 | 107 | 76 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3486 | 3452 | 0 | 0 | 0 | 42 | 0 | 43 | 0 | 60 | 0 | 12 | 0 | 0 | no data | 145.25 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 143.8333 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 50.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-05-06 | 93 | 32.3% | 63 | 108 | 78 | 11 | 2 | 12 | 21 | 12 | 16 | 10 | 6 | 10 | 45 | 3465 | 3463 | 1686 | 1692 | 1752 | 42 | 0 | 43 | 0 | 62 | 0 | 66 | 6 | 150 | 48.67% | 144.375 | 48.83% | 100% | 97.65% | 4.202 | 133.25 | 559.9165 | 14.8366 | 999.2303 | 14825.21 | 9092.8643 | 144.2917 | 23 | 42 | 19 | 93 | 34 | 66 | 6 | 477 | 566 | 709 | 89 | 9092.8643 | 29.5417 | 1.187 | 1.29 | 11.6 | 12.14 | 0.81 | 50.06 | 0.9376 | 87.24 | 86.62 | 0.62 | 11237 | 11487 | 250 | 8.55 | 2.477
Week 19 | 2019-05-07 | 93.4 | 32.7% | 65.6 | 109 | 77 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3464 | 3476.5 | 3476.5 | 3445 | 3545 | 43 | 0 | 43 | 0 | 62 | 0 | 9 | -31.5 | 154 | 95.91% | 144.3333 | 99.45% | 100% | 100% | 7.909 | 137.99 | 1091.3629 | 28.9683 | 998.9547 | 28938.0293 | 8716.8047 | 144.8542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1024 | 1036 | 1485 | 12 | 8716.8047 | 61.875 | 2.326 | 2.276 | 24.38 | 21.62 | 20.06 | 50.09 | 0.9355 | 87.15 | 86.65 | 0.5 | 11178 | 11436 | 258 | 0 | 4.602
| 2019-05-08 | 93.6 | 37.4% | 66.2 | 107 | 78 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 20 | 56 | 3462 | 3398 | 3360 | 3286 | 3392 | 42 | 0 | 42 | 0 | 60 | 0 | 106 | -74 | 146 | 96.8% | 144.25 | 94.92% | 100% | 98.67% | 7.835 | 136.85 | 1072.2197 | 27.6665 | 999.6241 | 27656.0801 | 8742.6354 | 141.5833 | 0 | 0 | 0 | 0 | 15 | 184 | 0 | 1000 | 1014 | 1378 | 0 | 8742.6354 | 57.4167 | 1.815 | 1.861 | 24.05 | 21.38 | 19.91 | 50.08 | 0.9359 | 87.15 | 86.85 | 0.3 | 11306 | 11546 | 240 | 4.08 | 3.676
| 2019-05-09 | 94.7 | 37.4% | 67.2 | 107 | 83 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 10 | 59 | 3450 | 3389 | 3149 | 3144 | 3237 | 42 | 0 | 42 | 0 | 60 | 0 | 93 | -5 | 143 | 94.32% | 143.75 | 91.13% | 100% | 94.35% | 7.827 | 133.62 | 1045.8437 | 26.0551 | 999.9969 | 26055.051 | 8619.8775 | 141.2083 | 0 | 0 | 0 | 0 | 15 | 781 | 0 | 999 | 1012 | 1226 | 0 | 8619.8775 | 51.0833 | 1.025 | 0.971 | 23.94 | 21.23 | 19.83 | 50.09 | 0.937 | 87.32 | 86.95 | 0.37 | 11259 | 11518 | 259 | 1.05 | 1.996
| 2019-05-10 | 93.78 | 37.39% | 66.06 | 106.26 | 79.44 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 20 | 54 | 3456 | 3393 | 3335 | 3289 | 3390 | 42 | 0 | 42 | 0 | 60 | 0 | 95 | -46 | 147 | 96.09% | 144 | 95.17% | 100% | 98.74% | 7.853 | 137.35 | 1078.6095 | 27.7765 | 1002.8038 | 27854.42 | 8796.9077 | 141.375 | 0 | 0 | 0 | 0 | 14 | 186 | 0 | 1005 | 1013 | 1372 | 8 | 8796.9077 | 57.1667 | 1.802 | 1.792 | 24 | 21.23 | 19.83 | 50.1 | 0.9356 | 87.26 | 86.78 | 0.48 | 11225 | 11493 | 268 | 5 | 3.594
| 2019-05-11 | 90.55 | 41.69% | 66.33 | 100.24 | 82.54 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 2 | 40 | 3493 | 3425 | 3056 | 3064 | 3153 | 42 | 0 | 42 | 0 | 60 | 0 | 89 | 8 | 147 | 89.37% | 145.5417 | 87.72% | 100% | 90.74% | 7.808 | 135.06 | 1054.5485 | 25.0698 | 1008.4285 | 25281.09 | 8595.1823 | 142.7083 | 0 | 0 | 0 | 0 | 15 | 1280 | 0 | 1009 | 1016 | 1128 | 7 | 8595.1823 | 47 | 0.533 | 0.438 | 24.06 | 21.27 | 19.72 | 50.09 | 0.9361 | 87.33 | 86.8 | 0.53 | 11207 | 11461 | 254 | 0 | 0.971
| 2019-05-12 | 92.08 | 45.18% | 67.7 | 103.12 | 78.51 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 9 | 44 | 3474 | 3415 | 3161 | 3144 | 3235 | 42 | 0 | 42 | 0 | 60 | 0 | 91 | -17 | 144 | 93.61% | 144.75 | 90.5% | 100% | 93.81% | 7.931 | 136.3 | 1080.9953 | 25.9365 | 1012.3848 | 26257.689 | 8695.5103 | 142.2917 | 0 | 0 | 0 | 0 | 15 | 856 | 0 | 1000 | 1011 | 1224 | 11 | 8695.5103 | 51 | 1.061 | 0.985 | 23.88 | 21.18 | 19.51 | 50.07 | 0.9358 | 87.41 | 86.79 | 0.62 | 11220 | 11457 | 237 | 5.25 | 2.046
| 2019-05-13 | 93.1 | 43% | 68 | 105 | 81 | 17 | 9 | 24 | 0 | 6 | 35 | 0 | 0 | 0 | 0 | 3464 | 3411 | 2590 | 2572 | 2654 | 41 | 0 | 42 | 0 | 59 | 0 | 82 | -18 | 130 | 85.06% | 144.3333 | 74.25% | 100% | 85.08% | 7.925 | 137.26 | 1087.7855 | 21.0128 | 1013.3481 | 21293.23 | 8701.7945 | 142.125 | 17 | 16 | 0 | 0 | 21 | 1440 | 0 | 713 | 1009 | 932 | 296 | 8701.7945 | 38.8333 | 0.276 | 0.305 | 17.2 | 21.15 | 19.9 | 50.11 | 0.9356 | 87.4 | 86.96 | 0.44 | 11273 | 11492 | 219 | 0 | 0.581
Week 20 | 2019-05-14 | 87.6 | 48% | 67 | 98 | 76 | 14 | 22 | 24 | 0 | 8 | 59 | 0 | 0 | 14 | 9 | 3522 | 3429 | 2631 | 2593 | 2685 | 42 | 0 | 43 | 0 | 60 | 0 | 92 | -38 | 144 | 77.69% | 146.75 | 73.62% | 100% | 88.62% | 7.831 | 134.03 | 1049.5889 | 21.868 | 1012.3463 | 22138.01 | 8942.3829 | 142.875 | 18 | 39 | 0 | 0 | 39 | 591 | 0 | 612 | 1016 | 1057 | 404 | 8942.3829 | 44.0417 | 1.298 | 1.398 | 14.78 | 21.32 | 19.63 | 50.07 | 0.9365 | 87.5 | 86.95 | 0.55 | 11236 | 11460 | 224 | 5.7 | 2.696
| 2019-05-15 | 84.1 | 57.5% | 67.9 | 95 | 74 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 8 | 26 | 3561 | 3433 | 3150 | 3148 | 3240 | 42 | 0 | 43 | 0 | 60 | 0 | 92 | -2 | 143 | 94.41% | 148.375 | 88.4% | 100% | 93.29% | 7.807 | 135.35 | 1056.6774 | 26.03 | 1010.56 | 26304.8768 | 8691.7263 | 143.0417 | 0 | 0 | 0 | 0 | 15 | 934 | 0 | 1013 | 1023 | 1204 | 10 | 8691.7263 | 50.1667 | 0.897 | 0.741 | 24.2 | 21.47 | 20.15 | 50.12 | 0.9357 | 87.59 | 86.97 | 0.62 | 11250 | 11481 | 231 | 0 | 1.638
| 2019-05-16 | 86 | 51.5% | 70.5 | 97 | 74 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3537 | 3446 | 3024 | 3032 | 3118 | 42 | 0 | 43 | 0 | 60 | 0 | 86 | 8 | 132 | 98.42% | 147.375 | 85.72% | 100% | 89.66% | 7.83 | 138.79 | 1086.7257 | 24.862 | 1004.1298 | 24964.705 | 8592.1605 | 143.5833 | 0 | 0 | 0 | 0 | 15 | 1440 | 0 | 1008 | 1022 | 1088 | 14 | 8592.1605 | 45.3333 | 0.4 | 0.181 | 24.281 | 21.566 | 19.892 | 50.09 | 0.9351 | 87.55 | 86.93 | 0.62 | 11321 | 11523 | 202 | 4.95 | 0.581
| 2019-05-17 | 80.3 | 66.7% | 69 | 88 | 72 | 14 | 28 | 20 | 46 | 9 | 16 | 2 | 57 | 0 | 0 | 3595 | 3479 | 2227 | 2240 | 2307 | 42 | 0 | 43 | 0 | 60 | 0 | 71 | 13 | 132 | 72.82% | 149.7917 | 62.31% | 100% | 83.86% | 6.678 | 132.66 | 885.9035 | 18.6742 | 997.4424 | 18626.421 | 8710.8591 | 144.9583 | 16 | 16 | 19 | 17 | 23 | 1440 | 4 | 618 | 891 | 798 | 273 | 8710.8591 | 33.25 | 0.236 | 0.118 | 14.94 | 18.93 | 17.46 | 50.12 | 0.9371 | 87.75 | 86.92 | 0.83 | 11341 | 11547 | 206 | 0 | 0.354
| 2019-05-18 | 83.4 | 60.9% | 75.5 | 93 | 73 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3562 | 3520 | 0 | 0 | 0 | 42 | 0 | 43 | 0 | 60 | 0 | 14 | 0 | 0 | no data | 148.4167 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 146.6667 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 50.1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| 2019-05-19 | 89.5 | 51.5% | 70.3 | 102 | 77 | 0 | 0 | 2 | 42 | 24 | 0 | 19 | 8 | 0 | 0 | 3499 | 3477 | 211 | 209 | 223 | 42 | 0 | 43 | 0 | 60 | 0 | 27 | -2 | 62 | 14.99% | 145.7917 | 5.973% | 100% | 95.32% | 1.615 | 151.58 | 244.8017 | 2.1419 | 995.9484 | 2133.181 | 11377.9077 | 144.875 | 0 | 0 | 19 | 130 | 41 | 178 | 13 | 0 | 166 | 57 | 166 | 11377.9077 | 2.375 | 0 | 0 | 0 | 3.98 | 3.36 | 50.11 | 0.9306 | 0 | 87.21 |  | 0 | 11699 | 11699 | 0 | 0
| 2019-05-20 | 88.7 | 45.4% | 72.3 | 101 | 77 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3508 | 3494 | 0 | 0 | 0 | 42 | 0 | 43 | 0 | 60 | 0 | 17 | 0 | 0 | no data | 146.1667 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 145.5833 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 50.09 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
Week 21 | 2019-05-21 | 93.6 | 42.4% | 63.9 | 105 | 80 | 11 | 38 | 12 | 23 | 11 | 23 | 9 | 10 | 5 | 8 | 3464 | 3452 | 1674 | 1649 | 1706 | 42 | 0 | 43 | 0 | 60 | 0 | 61 | -25 | 145 | 49.02% | 144.3333 | 47.6% | 100% | 94.62% | 4.364 | 143.7 | 627.1068 | 14.4711 | 994.8462 | 14396.558 | 9110.7731 | 143.8333 | 23 | 59 | 16 | 147 | 17 | 443 | 4 | 495 | 584 | 627 | 89 | 8737.953 | 26.125 | 0.531 | 0.474 | 23.36 | 21.37 | 18.59 | 50.13 | 0.935 | 87.7 | 87.3 |  | 11406 | 11607 | 201 | 7.6 | 1.005
| 2019-05-22 | 93.3 | 44.8% | 74.9 | 104 | 83 | 15 | 36 | 24 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 3462 | 3137 | 2438 | 2400 | 2482 | 42 | 0 | 43 | 0 | 60 | 0 | 82 | -38 | 128 | 80.79% | 144.25 | 69.32% | 100% | 82.51% | 7.711 | 136.56 | 1053.0142 | 20.0076 | 995.5254 | 19918.073 | 8737.953 | 130.7083 | 22 | 24 | 0 | 0 | 25 | 1440 | 0 | 650 | 1010 | 822 | 360 | 8605.3389 | 34.25 | 0 | 0 | 15.86 | 21.47 | 18.61 | 50.1 | 0.9365 | 87.58 | 87.16 |  | 11371 | 11538 | 167 | 3.75 | 0
| 2019-05-23 | 91.28 | 46.1% | 74.33 | 102.4 | 79.84 | 23 | 1 | 24 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 3488 | 3025 | 2950 | 2886 | 2968 | 41 | 0 | 42 | 0 | 60 | 0 | 82 | -64 | 128 | 96.61% | 145.3333 | 82.74% | 100% | 87.3% | 7.66 | 138.9 | 1063.974 | 23.882 | 995.3551 | 23771.034 | 8605.3389 | 126.0417 | 15 | 16 | 0 | 0 | 18 | 1440 | 0 | 961 | 1007 | 1000 | 46 | 8605.3389 | 41.6667 | 0 | 0 | 24.09 | 21.4 | 18.95 | 50.1 | 0.936 | 87.65 | 87.16 |  | 11360 | 11534 | 174 | 0 | 0
| 2019-05-24 | 87.33 | 54.9% | 75.55 | 97.05 | 76.7 | 9 | 35 | 24 | 0 | 13 | 25 | 0 | 0 | 0 | 0 | 3525 | 3282 | 2090 | 2046 | 2124 | 41 | 0 | 42 | 0 | 60 | 0 | 78 | -44 | 126 | 70.24% | 146.875 | 58.04% | 100% | 77.74% | 7.597 | 131.56 | 999.4613 | 17.2302 | 994.7818 | 17140.3029 | 8865.9649 | 136.75 | 20 | 60 | 0 | 0 | 31 | 1440 | 0 | 417 | 1011 | 696 | 594 | 8865.9649 | 29 | 0 | 0 | 24 | 21.44 | 19.12 | 50.14 | 0.9382 | 87 | 87.07 |  | 11234 | 11551 |  | 5.9 | 0
| 2019-05-25 | 87 | 49.8% | 75.3 | 99 | 75 | 14 | 3 | 24 | 0 | 9 | 24 | 0 | 0 | 0 | 0 | 3529 | 3224 | 2384 | 2334 | 2411 | 42 | 0 | 42 | 0 | 60 | 0 | 77 | -50 | 127 | 79.1% | 147.0417 | 66.14% | 100% | 81.66% | 7.629 | 132 | 1007.028 | 19.4927 | 994.2431 | 19380.4661 | 8735.0018 | 134.3333 | 18 | 33 | 0 | 0 | 26 | 1440 | 0 | 597 | 1017 | 797 | 420 | 8735.0018 | 33.2083 | 0 | 0 | 24.13 | 21.65 | 18.93 | 50.15 | 0.9379 | 87.7 | 86.98 |  | 11377 | 11549 |  | 0 | 0
| 2019-05-26 | 91 | 44% | 73 | 103 | 78 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3481 | 3009 | 3009 | 2943 | 3030 | 42 | 0 | 42 | 0 | 60 | 0 | 87 | -66 | 128 | 98.63% | 145.0417 | 84.54% | 100% | 87.5% | 7.62 | 132.94 | 1013.0028 | 24.0746 | 1000.244 | 24080.4856 | 8526.4996 | 125.375 | 0 | 0 | 0 | 0 | 18 | 1440 | 0 | 1001 | 1007 | 1022 | 6 | 8526.4996 | 42.5833 | 0 | 0 | 24 | 21.34 | 18.52 | 50.11 | 0.9377 | 87.57 | 87.06 |  | 11282 | 11498 |  | 4.8 | 0
| 2019-05-27 | 94.9 | 35.7% | 72.3 | 107 | 83 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3447 | 3013 | 3013 | 2950 | 3036 | 42 | 0 | 42 | 0 | 60 | 0 | 86 | -63 | 129 | 98.06% | 143.625 | 85.58% | 100% | 88.19% | 7.635 | 130.6 | 997.131 | 23.8291 | 1012.3088 | 24122.4226 | 8515.1029 | 125.5417 | 0 | 0 | 0 | 0 | 17 | 1440 | 0 | 1000 | 1011 | 1025 | 11 | 8515.1029 | 42.7083 | 0 | 0 | 23.91 | 21.28 | 18.51 | 50.12 | 0.9386 | 87.39 | 87.04 |  | 11230 | 11441 |  | 0 | 0
Week 22 | 2019-05-28 | 97 | 34.5% | 72.9 | 109 | 83 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3429 | 3006 | 3006 | 2935 | 3024 | 41 | 0 | 42 | 0 | 60 | 0 | 89 | -71 | 129 | 97.67% | 142.875 | 85.59% | 100% | 87.41% | 7.674 | 141.11 | 1082.8781 | 23.706 | 1014.93 | 24059.9306 | 8566.5447 | 125.25 | 0 | 0 | 0 | 0 | 18 | 1440 | 0 | 994 | 1007 | 1023 | 13 | 8566.5447 | 42.625 | 0 | 0 | 23.78 | 21.21 | 18.37 | 50.11 | 0.936 | 87.39 | 87.11 | 0 | 11243 | 11440 | 5.3
| 2019-05-29 | 97.9 | 36.7% | 74.7 | 112 | 84 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3417 | 2983 | 2983 | 2918 | 3004 | 41 | 0 | 42 | 0 | 60 | 0 | 86 | -65 | 127 | 98.56% | 142.375 | 85.4% | 100% | 87.41% | 7.576 | 135.67 | 1027.8359 | 23.541 | 1014.06 | 23871.9865 | 8533.1811 | 124.2917 | 0 | 0 | 0 | 0 | 18 | 1440 | 0 | 986 | 1000 | 1018 | 14 | 8533.1811 | 42.4167 | 0 | 0 | 23.65 | 21 | 18.65 | 50.12 | 0.9371 | 87.53 | 86.76 | 0 | 11264 | 11414 | 0
| 2019-05-30 | 98.5 | 34.8% | 74.3 | 112 | 84 | 22 | 15 | 22 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 3409 | 2977 | 2977 | 2743 | 2827 | 41 | 70 | 42 | 55 | 60 | 100 | 86 | -234 | 128 | 92.02% | 142.0417 | 80.46% | 94.57% | 81.08% | 7.186 | 136.99 | 984.4101 | 22.531 | 1015.223 | 22873.9894 | 8697.9218 | 124.0417 | 11 | 35 | 12 | 49 | 20 | 1340 | 2 | 936 | 952 | 939 | 16 | 8697.9218 | 39.125 | 0 | 0 | 22.56 | 20.22 | 17.65 | 50.1 | 0.9369 | 87.33 | 86.7 | 0 | 11276 | 11482 | 0
| 2019-05-31 | 99 | 37.98% | 75.2 | 111 | 85 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3404 | 2961 | 2961 | 2893 | 2978 | 41 | 0 | 42 | 0 | 60 | 0 | 85 | -68 | 127 | 97.7% | 141.8333 | 84.99% | 100% | 87.41% | 7.583 | 134.95 | 1023.3258 | 23.565 | 1007.8 | 23748.807 | 8562.7836 | 123.375 | 0 | 0 | 0 | 0 | 18 | 1440 | 0 | 983 | 988 | 1007 | 5 | 8562.7836 | 0 | 0 | 0 | 23.65 | 20.96 | 18.39 | 50.1 | 0.9375 | 87.56 | 86.56 | 0 | 11302 | 11537 | 5.3
| 2019-06-01 | 100.7 | 35% | 76.2 | 114 | 86 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3389 | 2953 | 2953 | 2885 | 2972 | 41 | 0 | 41 | 0 | 60 | 0 | 87 | -68 | 127 | 97.51% | 141.2083 | 85.13% | 100% | 87.32% | 7.57 | 134.32 | 1016.8024 | 23.5144 | 1007.2951 | 23685.97 | 8562.4861 | 123.0417 | 0 | 0 | 0 | 0 | 18 | 1440 | 0 | 978 | 984 | 1010 | 6 | 8562.4861 | 0 | 0 | 0 | 23.58 | 20.93 | 18.3 | 50.12 | 0.9384 | 87.56 | 86.79 | 0 | 11329 | 11574 | 0
| 2019-06-02 | 101.9 | 34.2% | 76.2 | 114 | 87 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3372 | 2957 | 2957 | 2895 | 2979 | 41 | 0 | 41 | 0 | 60 | 0 | 84 | -62 | 127 | 97.74% | 140.5 | 85.85% | 100% | 87.32% | 7.567 | 139.14 | 1052.8724 | 23.5133 | 1007.0292 | 23678.6 | 8542.8229 | 123.2083 | 0 | 0 | 0 | 0 | 18 | 1440 | 0 | 980 | 988 | 1011 | 8 | 8542.8229 | 0 | 0 | 0 | 23.63 | 20.9 | 18.59 | 50.12 | 0.9362 | 87.78 | 86.72 | 0 | 11335 | 11525 | 5.5
| 2019-06-03 | 102.2 | 30.78% | 74.73 | 115.24 | 87.23 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 3369 | 3145 | 3145 | 3092 | 3187 | 41 | 0 | 41 | 0 | 60 | 0 | 95 | -53 | 142 | 93.52% | 140.375 | 91.78% | 100% | 94.35% | 7.54 | 134.79 | 1016.3166 | 25.7112 | 1006.6749 | 25882.79 | 8699.5817 | 131.0417 | 0 | 0 | 0 | 0 | 17.5 | 660 | 0 | 982 | 989 | 1216 | 7 | 8699.5817 | 50.6667 | 1.061 | 1.12 | 23.65 | 21 | 18.14 | 50.14 | 0.9379 | 87.73 | 86.66 | 2.181 | 11327 | 11538 | 0
Week 23 | 2019-06-04 | 97.6 | 38.8% | 75.6 | 108 | 85 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 3421 | 3118 | 3118 | 3047 | 3136 | 41 | 0 | 41 | 0 | 60 | 0 | 89 | -71 | 143 | 91.38% | 142.5417 | 89.07% | 100% | 92.08% | 7.536 | 130.84 | 986.0102 | 25.3227 | 1004.0406 | 25425.03 | 8667.8832 | 129.9167 | 0 | 0 | 0 | 0 | 15 | 1080 | 0 | 985 | 985 | 1166 | 0 | 8667.8832 | 48.5833 | 0.861 | 0.661 | 23.78 | 20.99 | 18.35 | 50.11 | 0.9389 | 87.78 | 86.89 | 1.522 | 11345 | 11586 | 5.02
| 2019-06-05 | 95.7 | 42% | 76.1 | 107 | 86 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3439 | 3026 | 3026 | 2969 | 3050 | 41 | 0 | 41 | 0 | 60 | 0 | 81 | -57 | 130 | 97.76% | 143.2917 | 86.33% | 100% | 89.44% | 7.54 | 130.43 | 983.4422 | 24.3497 | 1007.1175 | 24523.01 | 8590.9236 | 126.0833 | 0 | 0 | 0 | 0 | 15 | 1440 | 0 | 984 | 984 | 1082 | 0 | 8590.9236 | 45.0833 | 0.465 | 0.297 | 23.74 | 20.95 | 18.3 | 50.1 | 0.9389 | 87.86 | 86.86 | 0.762 | 11337 | 11558 | 0
| 2019-06-06 | 95.9 | 34.7% | 72.7 | 109 | 83 | 20 | 2 | 24 | 0 | 3 | 20 | 0 | 0 | 4 | 0 | 3442 | 3185 | 2880 | 2825 | 2909 | 41 | 0 | 42 | 0 | 60 | 0 | 84 | -55 | 146 | 83.02% | 143.4167 | 82.07% | 100% | 88.05% | 7.509 | 133.78 | 1004.554 | 23.5486 | 1004.9536 | 23665.3 | 8732.6917 | 132.7083 | 16 | 38 | 0 | 0 | 20 | 1200 | 0 | 849 | 1000 | 1060 | 0 | 8732.6917 | 44.1667 | 0.682 | 0.667 | 20.66 | 21.31 | 18.22 | 50.12 | 0.9376 | 87.52 | 86.65 | 1.349 | 11367 | 11545 | 5.7
| 2019-06-07 | 97.6 | 37% | 74.7 | 109 | 84 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 7 | 20 | 3420 | 3160 | 3160 | 3093 | 3181 | 41 | 0 | 41 | 0 | 60 | 0 | 88 | -67 | 146 | 90.78% | 142.5 | 90.44% | 100% | 92.66% | 7.531 | 134.98 | 1016.5344 | 25.797 | 1001.4913 | 25835.5 | 8681.5501 | 131.6667 | 0 | 0 | 0 | 0 | 15 | 1000 | 0 | 993 | 990 | 1198 | -3 | 8681.5501 | 49.9167 | 1.011 | 0.935 | 24.02 | 21.17 | 18.24 | 50.11 | 0.9376 | 87.57 | 86.73 | 1.946 | 11370 | 11593 | 0
| 2019-06-08 | 99 | 37.4% | 74.8 | 108 | 86 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 3410 | 3057 | 3057 | 2990 | 3076 | 41 | 0 | 41 | 0 | 60 | 0 | 86 | -67 | 144 | 89% | 142.0833 | 87.68% | 100% | 89.88% | 7.474 | 130.66 | 976.5528 | 24.8078 | 997.708 | 24750.91 | 8604.5026 | 127.375 | 0 | 0 | 0 | 0 | 15 | 1380 | 0 | 991 | 987 | 1098 | -4 | 8604.5026 | 45.75 | 0.554 | 0.335 | 23.99 | 21.17 | 17.96 | 50.1 | 0.9391 | 87.56 | 86.7 | 0.889 | 11388 | 11622 | 5.25
| 2019-06-09 | 99.8 | 37% | 75.9 | 112 | 85 | 24 | 0 | 22 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 3395 | 2981 | 2981 | 2912 | 2999 | 41 | 0 | 41 | 0 | 60 | 0 | 87 | -69 | 130 | 96.12% | 141.4583 | 85.77% | 100% | 87.88% | 7.474 | 133.39 | 996.9569 | 24.2548 | 996.8357 | 24178.039 | 8645.2596 | 124.2083 | 0 | 0 | 19 | 92 | 16 | 1440 | 0 | 984 | 956 | 1059 | -28 | 8645.2596 | 44.125 | 0.434 | 0.244 | 23.95 | 20.78 | 17.22 | 50.12 | 0.9386 | 87.65 | 86.74 | 0.678 | 11441 | 11675 | 0
| 2019-06-10 | 101.2 | 37.1% | 76.2 | 113 | 87 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 3382 | 3146 | 3146 | 3086 | 3179 | 41 | 0 | 41 | 0 | 60 | 0 | 93 | -60 | 142 | 93.28% | 140.9167 | 91.25% | 100% | 94.28% | 7.4 | 130.3 | 964.22 | 26.0233 | 998.0429 | 25972.4 | 8728.652 | 131.0833 | 0 | 0 | 0 | 0 | 15 | 780 | 0 | 979 | 977 | 1223 | -2 | 8728.652 | 50.9583 | 1.267 | 1.192 | 23.84 | 21 | 18.03 | 50.14 | 0.9391 | 87.62 | 86.73 | 2.459 | 11435 | 11649 | 5.35
Week 24 | 2019-06-11 | 100.1 | 41.3% | 77 | 110 | 93 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 3394 | 3155 | 3155 | 3087 | 3181 | 40 | 0 | 41 | 0 | 60 | 0 | 94 | -68 | 141 | 94% | 141.4167 | 90.95% | 100% | 94.68% | 7.379 | 131.62 | 971.224 | 25.9337 | 1001.3642 | 25969.119 | 8727.0304 | 131.4583 | 0 | 0 | 0 | 0 | 15 | 720 | 0 | 968 | 972 | 1241 | 4 | 8727.0304 | 51.7083 | 1.335 | 1.263 | 23.44 | 20.71 | 18.04 | 50.1 | 0.9385 | 87.46 | 86.74 | 2.598 | 11367 | 11569 | 0
| 2019-06-12 | 94.73 | 41.47% | 75.6 | 104 | 86 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 8 | 3 | 3454 | 3174 | 3160 | 3060 | 3151 | 41 | 0 | 41 | 0 | 60 | 0 | 91 | -100 | 140 | 93.78% | 143.9167 | 88.59% | 100% | 92.98% | 7.382 | 132.36 | 977.0815 | 25.5395 | 1006.8686 | 25714.949 | 8722.8858 | 132.25 | 0 | 0 | 0 | 0 | 15 | 957 | 0 | 981 | 981 | 1189 | 0 | 8722.8858 | 49.5417 | 0.861 | 0.956 | 23.68 | 20.86 | 18.2 | 50.12 | 0.938 | 87.52 | 86.83 | 1.817 | 11345 | 11542 | 6.25
| 2019-06-13 | 95.95 | 36.3% | 73.5 | 109 | 83 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 12 | 55 | 3437 | 3357 | 3175 | 3144 | 3240 | 41 | 0 | 41 | 0 | 60 | 0 | 96 | -31 | 142 | 95.07% | 143.2083 | 91.48% | 100% | 95.12% | 7.449 | 135.31 | 1007.9242 | 26.5489 | 997.9043 | 26493.221 | 8747.1836 | 139.875 | 0 | 0 | 0 | 0 | 15 | 665 | 0 | 993 | 990 | 1257 | -3 | 8747.1836 | 52.375 | 1.352 | 1.314 | 23.97 | 21.08 | 18.03 | 50.11 | 0.9373 | 87.42 | 86.7 | 2.666 | 11359 | 11545 | 0
| 2019-06-14 | 100.55 | 35.17% | 75.11 | 112 | 86 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 3390 | 3168 | 3168 | 3109 | 3203 | 41 | 0 | 41 | 0 | 60 | 0 | 94 | -59 | 140 | 95.33% | 141.25 | 91.71% | 100% | 95.16% | 7.453 | 133.15 | 992.3669 | 26.2413 | 996.6999 | 26154.66 | 8731.7552 | 132 | 0 | 0 | 0 | 0 | 15 | 660 | 0 | 981 | 982 | 1240 | 1 | 8731.7552 | 51.6667 | 1.236 | 1.213 | 23.76 | 20.95 | 17.9 | 50.14 | 0.9381 | 87.39 | 86.66 | 2.449 | 11368 | 11553 | 6.02
| 2019-06-15 | 98.52 | 51.86% | 80.72 | 107 | 89 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 3409 | 3150 | 3150 | 3080 | 3174 | 40 | 0 | 40 | 0 | 60 | 0 | 94 | -70 | 140 | 94.46% | 142.0417 | 90.35% | 100% | 94.76% | 7.43 | 135.33 | 1005.5019 | 26.2364 | 996.8628 | 26154.1 | 8818.0526 | 131.25 | 0 | 0 | 0 | 0 | 16 | 660 | 0 | 962 | 961 | 1251 | -1 | 8818.0526 | 52.125 | 1.417 | 1.375 | 23.44 | 20.59 | 18.07 | 50.12 | 0.9373 | 87.85 | 86.96 | 2.792 | 11452 | 11635 | 0
| 2019-06-16 | 93.3 | 52.96% | 79.35 | 103.2 | 80.06 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3469 | 2984 | 2984 | 2918 | 3004 | 41 | 0 | 41 | 0 | 60 | 0 | 86 | -66 | 129 | 97.03% | 144.5417 | 84.12% | 100% | 88.73% | 7.405 | 134.4 | 995.232 | 24.266 | 998.3781 | 24226.6562 | 8643.5532 | 124.3333 | 0 | 0 | 0 | 0 | 16 | 1440 | 0 | 974 | 971 | 1059 | -3 | 8643.5532 | 44.125 | 0.354 | 0.227 | 23.64 | 20.68 | 18.22 | 50.15 | 0.9377 | 87.83 | 87.02 | 0.581 | 11404 | 11567 | 0
| 2019-06-17 | 95.23 | 54.43% | 80.26 | 102 | 88.96 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3448 | 2964 | 2964 | 2898 | 2987 | 40 | 0 | 40 | 0 | 60 | 0 | 89 | -66 | 129 | 96.48% | 143.6667 | 84.05% | 100% | 88.57% | 7.363 | 132.39 | 974.7876 | 24.0724 | 1001.7665 | 24114.9582 | 8657.6072 | 123.5 | 0 | 0 | 0 | 0 | 16 | 1440 | 0 | 967 | 966 | 1054 | -1 | 8657.6072 | 43.9167 | 0.354 | 0.202 | 23.51 | 20.62 | 18.05 | 50.13 | 0.9382 | 87.81 | 87.02 | 0.556 | 11418 | 11594 | 0
Week 25 | 2019-06-18 | 87.9 | 56.1% | 70.4 | 99 | 76 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3523 | 3027 | 3027 | 2963 | 3050 | 41 | 0 | 41 | 0 | 60 | 0 | 87 | -64 | 129 | 98.51% | 146.7917 | 84.1% | 100% | 89.44% | 7.329 | 133.54 | 978.7147 | 24.5064 | 1001.285 | 24537.906 | 8611.7518 | 126.125 | 0 | 0 | 0 | 0 | 15 | 1440 | 0 | 990 | 988 | 1072 | -2 | 8768.8346 | 44.6667 | 0.354 | 0.202 | 23.9 | 21.38 | 17.66 | 50.17 | 0.9375 | 87.7 | 86.89 | 0.556 | 11335 | 11626 | 4.8
| 2019-06-19 | 90.4 | 55% | 78 | 102 | 78 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 3490 | 3200 | 3200 | 3126 | 3220 | 41 | 0 | 41 | 0 | 60 | 0 | 94 | -74 | 141 | 95.15% | 145.4167 | 89.57% | 100% | 95.16% | 7.337 | 137.86 | 1011.4788 | 26.4014 | 999.9428 | 26399.898 | 8768.8346 | 133.3333 | 0 | 0 | 0 | 0 | 15 | 660 | 0 | 983 | 979 | 1258 | -4 | 8824.4469 | 52.4167 | 1.32 | 1.251 | 23.8 | 20.93 | 17.93 | 50.09 | 0.936 | 87.8 | 86.98 | 2.571 | 11413 | 11574 | 0
| 2019-06-20 | 91.4 | 62.1% | 81.9 | 105 | 73 | 19 | 11 | 24 | 0 | 4 | 33 | 0 | 0 | 7 | 5 | 3483 | 3181 | 2780 | 2719 | 2805 | 40 | 0 | 40 | 0 | 60 | 0 | 86 | -61 | 139 | 84.08% | 145.125 | 78.06% | 100% | 88.8% | 7.315 | 136.48 | 998.3512 | 22.9706 | 1001.0746 | 22995.3198 | 8824.4469 | 132.5417 | 15 | 16 | 0 | 0 | 22 | 1015 | 0 | 776 | 969 | 1060 | 193 | 8824.4469 | 44.1667 | 0.827 | 0.844 | 18.94 | 20.72 | 17.63 | 50.16 | 0.9364 | 87.91 | 87.1 | 1.671 | 11442 | 11574 | 0
| 2019-06-21 | 87.6 | 61.5% | 78.9 | 97 | 77 | 13 | 49 | 24 | 0 | 9 | 20 | 0 | 0 | 0 | 40 | 3517 | 3207 | 2367 | 2335 | 2412 | 40 | 0 | 41 | 0 | 60 | 0 | 77 | -32 | 133 | 75.56% | 146.5417 | 66.39% | 100% | 82.34% | 7.181 | 136.65 | 981.2836 | 19.7278 | 1000.4904 | 19737.4799 | 8873.1321 | 133.625 | 17 | 51 | 0 | 0 | 25 | 1400 | 0 | 579 | 980 | 853 | 401 | 8873.1321 | 35.5417 | 0.288 | 0.528 | 14.26 | 21.01 | 17.62 | 50.13 | 0.9364 | 87.95 | 87.02 | 0.816 | 11431 | 11552 | 0.75
| 2019-06-22 | 95.4 | 56% | 82.3 | 105 | 87 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3445 | 2961 | 2961 | 2897 | 2983 | 40 | 0 | 40 | 0 | 60 | 0 | 86 | -64 | 126 | 98.64% | 143.5417 | 84.09% | 100% | 88.57% | 7.29 | 138.01 | 1006.0929 | 24.2519 | 999.5069 | 24239.9317 | 8714.5408 | 123.375 | 0 | 0 | 0 | 0 | 16 | 1440 | 0 | 961 | 962 | 1060 | 1 | 8714.5408 | 44.1667 | 0.404 | 0.253 | 23.56 | 20.87 | 17.64 | 50.11 | 0.9364 | 88.05 | 87.29 | 0.657 | 11519 | 11722 | 5.38
| 2019-06-23 | 93.2 | 57.2% | 81 | 106 | 82 | 21 | 51 | 24 | 0 | 1 | 54 | 0 | 0 | 0 | 0 | 3467 | 3012 | 2845 | 2780 | 2864 | 40 | 0 | 40 | 0 | 60 | 0 | 84 | -65 | 127 | 93.96% | 144.4583 | 80.18% | 100% | 87.03% | 7.177 | 139 | 997.603 | 23.379 | 994.0145 | 23239.078 | 8718.2306 | 125.5 | 15 | 15 | 0 | 0 | 18 | 1440 | 0 | 883 | 967 | 1014 | 84 | 8718.2306 | 42.25 | 0.354 | 0.253 | 21.68 | 20.97 | 17.59 | 50.12 | 0.9356 | 87.97 | 87.3 | 0.607 | 11529 | 11706 | 0.75
| 2019-06-24 | 86.5 | 65.6% | 80.4 | 96.48 | 79 | 11 | 16 | 24 | 0 | 12 | 6 | 0 | 0 | 1 | 3 | 3535 | 3271 | 2193 | 2149 | 2232 | 40 | 0 | 41 | 0 | 60 | 0 | 83 | -44 | 140 | 66.43% | 147.2917 | 60.79% | 100% | 79.98% | 7.092 | 136.42 | 967.4906 | 18.306 | 996.2806 | 18237.912 | 8936.9021 | 136.2917 | 19 | 38 | 0 | 0 | 29 | 1377 | 0 | 471 | 982 | 779 | 511 | 8936.9021 | 32.4583 | 0.333 | 0.417 | 11.63 | 21.08 | 17.84 | 50.15 | 0.9366 | 88.17 | 87.17 | 0.75 | 11461 | 11601 | 4.8
Week 26 | 2019-06-25 | 92.2 | 61.8% | 82.6 | 102 | 83 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3474 | 2916 | 2916 | 2855 | 2939 | 40 | 0 | 41 | 0 | 60 | 0 | 84 | -61 | 126 | 97.19% | 144.75 | 82.18% | 100% | 87.23% | 7.255 | 136 | 986.68 | 23.904 | 994.7289 | 23777.9996 | 8674.1435 | 121.5 | 0 | 0 | 0 | 0 | 18 | 1440 | 0 | 965 | 964 | 1010 | -1 | 8674.1435 | 42.0833 | 0.131 | 0.099 | 23.61 | 20.89 | 17.6 | 50.15 | 0.9366 | 88.14 | 87.32 | 0.23 | 11495 | 11708 | 5.35
| 2019-06-26 | 93.7 | 57.5% | 81 | 106 | 82 | 14 | 2 | 24 | 0 | 9 | 8 | 0 | 0 | 0 | 0 | 3358 | 3106 | 2277 | 2231 | 2308 | 40 | 0 | 41 | 0 | 60 | 0 | 77 | -46 | 123 | 78.18% | 139.9167 | 66.44% | 100% | 79.7% | 7.071 | 135.4 | 957.4134 | 18.863 | 1001.007 | 18881.995 | 8892.608 | 129.4167 | 18 | 50 | 0 | 0 | 28 | 1440 | 0 | 576 | 963 | 769 | 387 | 8892.608 | 32.0417 | 0 | 0 | 14.23 | 20.76 | 17.38 | 50.14 | 0.9366 | 87.99 | 87.25 | 0 | 11455 | 11617 | 0
| 2019-06-27 | 91 | 60.1% | 80 | 100 | 80 | 15 | 0 | 24 | 0 | 8 | 23 | 0 | 0 | 0 | 0 | 3485 | 3182 | 2313 | 2281 | 2360 | 40 | 0 | 40 | 0 | 60 | 0 | 79 | -32 | 122 | 80.6% | 145.2083 | 65.45% | 100% | 80.29% | 7.34 | 139.55 | 1024.297 | 19.305 | 999.27 | 19290.9074 | 8906.2711 | 132.5833 | 23 | 37 | 0 | 0 | 27 | 1440 | 0 | 609 | 961 | 790 | 352 | 8906.2711 | 32.9167 | 0 | 0 | 15.08 | 20.8 | 17.51 | 50.09 | 0.9346 | 88.27 | 87.12 | 0 | 11513 | 11674 | 6.57
| 2019-06-28 | 96.47 | 59.49% | 84.66 | 107 | 87 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3432 | 2863 | 2863 | 2794 | 2880 | 40 | 0 | 39 | 0 | 60 | 0 | 86 | -69 | 124 | 96.77% | 143 | 81.41% | 100% | 86.33% | 7.337 | 134.18 | 984.4787 | 23.3833 | 992.3606 | 23204.7115 | 8657.5484 | 119.2917 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 953 | 946 | 981 | -7 | 8657.5484 | 40.875 | 0 | 0 | 23.43 | 20.66 | 17.64 | 50.1 | 0.9366 | 88.35 | 87.19 | 0 | 11548 | 11820 | 3.42
| 2019-06-29 | 96.86 | 56.8% | 82 | 106.5 | 84.7 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3428 | 2880 | 2880 | 2810 | 2891 | 40 | 0 | 40 | 0 | 60 | 0 | 81 | -70 | 124 | 97.14% | 142.8333 | 81.97% | 100% | 86.43% | 7.342 | 133.64 | 981.1849 | 23.3734 | 995.5204 | 23268.7399 | 8629.8665 | 120 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 957 | 949 | 985 | -8 | 8629.8665 | 41.0417 | 0 | 0 | 23.36 | 20.6 | 17.52 | 50.13 | 0.9368 | 88.18 | 87.15 | 0 | 11463 | 11729 | 0
| 2019-06-30 | 95.5 | 53.1% | 80.5 | 104 | 85 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3443 | 2895 | 2895 | 2833 | 2919 | 40 | 0 | 40 | 0 | 60 | 0 | 86 | -62 | 124 | 98.08% | 143.4583 | 82.28% | 100% | 86.43% | 7.441 | 132.86 | 988.6113 | 23.5201 | 997.461 | 23460.3998 | 8630.078 | 120.625 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 968 | 959 | 992 | -9 | 8630.078 | 41.3333 | 0 | 0 | 23.47 | 20.68 | 17.63 | 50.12 | 0.9371 | 88.1 | 87.1 | 0 | 11415 | 11681 | 4.3
| 2019-07-01 | 99 | 54.1% | 83 | 108 | 90 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3401 | 2867 | 2867 | 2795 | 2880 | 40 | 0 | 39 | 0 | 60 | 0 | 85 | -72 | 121 | 99.17% | 141.7083 | 82.18% | 100% | 86.33% | 7.28 | 134.88 | 981.9264 | 23.3108 | 997.3051 | 23247.98 | 8669.0184 | 119.4583 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 951 | 946 | 983 | -5 | 8669.0184 | 40.9583 | 0 | 0 | 23.27 | 20.52 | 17.49 | 50.1 | 0.9365 | 88.19 | 87.15 | 0 | 11477 | 11729 | 0.8
Week 27 | 2019-07-02 | 98 | 55% | 82 | 108 | 86 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3418 | 2874 | 2874 | 2813 | 2900 | 40 | 0 | 40 | 0 | 60 | 0 | 87 | -61 | 123 | 98.24% | 142.4167 | 82.3% | 100% | 86.43% | 7.29 | 136.1 | 992.169 | 23.3825 | 998.9244 | 23357.39 | 8656.0821 | 119.75 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 959 | 954 | 987 | -5 | 8656.0821 | 41.125 | 0 | 0 | 23.3 | 20.62 | 17.44 | 50.13 | 0.9359 | 88.06 | 87.18 | 0 | 11426 | 11682 | 0.5
| 2019-07-03 | 99.2 | 52.1% | 81.9 | 110 | 86 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3407 | 2873 | 2873 | 2806 | 2893 | 40 | 0 | 40 | 0 | 60 | 0 | 87 | -67 | 124 | 97.21% | 141.9583 | 82.36% | 100% | 86.43% | 7.18 | 135.92 | 975.9056 | 23.3575 | 999.4152 | 23343.88 | 8667.0654 | 119.7083 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 957 | 951 | 985 | -6 | 8667.0654 | 41.0417 | 0 | 0 | 23.29 | 20.58 | 17.34 | 50.15 | 0.9361 | 88.1 | 87.15 | 0 | 11437 | 11686 | 3.25
| 2019-07-04 | 99.5 | 51.3% | 81.7 | 110 | 88 | 23 | 3 | 24 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 3404 | 2821 | 2821 | 2759 | 2849 | 40 | 0 | 40 | 0 | 60 | 0 | 90 | -62 | 122 | 97.3% | 141.8333 | 81.05% | 100% | 85.6% | 7.18 | 134.81 | 967.9358 | 22.9969 | 997.8749 | 22948.04 | 8668.3493 | 117.5417 | 16 | 15 | 0 | 0 | 20 | 1440 | 0 | 924 | 954 | 971 | 30 | 8668.3493 | 40.4583 | 0 | 0 | 22.55 | 20.6 | 17.28 | 50.17 | 0.9362 | 88.06 | 87.12 | 0 | 11452 | 11674 | 5.25
| 2019-07-05 | 96.8 | 59.8% | 84.9 | 107 | 87 | 16 | 33 | 24 | 0 | 7 | 6 | 0 | 0 | 0 | 0 | 3429 | 3032 | 2384 | 2326 | 2409 | 39 | 0 | 39 | 0 | 60 | 0 | 83 | -58 | 120 | 83.65% | 142.875 | 67.83% | 100% | 80.96% | 6.9 | 131.35 | 906.315 | 19.6955 | 997.3684 | 19643.62 | 8834.8818 | 126.3333 | 19 | 21 | 0 | 0 | 26 | 1440 | 0 | 657 | 940 | 812 | 283 | 8834.8818 | 33.8333 | 0 | 0 | 16.25 | 20.51 | 17.09 | 50.14 | 0.9375 | 88.37 | 87.29 | 0 | 11522 | 11755 | 0
| 2019-07-06 | 92.3 | 61.2% | 81.9 | 99 | 82 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3474 | 2868 | 2868 | 2816 | 2901 | 40 | 0 | 40 | 0 | 60 | 0 | 85 | -52 | 124 | 97.48% | 144.75 | 81.06% | 100% | 86.43% | 6.8 | 132.63 | 901.884 | 23.5227 | 996.8384 | 23448.38 | 8647.1108 | 119.5 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 962 | 955 | 984 | -7 | 8647.1108 | 41 | 0 | 0 | 23.43 | 20.69 | 17.35 | 50.15 | 0.9365 | 88.18 | 87.21 | 0 | 11444 | 11685 | 4.4
| 2019-07-07 | 94.6 | 59.5% | 83.8 | 104 | 86 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3452 | 2861 | 2861 | 2804 | 2889 | 40 | 0 | 40 | 0 | 60 | 0 | 85 | -57 | 122 | 98.67% | 143.8333 | 81.23% | 100% | 86.43% | 6.8 | 130.55 | 887.74 | 23.439 | 996.6295 | 23359.96 | 8647.5392 | 119.2083 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 955 | 952 | 982 | -3 | 8647.5392 | 40.9167 | 0 | 0 | 23.33 | 20.64 | 17.09 | 50.13 | 0.9373 | 88.23 | 87.22 | 0 | 11459 | 11683 | 0
| 2019-07-08 | 99.5 | 55.5% | 84 | 108 | 90 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3399 | 2834 | 2834 | 2770 | 2856 | 39 | 0 | 39 | 0 | 60 | 0 | 86 | -64 | 121 | 98.35% | 141.625 | 81.49% | 100% | 86.23% | 6.7 | 134.78 | 903.026 | 23.2334 | 996.6445 | 23155.42 | 8685.3596 | 118.0833 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 945 | 937 | 974 | -8 | 8685.3596 | 40.5833 | 0 | 0 | 23.13 | 20.46 | 16.09 | 50.11 | 0.9353 | 88.24 | 87.3 | 0 | 11507 | 11713 | 3.4
Week 28 | 2019-07-09 | 97.9 | 57.4% | 84.2 | 105 | 93 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3419 | 2832 | 2832 | 2768 | 2855 | 39 | 0 | 39 | 0 | 60 | 0 | 87 | -64 | 121 | 98.31% | 142.4583 | 80.96% | 100% | 85.51% | 6.7 | 132.76 | 889.492 | 23.0205 | 1006.956 | 23180.65 | 8695.8605 | 118 | 0 | 0 | 0 | 0 | 20 | 1440 | 0 | 943 | 939 | 973 | -4 | 8695.8605 | 40.5417 | 0 | 0 | 22.96 | 20.42 | 15.82 | 50.15 | 0.9355 | 88.1 | 87.43 | 0 | 11437 | 11616 | 0
| 2019-07-10 | 97.92 | 62.2% | 84.85 | 104.4 | 92.58 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3417 | 2821 | 2821 | 2757 | 2849 | 39 | 0 | 39 | 0 | 60 | 0 | 92 | -64 | 120 | 98.92% | 142.375 | 80.68% | 100% | 85.51% | 6.6 | 130.58 | 861.828 | 22.9548 | 1009.9418 | 23182.99 | 8721.3703 | 117.5417 | 0 | 0 | 0 | 0 | 20 | 1440 | 0 | 939 | 940 | 970 | 1 | 8721.3703 | 40.4167 | 0 | 0 | 22.92 | 20.4 | 15.76 | 50.11 | 0.9362 | 88.15 | 87.43 | 0 | 11447 | 11619 | 4.75
| 2019-07-11 | 96.61 | 60.71% | 83.98 | 104.5 | 91.5 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3430 | 2831 | 2831 | 2770 | 2861 | 39 | 0 | 39 | 0 | 60 | 0 | 91 | -61 | 121 | 98.52% | 142.9167 | 80.76% | 100% | 86.23% | 6.6 | 129.73 | 856.218 | 23.1079 | 1006.1144 | 23249.221 | 8702.3245 | 117.9583 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 944 | 943 | 974 | -1 | 8702.3245 | 40.5833 | 0 | 0 | 23.05 | 20.5 | 15.8 | 50.15 | 0.9363 | 88.1 | 87.35 | 0 | 11479 | 11618 | 0
| 2019-07-12 | 96 | 62% | 83.35 | 102 | 90 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3437 | 2839 | 2839 | 2780 | 2870 | 39 | 0 | 39 | 0 | 60 | 0 | 90 | -59 | 121 | 98.83% | 143.2083 | 80.88% | 100% | 86.23% | 6.6 | 128.92 | 850.872 | 23.2205 | 1005.1136 | 23339.25 | 8701.4827 | 118.2917 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 947 | 946 | 977 | -1 | 8701.4827 | 40.7083 | 0 | 0 | 23.12 | 20.61 | 15.88 | 50.13 | 0.9366 | 88.03 | 87.31 | 0 | 11473 | 11622 | 0
| 2019-07-13 | 96 | 62% | 83 | 103 | 89 | 23 | 35 | 23 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 3436 | 2810 | 2810 | 2753 | 2842 | 39 | 0 | 39 | 0 | 60 | 34 | 89 | -57 | 121 | 97.87% | 143.1667 | 80.12% | 98.97% | 84.6% | 6.65 | 133.87 | 890.2355 | 23.2012 | 1004.2753 | 23300.391 | 8787.0056 | 117.0833 | 9 | 25 | 9 | 25 | 20 | 1406 | 0 | 943 | 946 | 953 | 3 | 8787.0056 | 39.7083 | 0 | 0 | 23.05 | 20.61 | 15.95 | 50.16 | 0.9348 | 87.74 | 87.32 | 0 | 11487 | 11645 | 0
| 2019-07-14 | 95.7 | 60.3% | 82.9 | 102 | 91 | 24 | 0 | 12 | 26 | 7 | 6 | 0 | 0 | 0 | 0 | 3440 | 2754 | 2140 | 2102 | 2187 | 39 | 0 | 39 | 213 | 60 | 0 | 85 | -38 | 121 | 75.31% | 143.3333 | 61.1% | 95.82% | 73.58% | 3.459 | 145.91 | 504.7027 | 18.1552 | 1002.5994 | 18202.391 | 8899.664 | 114.75 | 0 | 0 | 18 | 55 | 30 | 1440 | 0 | 946 | 510 | 731 | -436 | 8899.664 | 30.4583 | 0 | 0 | 23.12 | 11.37 | 8.6 | 50.14 | 0.9308 | 87.66 | 87.55 | 0 | 11480 | 11648 | 5.87
| 2019-07-15 | 93.4 | 66.2% | 85.6 | 101 | 87 | 9 | 47 | 24 | 0 | 13 | 22 | 0 | 0 | 0 | 0 | 3466 | 3169 | 1985 | 1948 | 2030 | 39 | 0 | 39 | 0 | 60 | 0 | 82 | -37 | 120 | 70.49% | 144.4167 | 56.2% | 100% | 76.27% | 6.6 | 127.94 | 844.404 | 16.5273 | 1009.5031 | 16684.35 | 8998.3337 | 132.0417 | 19 | 57 | 0 | 0 | 32 | 1440 | 0 | 399 | 952 | 679 | 553 | 8998.3337 | 28.2917 | 0 | 0 | 22.91 | 20.6 | 15.9 | 50.11 | 0.937 | 87.77 | 87.56 | 0 | 11444 | 11561 | 0
Week 29 | 2019-07-16 | 92.5 | 66.8% | 85 | 100 | 86 | 1 | 5 | 24 | 0 | 22 | 41 | 0 | 0 | 0 | 0 | 3476 | 3362 | 1468 | 1426 | 1503 | 39 | 0 | 39 | 0 | 60 | 0 | 77 | -42 | 120 | 52.19% | 144.8333 | 41.02% | 100% | 85.39% | 6.5 | 134.12 | 871.78 | 11.9988 | 1017.7101 | 12211.28 | 9174.6564 | 140.0833 | 17 | 14 | 0 | 0 | 20 | 1440 | 0 | 48 | 955 | 500 | 907 | 9107.8452 | 20.8333 | 0 | 0 | 23.1 | 20.63 | 15.88 | 50.12 | 0.9347 | 87.63 | 87.51 | 0 | 11323 | 11524 | 4.87
| 2019-07-17 | 90.9 | 65.6% | 83.4 | 100 | 81 | 9 | 41 | 14 | 51 | 13 | 36 | 7 | 45 | 0 | 0 | 3489 | 3154 | 1485 | 1456 | 1516 | 39 | 0 | 39 | 0 | 60 | 0 | 70 | -29 | 120 | 52.64% | 145.375 | 41.73% | 100% | 86.75% | 4.272 | 136.37 | 582.5726 | 12.4401 | 1019.1598 | 12678.45 | 9107.8452 | 131.4167 | 20 | 43 | 14 | 84 | 27 | 900 | 10 | 395 | 625 | 496 | 230 | 8693.8783 | 20.6667 | 0 | 0 | 9.84 | 13.67 | 10.59 | 51.14 | 0.9342 | 87.8 | 87.49 | 0 | 11468 | 11577 | 0
| 2019-07-18 | 87.4 | 72.2% | 84.5 | 101 | 76 | 18 | 53 | 24 | 0 | 4 | 52 | 0 | 0 | 0 | 0 | 3528 | 3007 | 2576 | 2530 | 2612 | 40 | 0 | 40 | 0 | 60 | 0 | 82 | -46 | 125 | 87.07% | 147 | 71.71% | 100% | 83.43% | 6.1 | 126.43 | 771.223 | 20.879 | 1016.5366 | 21224.289 | 8693.8783 | 125.2917 | 19 | 15 | 0 | 0 | 23 | 1440 | 0 | 762 | 963 | 887 | 201 | 8693.8783 | 36.9583 | 0 | 0 | 23.26 | 20.87 | 15.98 | 50.18 | 0.9371 | 87.94 | 87.38 | 0 | 11379 | 11566 | 5.3
| 2019-07-19 | 88.1 | 70.3% | 83.4 | 97 | 80 | 0 | 0 | 16 | 58 | 24 | 0 | 5 | 30 | 0 | 0 | 3519 | 3446 | 1004 | 999 | 1058 | 40 | 0 | 40 | 0 | 60 | 0 | 65 | -5 | 61 | 72.27% | 146.625 | 28.39% | 100% | 78.61% | 4.174 | 133.65 | 557.8551 | 8.5752 | 1020.9681 | 8754.963 | 9322.1402 | 143.5833 | 0 | 0 | 17 | 92 | 40 | 1039 | 6 | 0 | 719 | 339 | 719 | 9322.1402 | 14.125 | 0 | 0 | 0 | 20.2 | 15.6 | 50.18 | 0.9353 | 0 | 87.34 | 0 | 0 | 11716 | 0
| 2019-07-20 | 91.3 | 66.7% | 84.5 | 98.6 | 82.8 | 14 | 57 | 24 | 0 | 8 | 27 | 0 | 0 | 0 | 0 | 3484 | 3111 | 2313 | 2271 | 2358 | 40 | 0 | 40 | 0 | 60 | 0 | 87 | -42 | 122 | 80.53% | 145.1667 | 65.18% | 100% | 76.04% | 5.7 | 127.56 | 727.092 | 19.0004 | 1015.4318 | 19293.631 | 8815.8181 | 129.625 | 22 | 36 | 0 | 0 | 33 | 1440 | 0 | 606 | 959 | 793 | 353 | 8815.8181 | 33.0417 | 0 | 0 | 9.05 | 20.9 | 15.7 | 50.14 | 0.9371 | 87.76 | 87.29 | 0 | 11244 | 11630 | 5.75
| 2019-07-21 | 93.5 | 66.6% | 86.4 | 101 | 86 | 24 | 0 | 1 | 5 | 0 | 0 | 9 | 9 | 0 | 0 | 3461 | 2267 | 1427 | 1401 | 1474 | 40 | 0 | 40 | 810 | 60 | 0 | 73 | -26 | 120 | 51.18% | 144.2083 | 40.48% | 83.93% | 55.16% | 0.225 | 123.72 | 27.837 | 12.5858 | 1006.2126 | 12663.99 | 9059.1199 | 94.4583 | 0 | 0 | 25 | 16 | 40 | 1440 | 0 | 948 | 47 | 479 | -901 | 9059.1199 | 19.9583 | 0 | 0 | 23.08 | 0.83 | 1.14 | 50.15 | 0.9379 | 87.99 | 87.4 | 0 | 11408 | 11715 | 0
| 2019-07-22 | 94.1 | 65.7% | 86.5 | 102 | 86 | 24 | 0 | 18 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 3458 | 2543 | 2511 | 2453 | 2543 | 40 | 0 | 40 | 301 | 60 | 0 | 90 | -58 | 122 | 86.85% | 144.0833 | 70.94% | 94.03% | 76.47% | 4.267 | 134.26 | 572.8874 | 20.8693 | 1005.9835 | 20994.16 | 8792.1106 | 105.9583 | 0 | 0 | 22 | 38 | 24 | 1440 | 0 | 949 | 740 | 854 | -209 | 8792.1106 | 35.5833 | 0 | 0 | 23.26 | 16.31 | 12.38 | 50.15 | 0.9348 | 88.05 | 87.45 | 0 | 11534 | 11688 | 5.77
Week 30 | 2019-07-23 | 96.1 | 60% | 85.1 | 105 | 87 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3441 | 2860 | 2860 | 2791 | 2880 | 40 | 0 | 40 | 0 | 60 | 0 | 89 | -69 | 121 | 99.17% | 143.375 | 81.11% | 100% | 86.43% | 5.72 | 126.41 | 723.0652 | 23.3983 | 1007.0129 | 23562.359 | 8701.3344 | 119.1667 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 947 | 949 | 984 | 2 | 8701.3344 | 41 | 0 | 0 | 23.24 | 20.86 | 15.84 | 50.13 | 0.9376 | 87.99 | 87.41 | 0 | 11532 | 11739 | 0
| 2019-07-24 | 98.8 | 59.9% | 86.4 | 108 | 90 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3407 | 2834 | 2834 | 2765 | 2850 | 39 | 0 | 39 | 0 | 60 | 0 | 85 | -69 | 121 | 98.14% | 141.9583 | 81.16% | 100% | 85.51% | 5.75 | 131.77 | 757.6775 | 23.3778 | 1002.7295 | 23441.57 | 8751.9882 | 118.0833 | 0 | 0 | 0 | 0 | 20 | 1440 | 0 | 936 | 938 | 976 | 2 | 8751.9882 | 40.6667 | 0 | 0 | 23.15 | 20.73 | 15.75 | 50.14 | 0.9358 | 88 | 87.44 | 0 | 11622 | 11803 | 0
| 2019-07-25 | 95.8 | 60.9% | 83.9 | 102 | 86 | 15 | 53 | 21 | 35 | 5 | 11 | 0 | 0 | 0 | 0 | 3439 | 2981 | 2261 | 2222 | 2302 | 40 | 106 | 40 | 79 | 60 | 133 | 81 | -39 | 123 | 77.98% | 143.2917 | 64.61% | 92.37% | 75.28% | 5.323 | 125.66 | 668.8882 | 19.3612 | 1001.891 | 19397.7905 | 9030.9085 | 124.2083 | 15 | 70 | 11 | 66 | 25 | 1307 | 1 | 660 | 880 | 762 | 220 | 9030.9085 | 31.75 | 0 | 0 | 16.54 | 19.56 | 15 | 50.16 | 0.9377 | 88.18 | 87.34 | 0 | 11585 | 11805 | 6.2
| 2019-07-26 | 86.2 | 75.8% | 85.2 | 93 | 78 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3536 | 2895 | 2895 | 2829 | 2917 | 40 | 0 | 40 | 0 | 60 | 0 | 88 | -66 | 124 | 98.02% | 147.3333 | 80.01% | 100% | 86.43% | 5.62 | 125.93 | 707.7266 | 24.0018 | 999.9308 | 24000.18 | 8733.7952 | 120.625 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 968 | 957 | 992 | -11 | 8733.7952 | 41.3333 | 0 | 0 | 23.66 | 20.99 | 16 | 50.14 | 0.9373 | 88.14 | 87.28 | 0 | 11497 | 11701 | 0
| 2019-07-27 | 88.5 | 74.4% | 86.7 | 97 | 83 | 10 | 52 | 18 | 40 | 9 | 52 | 5 | 2 | 0 | 0 | 3510 | 2917 | 1800 | 1743 | 1805 | 39 | 0 | 39 | 0 | 60 | 0 | 67 | -57 | 121 | 62.16% | 146.25 | 49.66% | 100% | 83.46% | 4.392 | 127.28 | 559.0138 | 14.9535 | 999.8502 | 14951.25 | 8898.6023 | 121.5417 | 22 | 35 | 13 | 18 | 32 | 996 | 5 | 455 | 741 | 609 | 286 | 8898.6023 | 25.375 | 0 | 0 | 11.4 | 16.38 | 12.37 | 50.12 | 0.9371 | 88.24 | 87.37 | 0 | 11577 | 11765 | 6
| 2019-07-28 | 87.8 | 75.7% | 86.9 | 94 | 84 | 0 | 0 | 16 | 29 | 24 | 0 | 6 | 31 | 0 | 0 | 3514 | 3440 | 938 | 941 | 994 | 39 | 0 | 39 | 0 | 60 | 0 | 60 | 3 | 60 | 69.03% | 146.4167 | 26.78% | 100% | 79.28% | 3.987 | 138.71 | 553.0368 | 8.2486 | 999.8974 | 8247.718 | 9352.5555 | 143.3333 | 0 | 0 | 18 | 60 | 41 | 978 | 7 | 0 | 677 | 317 | 677 | 9352.5555 | 13.2083 | 0 | 0 | 0 | 15.19 | 11.2 | 50.13 | 0.9333 | 0 | 87.34 | 0 | 0 | 11796 | 0
| 2019-07-29 | 87.03 | 77.02% | 87.05 | 98 | 84 | 14 | 27 | 24 | 0 | 8 | 45 | 0 | 0 | 0 | 0 | 3526 | 3124 | 2279 | 2247 | 2326 | 39 | 0 | 39 | 0 | 60 | 0 | 79 | -32 | 122 | 79.44% | 146.9167 | 63.73% | 100% | 79.99% | 5.6 | 127.27 | 712.712 | 19.1619 | 1000.5725 | 19172.92 | 8849.8585 | 130.1667 | 21 | 42 | 0 | 0 | 27 | 1440 | 0 | 592 | 955 | 779 | 363 | 8849.8585 | 32.4583 | 0 | 0 | 14.69 | 20.91 | 16.05 | 50.12 | 0.9369 | 88.23 | 87.35 | 0 | 11494 | 11691 | 7.05
Week 31 | 2019-07-30 | 92.6 | 61.1% | 86.5 | 101 | 84 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3469 | 2853 | 2853 | 2792 | 2880 | 40 | 0 | 40 | 0 | 60 | 0 | 88 | -61 | 122 | 98.36% | 144.5417 | 80.48% | 100% | 86.43% | 5.706 | 130.56 | 744.9754 | 23.3483 | 1010.8016 | 23600.449 | 8719.7079 | 118.875 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 951 | 947 | 982 | -4 | 8719.7079 | 40.9167 | 0 | 0 | 23.26 | 20.76 | 15.53 | 50.14 | 0.9359 | 88.22 | 87.42 | 0 | 11481 | 11720 | 0
| 2019-07-31 | 95.9 | 63.7% | 86.5 | 106 | 87 | 20 | 23 | 24 | 0 | 3 | 37 | 0 | 0 | 0 | 0 | 3442 | 2921 | 2593 | 2538 | 2623 | 39 | 0 | 39 | 0 | 60 | 0 | 85 | -55 | 120 | 91.08% | 143.4167 | 73.74% | 100% | 83.07% | 5.684 | 131.38 | 746.7639 | 21.3749 | 1009.8334 | 21585.119 | 8799.0082 | 121.7083 | 17 | 31 | 0 | 0 | 23 | 1440 | 0 | 793 | 940 | 890 | 147 | 8799.0082 | 37.0833 | 0 | 0 | 19.61 | 20.66 | 15.68 | 50.11 | 0.9358 | 88.23 | 87.47 | 0 | 11550 | 11748 | 5.45
| 2019-08-01 | 90.7 | 71.5% | 86.6 | 100 | 86 | 12 | 49 | 22 | 32 | 10 | 56 | 0 | 0 | 0 | 0 | 3493 | 3134 | 2071 | 2049 | 2128 | 39 | 0 | 39 | 71 | 60 | 102 | 80 | -22 | 121 | 73.28% | 145.5417 | 58.66% | 95.53% | 76.4% | 4.03 | 134.08 | 540.3424 | 17.4019 | 1009.9989 | 17575.91 | 8841.5092 | 130.5833 | 16 | 15 | 18 | 17 | 28 | 1338 | 1 | 515 | 898 | 715 | 383 | 8841.5092 | 29.7917 | 0 | 0 | 12.66 | 19.67 | 15.47 | 50.12 | 0.9347 | 88.28 | 87.43 | 0 | 11516 | 11747 | 0
| 2019-08-02 | 89.6 | 71.3% | 81.3 | 98 | 83 | 17 | 4 | 24 | 0 | 6 | 13 | 0 | 0 | 0 | 0 | 3499 | 3048 | 2439 | 2398 | 2475 | 40 | 0 | 40 | 0 | 60 | 0 | 77 | -41 | 122 | 84.53% | 145.7917 | 68.53% | 100% | 81.67% | 4.687 | 124.44 | 583.2503 | 20.2767 | 1009.6328 | 20472.051 | 8780.3592 | 127 | 22 | 43 | 0 | 0 | 25 | 1440 | 0 | 693 | 947 | 835 | 254 | 8780.3592 | 34.7917 | 0 | 0 | 23.39 | 20.61 | 15.96 | 50.11 | 0.9379 | 88.14 | 87.41 | 0 | 11495 | 11631 | 6
| 2019-08-03 | 90.9 | 71.02% | 86.4 | 97 | 85 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3483 | 2857 | 2857 | 2795 | 2878 | 40 | 0 | 39 | 0 | 60 | 0 | 83 | -62 | 121 | 99.1% | 145.125 | 80.25% | 100% | 86.33% | 4.904 | 124.51 | 610.597 | 23.5055 | 1006.9418 | 23668.67 | 8686.6787 | 119.0417 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 952 | 943 | 983 | -9 | 8686.6787 | 40.9583 | 0 | 0 | 23.39 | 20.77 | 16.08 | 50.11 | 0.938 | 88.18 | 87.46 | 0 | 11538 | 11798 | 0
| 2019-08-04 | 94.46 | 62.68% | 85.05 | 104 | 86 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3454 | 2867 | 2867 | 2801 | 2886 | 40 | 0 | 39 | 0 | 60 | 0 | 85 | -66 | 121 | 99.38% | 143.9167 | 81.09% | 100% | 86.33% | 5.13 | 125.87 | 645.7131 | 23.6106 | 1002.5472 | 23670.75 | 8681.3506 | 119.4583 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 954 | 946 | 986 | -8 | 8681.3506 | 41.0833 | 0 | 0 | 23.51 | 20.86 | 16.03 | 50.15 | 0.9377 | 88.08 | 87.39 | 0 | 11586 | 11820 | 4.8
| 2019-08-05 | 95.9 | 62.69% | 86.1 | 103 | 88 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3442 | 2841 | 2841 | 2772 | 2855 | 39 | 0 | 39 | 0 | 60 | 0 | 83 | -69 | 121 | 98.31% | 143.4167 | 80.53% | 100% | 86.23% | 5 | 125.41 | 627.05 | 23.3867 | 1002.0063 | 23433.6 | 8679.8882 | 118.375 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 942 | 934 | 979 | -8 | 8679.8882 | 40.7917 | 0 | 0 | 23.28 | 20.72 | 15.56 | 50.13 | 0.9379 | 88.12 | 87.46 | 0 | 11607 | 11833 | 0
Week 32 | 2019-08-06 | 97.16 | 64.22% | 87.49 | 106 | 89 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3429 | 2818 | 2818 | 2748 | 2837 | 39 | 0 | 39 | 0 | 60 | 0 | 89 | -70 | 120 | 98.51% | 142.875 | 80.14% | 100% | 86.23% | 5.119 | 134.04 | 686.1508 | 23.1221 | 1008.2241 | 23312.289 | 8733.0567 | 117.4167 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 935 | 930 | 972 | -5 | 8733.0567 | 40.5 | 0 | 0 | 23.01 | 20.43 | 15.73 | 50.13 | 0.9348 | 88.15 | 87.5 | 0 | 11561 | 11774 | 5.2
| 2019-08-07 | 92.5 | 69.7% | 87 | 97 | 87 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3479 | 2845 | 2845 | 2774 | 2859 | 39 | 0 | 39 | 0 | 60 | 0 | 85 | -71 | 121 | 98.45% | 144.9583 | 79.74% | 100% | 86.23% | 4.99 | 128.82 | 642.8118 | 23.3645 | 1008.5515 | 23564.34 | 8726.4426 | 118.5417 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 945 | 936 | 978 | -9 | 8726.4426 | 40.75 | 0 | 0 | 23.18 | 20.59 | 15.73 | 50.15 | 0.9365 | 88.1 | 87.46 | 0 | 11523 | 11779 | 0
| 2019-08-08 | 90.6 | 72.4% | 87.8 | 100 | 87 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3494 | 2852 | 2852 | 2784 | 2869 | 39 | 0 | 39 | 0 | 60 | 0 | 85 | -68 | 121 | 98.79% | 145.5833 | 79.68% | 100% | 86.23% | 4.97 | 132.06 | 656.3382 | 23.5216 | 1006.0068 | 23662.859 | 8735.3438 | 118.8333 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 948 | 939 | 982 | -9 | 8735.3438 | 40.9167 | 0 | 0 | 23.29 | 20.75 | 15.47 | 50.14 | 0.9354 | 88.06 | 87.4 | 0 | 11543 | 11783 | 0
| 2019-08-09 | 89 | 76.4% | 87.4 | 106 | 83 | 16 | 3 | 24 | 0 | 7 | 40 | 0 | 0 | 0 | 0 | 3510 | 3061 | 2366 | 2318 | 2396 | 39 | 0 | 39 | 0 | 60 | 0 | 78 | -48 | 121 | 82.51% | 146.25 | 66.04% | 100% | 81.02% | 5.092 | 128.54 | 654.5257 | 19.7122 | 1003.6798 | 19784.7472 | 8817.6328 | 127.5417 | 16 | 17 | 0 | 0 | 26 | 1440 | 0 | 638 | 941 | 817 | 303 | 8817.6328 | 34.0417 | 0 | 0 | 15.78 | 20.75 | 16.04 | 50.16 | 0.9367 | 88.07 | 87.41 | 0 | 11558 | 11780 | 5.47
| 2019-08-10 | 88.6 | 75.3% | 87.2 | 95 | 83 | 6 | 43 | 22 | 22 | 15 | 46 | 0 | 0 | 0 | 0 | 3512 | 3343 | 1750 | 1670 | 1745 | 39 | 42 | 39 | 79 | 60 | 117 | 75 | -80 | 119 | 61.1% | 146.3333 | 47.55% | 94.09% | 69.49% | 4.752 | 126.19 | 599.6549 | 14.569 | 1001.1939 | 14586.3645 | 9093.4248 | 139.2917 | 19 | 50 | 16 | 19 | 36 | 1323 | 0 | 282 | 891 | 572 | 609 | 9093.4248 | 23.8333 | 0 | 0 | 7.12 | 19.67 | 15.44 | 50.02 | 0.9375 | 87.88 | 87.49 | 0 | 11576 | 11780 | 0
| 2019-08-11 | 90.3 | 72% | 87.7 | 96 | 84 | 11 | 31 | 24 | 0 | 10 | 16 | 0 | 0 | 0 | 0 | 3497 | 3168 | 2090 | 2063 | 2144 | 39 | 68 | 39 | 0 | 60 | 0 | 81 | -27 | 120 | 74.44% | 145.7083 | 58.99% | 98.67% | 76.48% | 4.962 | 128.34 | 636.8231 | 17.8289 | 999.2286 | 17815.1109 | 8944.2239 | 132 | 16 | 56 | 0 | 0 | 30 | 1440 | 0 | 480 | 947 | 717 | 467 | 8944.2239 | 29.875 | 0 | 0 | 12.11 | 20.98 | 15.89 | 50.18 | 0.9368 | 88.37 | 87.36 | 0 | 11616 | 11830 | 5.75
| 2019-08-12 | 94.9 | 68.17% | 86.94 | 104 | 87 | 17 | 15 | 24 | 0 | 6 | 28 | 0 | 0 | 0 | 0 | 3448 | 3037 | 2426 | 2378 | 2462 | 40 | 0 | 40 | 0 | 60 | 0 | 84 | -48 | 121 | 84.78% | 143.6667 | 68.97% | 100% | 82.73% | 4.941 | 130.54 | 644.9981 | 20.2605 | 1000.3805 | 20268.2202 | 8794.4568 | 126.5417 | 15 | 17 | 0 | 0 | 24 | 1440 | 0 | 688 | 942 | 832 | 254 | 8794.4568 | 34.6667 | 0 | 0 | 17.07 | 20.73 | 16.05 | 50.15 | 0.936 | 88.28 | 87.39 | 0 | 11585 | 11799 | 0
Week 33 | 2019-08-13 | 92.66 | 66.13% | 84.35 | 99.7 | 86.7 | 11 | 51 | 24 | 0 | 11 | 12 | 0 | 0 | 0 | 0 | 3474 | 3166 | 2113 | 2085 | 2166 | 40 | 0 | 40 | 0 | 60 | 0 | 81 | -28 | 122 | 73.98% | 144.75 | 60.02% | 100% | 78.01% | 4.902 | 135.94 | 666.3779 | 17.9002 | 1000.7052 | 17912.7943 | 8910.8739 | 131.9167 | 20 | 57 | 0 | 0 | 30 | 1440 | 0 | 490 | 951 | 725 | 461 | 8910.8739 | 30.2083 | 0 | 0 | 12.3 | 20.94 | 16.01 | 50.14 | 0.9345 | 88.12 | 87.24 | 0 | 11555 | 11779 | 5.75
| 2019-08-14 | 93.2 | 63.8% | 79.1 | 101 | 86 | 19 | 16 | 24 | 0 | 4 | 10 | 0 | 0 | 0 | 0 | 3461 | 3016 | 2580 | 2533 | 2611 | 40 | 0 | 40 | 0 | 60 | 0 | 78 | -47 | 122 | 89.17% | 144.2083 | 73.19% | 100% | 83.27% | 4.964 | 132.62 | 658.3257 | 21.5046 | 1000.6005 | 21517.5001 | 8754.7674 | 125.6667 | 18 | 34 | 0 | 0 | 23 | 1440 | 0 | 779 | 947 | 885 | 168 | 8754.7674 | 36.875 | 0 | 0 | 19.19 | 20.93 | 16.1 | 50.15 | 0.9355 | 88.17 | 87.3 | 0 | 11467 | 11817 | 6.27
| 2019-08-15 | 95.2 | 62.4% | 85.2 | 104 | 86 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3449 | 2854 | 2854 | 2781 | 2870 | 40 | 0 | 39 | 0 | 60 | 0 | 89 | -73 | 122 | 98.02% | 143.7083 | 80.63% | 100% | 86.33% | 4.978 | 129.51 | 644.7008 | 23.4419 | 1001.6958 | 23481.6292 | 8675.4153 | 118.9167 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 951 | 938 | 981 | -13 | 8675.4153 | 40.875 | 0 | 0 | 23.38 | 20.73 | 15.28 | 50.11 | 0.9366 | 88.26 | 87.44 | 0 | 11549 | 11798 | 0
| 2019-08-16 | 92.6 | 64.7% | 84.6 | 101 | 83 | 22 | 30 | 24 | 0 | 1 | 17 | 0 | 0 | 0 | 0 | 3470 | 2903 | 2770 | 2712 | 2797 | 40 | 0 | 39 | 0 | 60 | 0 | 85 | -58 | 123 | 94.75% | 144.5833 | 78.16% | 100% | 85.52% | 5.088 | 131.61 | 669.6317 | 22.8417 | 1002.3395 | 22895.119 | 8689.0674 | 120.9583 | 14 | 13 | 0 | 0 | 20 | 1440 | 0 | 900 | 942 | 955 | 42 | 8689.0674 | 39.7917 | 0 | 0 | 22.09 | 20.79 | 14.78 | 50.14 | 0.9358 | 88.22 | 87.39 | 0 | 11518 | 11720 | 6.58
| 2019-08-17 | 88.8 | 70.7% | 85.16 | 98 | 83 | 10 | 5 | 24 | 0 | 13 | 4 | 0 | 0 | 0 | 0 | 3510 | 3195 | 2006 | 1976 | 2052 | 40 | 0 | 39 | 0 | 60 | 0 | 76 | -30 | 123 | 69.51% | 146.25 | 56.3% | 100% | 77.19% | 5.065 | 130.59 | 661.4384 | 16.7579 | 1010.1916 | 16928.689 | 8901.8863 | 133.125 | 20 | 51 | 0 | 0 | 31 | 1440 | 0 | 416 | 946 | 690 | 530 | 8901.8863 | 28.75 | 0 | 0 | 10.37 | 20.8 | 15.03 | 50.1 | 0.9359 | 88.34 | 87.36 | 0 | 11474 | 11708 | 6.1
| 2019-08-18 | 89.3 | 70.3% | 84.62 | 98 | 81 | 8 | 17 | 24 | 0 | 15 | 10 | 0 | 0 | 0 | 0 | 3509 | 3240 | 1891 | 1859 | 1939 | 40 | 0 | 39 | 0 | 60 | 0 | 80 | -32 | 121 | 66.77% | 146.2083 | 52.98% | 100% | 76.67% | 5 | 129.99 | 649.95 | 15.8599 | 1009.1136 | 16004.43 | 8958.7843 | 135 | 19 | 33 | 0 | 0 | 32 | 1440 | 0 | 341 | 949 | 649 | 608 | 8958.7843 | 27.0417 | 0 | 0 | 8.54 | 20.9 | 15.01 | 50.12 | 0.936 | 88.04 | 87.35 | 0 | 11520 | 11695 | 0
| 2019-08-19 | 87.8 | 63.15% | 79.16 | 97 | 78 | 13 | 6 | 24 | 0 | 10 | 10 | 0 | 0 | 0 | 0 | 3517 | 3154 | 2240 | 2200 | 2278 | 40 | 0 | 40 | 0 | 60 | 0 | 78 | -40 | 123 | 77.17% | 146.5417 | 62.55% | 100% | 79.63% | 5.063 | 131.36 | 665.0757 | 18.3482 | 1015.238 | 18627.75 | 8769.4662 | 131.4167 | 17 | 44 | 0 | 0 | 28 | 1440 | 0 | 546 | 966 | 766 | 420 | 8769.4662 | 31.9167 | 0 | 0 | 13.35 | 20.93 | 15.11 | 50.1 | 0.9355 | 87.97 | 87.11 | 0 | 11332 | 11528 | 5.7
Week 34 | 2019-08-20 | 91.6 | 66.8% | 84.6 | 98 | 84 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3484 | 2854 | 2854 | 2805 | 2891 | 40 | 0 | 39 | 0 | 60 | 0 | 86 | -49 | 123 | 97.93% | 145.1667 | 80.51% | 100% | 86.33% | 5.001 | 129.3 | 646.6293 | 23.0104 | 1020.8146 | 23489.311 | 8604.6133 | 118.9167 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 958 | 945 | 988 | -13 | 8631.781 | 41.1667 | 0 | 0 | 23.03 | 20.39 | 15.32 | 50.12 | 0.9371 | 88.11 | 87.25 | 0 | 11290 | 11537 | 5.72
| 2019-08-21 | 93.5 | 64.8% | 84.3 | 102 | 84 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3463 | 2868 | 2868 | 2796 | 2883 | 40 | 0 | 39 | 0 | 60 | 0 | 87 | -72 | 122 | 98.46% | 144.2917 | 80.74% | 100% | 86.33% | 5.017 | 131.15 | 657.9796 | 23.3168 | 1006.847 | 23476.48 | 8631.781 | 119.5 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 953 | 945 | 985 | -8 | 8618.3874 | 41.0417 | 0 | 0 | 23.22 | 20.69 | 15.25 | 50.13 | 0.9357 | 87.99 | 87.17 | 0 | 11435 | 11679 | 0
| 2019-08-22 | 93 | 64.3% | 83.8 | 103 | 85 | 22 | 51 | 24 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 3465 | 2886 | 2799 | 2741 | 2827 | 39 | 0 | 39 | 0 | 60 | 0 | 86 | -58 | 122 | 96.55% | 144.375 | 79.11% | 100% | 85.4% | 5.022 | 132.31 | 664.4608 | 22.9411 | 1000.7619 | 22958.539 | 8618.3874 | 120.25 | 14 | 15 | 0 | 0 | 20 | 1440 | 0 | 914 | 944 | 969 | 30 | 8618.3874 | 40.375 | 0 | 0 | 22.35 | 20.83 | 14.84 | 50.14 | 0.9353 | 87.98 | 87.13 | 0 | 11448 | 11702 | 6.5
| 2019-08-23 | 92 | 60.2% | 80.81 | 101 | 82 | 15 | 10 | 24 | 0 | 8 | 13 | 0 | 0 | 0 | 0 | 3471 | 3067 | 2330 | 2290 | 2372 | 39 | 0 | 39 | 0 | 60 | 0 | 82 | -40 | 121 | 81.68% | 144.625 | 65.98% | 100% | 80.1% | 5.016 | 131.67 | 660.4567 | 19.1948 | 1006.8274 | 19325.84 | 8727.6405 | 127.7917 | 18 | 37 | 0 | 0 | 27 | 1440 | 0 | 619 | 954 | 799 | 335 | 8727.6405 | 33.2917 | 0 | 0 | 15.19 | 20.89 | 15.05 | 50.14 | 0.9356 | 88.07 | 87.08 | 0 | 11426 | 11671 | 5.3
| 2019-08-24 | 93.8 | 63.7% | 84.5 | 103 | 84 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3462 | 2867 | 2867 | 2797 | 2880 | 40 | 0 | 39 | 0 | 60 | 0 | 83 | -70 | 122 | 98.36% | 144.25 | 80.79% | 100% | 86.33% | 5.064 | 134.55 | 681.3612 | 23.2659 | 1007.0845 | 23430.692 | 8620.684 | 119.4583 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 954 | 939 | 987 | -15 | 8620.684 | 41.125 | 0 | 0 | 23.26 | 20.68 | 14.95 | 50.13 | 0.935 | 88.09 | 87.18 | 0 | 11442 | 11718 | 0
| 2019-08-25 | 94.5 | 61.1% | 83.8 | 104 | 85 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3449 | 2867 | 2867 | 2805 | 2888 | 40 | 0 | 40 | 0 | 60 | 0 | 83 | -62 | 123 | 97.83% | 143.7083 | 81.33% | 100% | 86.43% | 5.071 | 132.77 | 673.2767 | 23.2928 | 1007.9725 | 23478.544 | 8610.2747 | 119.4583 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 957 | 942 | 989 | -15 | 8610.2747 | 41.2083 | 0 | 0 | 23.29 | 20.73 | 14.72 | 50.16 | 0.936 | 88.06 | 87.15 | 0 | 11432 | 11694 | 5.83
| 2019-08-26 | 91.96 | 67.4% | 85.2 | 99 | 84 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3476 | 2859 | 2859 | 2795 | 2881 | 40 | 0 | 39 | 0 | 60 | 0 | 86 | -64 | 122 | 98.39% | 144.8333 | 80.41% | 100% | 86.33% | 4.954 | 129.1 | 639.5614 | 23.3049 | 1006.8966 | 23465.584 | 8624.3812 | 119.125 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 954 | 941 | 986 | -13 | 8624.3812 | 41.0833 | 0 | 0 | 23.29 | 20.73 | 14.91 | 50.13 | 0.9364 | 88.1 | 87.3 | 0 | 11472 | 11737 | 5.01
Week 35 | 2019-08-27 | 92.6 | 61.1% | 86.5 | 101 | 84 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3469 | 2853 | 2853 | 2792 | 2880 | 40 | 0 | 40 | 0 | 60 | 0 | 88 | -61 | 122 | 98.36% | 144.5417 | 80.48% | 100% | 86.43% | 5.706 | 130.56 | 744.9754 | 23.3483 | 1010.8016 | 23600.449 | 8719.7079 | 118.875 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 951 | 947 | 982 | -4 | 8719.7079 | 40.9167 | 0 | 0 | 23.26 | 20.76 | 15.53 | 50.14 | 0.9359 | 88.22 | 87.42 | 0 | 11481 | 11720 | 0
| 2019-08-28 | 95.9 | 63.7% | 86.5 | 106 | 87 | 20 | 23 | 24 | 0 | 3 | 37 | 0 | 0 | 0 | 0 | 3442 | 2921 | 2593 | 2538 | 2623 | 39 | 0 | 39 | 0 | 60 | 0 | 85 | -55 | 120 | 91.08% | 143.4167 | 73.74% | 100% | 83.07% | 5.684 | 131.38 | 746.7639 | 21.3749 | 1009.8334 | 21585.119 | 8799.0082 | 121.7083 | 17 | 31 | 0 | 0 | 23 | 1440 | 0 | 793 | 940 | 890 | 147 | 8799.0082 | 37.0833 | 0 | 0 | 19.61 | 20.66 | 15.68 | 50.11 | 0.9358 | 88.23 | 87.47 | 0 | 11550 | 11748 | 5.45
| 2019-08-29 | 90.7 | 71.5% | 86.6 | 100 | 86 | 12 | 49 | 22 | 32 | 10 | 56 | 0 | 0 | 0 | 0 | 3493 | 3134 | 2071 | 2049 | 2128 | 39 | 0 | 39 | 71 | 60 | 102 | 80 | -22 | 121 | 73.28% | 145.5417 | 58.66% | 95.53% | 76.4% | 4.03 | 134.08 | 540.3424 | 17.4019 | 1009.9989 | 17575.91 | 8841.5092 | 130.5833 | 16 | 15 | 18 | 17 | 28 | 1338 | 1 | 515 | 898 | 715 | 383 | 8841.5092 | 29.7917 | 0 | 0 | 12.66 | 19.67 | 15.47 | 50.12 | 0.9347 | 88.28 | 87.43 | 0 | 11516 | 11747 | 0
| 2019-08-30 | 89.6 | 71.3% | 81.3 | 98 | 83 | 17 | 4 | 24 | 0 | 6 | 13 | 0 | 0 | 0 | 0 | 3499 | 3048 | 2439 | 2398 | 2475 | 40 | 0 | 40 | 0 | 60 | 0 | 77 | -41 | 122 | 84.53% | 145.7917 | 68.53% | 100% | 81.67% | 4.687 | 124.44 | 583.2503 | 20.2767 | 1009.6328 | 20472.051 | 8780.3592 | 127 | 22 | 43 | 0 | 0 | 25 | 1440 | 0 | 693 | 947 | 835 | 254 | 8780.3592 | 34.7917 | 0 | 0 | 23.39 | 20.61 | 15.96 | 50.11 | 0.9379 | 88.14 | 87.41 | 0 | 11495 | 11631 | 6
| 2019-08-31 | 90.9 | 71.02% | 86.4 | 97 | 85 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3483 | 2857 | 2857 | 2795 | 2878 | 40 | 0 | 39 | 0 | 60 | 0 | 83 | -62 | 121 | 99.1% | 145.125 | 80.25% | 100% | 86.33% | 4.891 | 124.51 | 608.9784 | 23.5055 | 1006.9418 | 23668.67 | 8686.0996 | 119.0417 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 952 | 943 | 983 | -9 | 8686.0996 | 40.9583 | 0 | 0 | 23.39 | 20.77 | 16.08 | 50.11 | 0.938 | 88.18 | 87.46 | 0 | 11538 | 11798 | 0
| 2019-09-01 | 90 | 70.3% | 85.8 | 99 | 84 | 20 | 3 | 22 | 32 | 2 | 3 | 0 | 0 | 0 | 0 | 3496 | 2908 | 2510 | 2460 | 2542 | 40 | 116 | 40 | 70 | 60 | 103 | 84 | -50 | 120 | 88.26% | 145.6667 | 70.37% | 93.24% | 78.47% | 4.39 | 136.66 | 599.9374 | 20.6432 | 1007.7026 | 20802.192 | 8700.0526 | 121.1667 | 0 | 0 | 21 | 18 | 22 | 1337 | 2 | 789 | 891 | 862 | 102 | 8700.0526 | 35.9167 | 0 | 0 | 19.31 | 19.64 | 13.3 | 50.14 | 0.9337 | 87.79 | 87.16 | 0 | 11462 | 11564 | 5
| 2019-09-02 | 90.1 | 71% | 86.5 | 97 | 82 | 0 | 0 | 24 | 0 | 7 | 13 | 0 | 0 | 0 | 0 | 3497 | 2202 | 1581 | 1558 | 1636 | 40 | 690 | 40 | 0 | 60 | 0 | 78 | -23 | 110 | 61.97% | 145.7083 | 44.55% | 86.31% | 58.31% | 4.805 | 139.66 | 671.0663 | 13.6121 | 1007.7026 | 13716.9659 | 9234.9372 | 91.75 | 10 | 317 | 0 | 0 | 37 | 1440 | 0 | 159 | 940 | 537 | 781 | 9234.9372 | 22.375 | 0 | 0 | 4.39 | 20.56 | 13.54 | 50.11 | 0.9328 | 88.35 | 87.22 | 0 | 12076 | 11541 | 2.13
Week 36 | 2019-09-03 | 93.96 | 67.07% | 87.18 | 103 | 85 | 11 | 4 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3457 | 2401 | 2401 | 2341 | 2426 | 39 | 305 | 39 | 0 | 60 | 0 | 85 | -60 | 121 | 83.54% | 144.0417 | 67.72% | 94.01% | 73.28% | 4.85 | 133.12 | 645.632 | 20.0226 | 1007.7026 | 20176.8751 | 8894.7062 | 100.0417 | 8 | 471 | 0 | 0 | 26 | 1440 | 0 | 674 | 930 | 822 | 256 | 8894.7062 | 34.25 | 0 | 0 | 17.12 | 20.5 | 13.56 | 50.09 | 0.9351 | 88.03 | 87.21 | 0 | 11577 | 11663 | 6
| 2019-09-04 | 95.7 | 65% | 87.1 | 105 | 87 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3441 | 2821 | 2821 | 2748 | 2833 | 39 | 0 | 39 | 0 | 60 | 0 | 85 | -73 | 120 | 98.37% | 143.375 | 79.86% | 100% | 86.23% | 4.399 | 133.58 | 587.6184 | 23.1154 | 1007.7026 | 23293.4698 | 8690.3523 | 117.5417 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 936 | 924 | 973 | -12 | 8690.3523 | 40.5417 | 0 | 0 | 23.09 | 20.5 | 13.27 | 50.14 | 0.9351 | 88.04 | 87.09 | 0 | 11586 | 11671 | 5.9
| 2019-09-05 | 96 | 63.9% | 87.3 | 105 | 88 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3439 | 2817 | 2817 | 2743 | 2832 | 40 | 0 | 39 | 0 | 60 | 0 | 89 | -74 | 120 | 98.33% | 143.2917 | 79.76% | 100% | 86.33% | 3.816 | 133.52 | 509.5123 | 23.0424 | 1007.6717 | 23219.1775 | 8650.6343 | 117.375 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 934 | 927 | 971 | -7 | 8650.6343 | 40.4583 | 0 | 0 | 23.03 | 20.49 | 13.23 | 50.14 | 0.9352 | 87.98 | 86.64 | 0 | 11574 | 11680 | 4.9
| 2019-09-06 | 94 | 68.9% | 88.3 | 102 | 87 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3462 | 2809 | 2809 | 2740 | 2827 | 39 | 0 | 39 | 0 | 60 | 0 | 87 | -69 | 120 | 98.16% | 144.25 | 79.15% | 100% | 85.51% | 4.151 | 131.9 | 547.5169 | 22.9379 | 1011.0299 | 23190.9117 | 8663.6601 | 117.0417 | 0 | 0 | 0 | 0 | 20 | 1440 | 0 | 934 | 924 | 969 | -10 | 8663.6601 | 40.375 | 0 | 0 | 22.98 | 20.39 | 13.26 | 50.16 | 0.9355 | 88.1 | 86.53 | 0 | 11552 | 11651 | 0.75
| 2019-09-07 | 92.07 | 71.3% | 88.7 | 98 | 86 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3476 | 2814 | 2814 | 2750 | 2834 | 39 | 0 | 39 | 0 | 60 | 0 | 84 | -64 | 120 | 98.4% | 144.8333 | 79.11% | 100% | 86.23% | 4.117 | 137.52 | 566.1698 | 23.187 | 1004.6305 | 23294.3312 | 8676.5458 | 117.25 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 936 | 927 | 971 | -9 | 8676.5458 | 40.4583 | 0 | 0 | 23.11 | 20.45 | 13.37 | 50.16 | 0.9337 | 87.98 | 86.46 | 0 | 11587 | 11636 | 5.99
| 2019-09-08 | 93.11 | 68.09% | 87.13 | 101 | 86 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3463 | 2828 | 2828 | 2758 | 2844 | 39 | 0 | 39 | 0 | 60 | 0 | 86 | -70 | 119 | 99.58% | 144.2917 | 79.64% | 100% | 86.23% | 4.099 | 136.64 | 560.0874 | 23.2774 | 1003.0081 | 23347.4493 | 8668.4324 | 117.8333 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 939 | 929 | 976 | -10 | 8668.4324 | 40.6667 | 0 | 0 | 23.19 | 20.63 | 13.42 | 50.15 | 0.9341 | 87.94 | 86.36 | 0 | 11597 | 11703 | 2.01
| 2019-09-09 | 94.9 | 64.8% | 86.6 | 105 | 86 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3451 | 2822 | 2822 | 2750 | 2838 | 39 | 0 | 39 | 0 | 60 | 0 | 88 | -72 | 120 | 98.54% | 143.7917 | 79.69% | 100% | 86.23% | 4.045 | 135.49 | 548.0571 | 23.3633 | 994.6925 | 23239.3326 | 8649.9599 | 117.5833 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 935 | 928 | 975 | -7 | 8649.9599 | 40.625 | 0 | 0 | 23.35 | 20.72 | 13.23 | 50.13 | 0.9344 | 87.7 | 86.26 | 0 | 11719 | 11774 | 3.45
Week 37 | 2019-09-10 | 94.6 | 63.6% | 85.7 | 104 | 87 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3453 | 2826 | 2826 | 2756 | 2840 | 39 | 0 | 39 | 0 | 60 | 0 | 84 | -70 | 121 | 97.8% | 143.875 | 79.81% | 100% | 86.23% | 4.05 | 133.36 | 540.108 | 23.3727 | 994.994 | 23255.7124 | 8634.1874 | 117.75 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 939 | 925 | 976 | -14 | 8634.1874 | 40.6667 | 0 | 0 | 23.35 | 20.6 | 12.63 | 50.12 | 0.9352 | 87.74 | 86.67 | 0 | 11687 | 11711 | 5.65
| 2019-09-11 | 93.43 | 65.15% | 85.64 | 102 | 85 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3458 | 2838 | 2838 | 2759 | 2842 | 39 | 0 | 38 | 0 | 60 | 0 | 83 | -79 | 121 | 97.87% | 144.0833 | 79.79% | 100% | 86.13% | 4.129 | 138.06 | 570.0497 | 23.3146 | 998.799 | 23286.6219 | 8646.8545 | 118.25 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 939 | 927 | 976 | -12 | 8646.8545 | 40.6667 | 0 | 0 | 23.24 | 20.3 | 12.4 | 50.1 | 0.9333 | 87.53 | 86.74 | 0 | 11617 | 11553 | 0
| 2019-09-12 | 93.3 | 66.2% | 86 | 102 | 85 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3465 | 2841 | 2841 | 2765 | 2852 | 39 | 0 | 39 | 0 | 60 | 0 | 87 | -76 | 124 | 95.83% | 144.375 | 79.8% | 100% | 86.23% | 4.1 | 137.51 | 563.791 | 23.2967 | 1006.2672 | 23442.6738 | 8682.2657 | 118.375 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 939 | 926 | 987 | -13 | 8682.2657 | 41.125 | 0.095 | 0 | 23.21 | 20.3 | 11.95 | 50.12 | 0.9336 | 87.61 | 86.89 | 0.095 | 11586 | 11508 | 5.5
| 2019-09-13 | 92.8 | 65.7% | 84.9 | 104 | 84 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3467 | 2845 | 2845 | 2775 | 2862 | 39 | 0 | 39 | 0 | 60 | 0 | 87 | -70 | 121 | 98.55% | 144.4583 | 80.04% | 100% | 86.23% | 4.091 | 138.58 | 566.9308 | 23.373 | 1001.6687 | 23411.9886 | 8641.052 | 118.5417 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 944 | 935 | 983 | -9 | 8641.052 | 40.9583 | 0 | 0 | 23.36 | 20.47 | 12.13 | 50.13 | 0.9332 | 87.57 | 86.99 | 0 | 11617 | 11501 | 0.25
| 2019-09-14 | 91.8 | 63.5% | 82.8 | 102 | 82 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3477 | 2865 | 2865 | 2805 | 2892 | 40 | 0 | 40 | 0 | 60 | 0 | 87 | -60 | 123 | 97.97% | 144.875 | 80.67% | 100% | 86.43% | 4.108 | 137.08 | 563.1246 | 23.5711 | 1001.3576 | 23603.1132 | 8615.4145 | 119.375 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 956 | 944 | 992 | -12 | 8615.4145 | 41.3333 | 0 | 0 | 23.58 | 20.57 | 12.07 | 50.11 | 0.9338 | 87.74 | 86.92 | 0 | 11583 | 11457 | 5.37
| 2019-09-15 | 92.4 | 66.5% | 84.8 | 104 | 84 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3473 | 2842 | 2842 | 2775 | 2858 | 39 | 0 | 39 | 0 | 60 | 0 | 83 | -67 | 121 | 98.42% | 144.7083 | 79.9% | 100% | 86.23% | 4.029 | 142.13 | 572.6418 | 23.3701 | 1002.439 | 23427.0847 | 8648.5501 | 118.4167 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 944 | 930 | 984 | -14 | 8648.5501 | 41 | 0 | 0 | 23.37 | 20.42 | 12.02 | 50.08 | 0.9322 | 87.83 | 87 | 0 | 11599 | 11508 | 5.5
| 2019-09-16 | 93.2 | 63.5% | 84 | 102 | 83 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3469 | 2849 | 2849 | 2785 | 2870 | 40 | 0 | 39 | 0 | 60 | 0 | 85 | -64 | 122 | 98.02% | 144.5417 | 80.28% | 100% | 86.33% | 4.002 | 144.42 | 577.9688 | 23.6415 | 994.8889 | 23520.6762 | 8653.0144 | 118.7083 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 948 | 935 | 987 | -13 | 8653.0144 | 41.125 | 0 | 0 | 23.59 | 20.65 | 12.02 | 50.1 | 0.9311 | 87.75 | 87.06 | 0 | 11681 | 11593 | 0.45
Week 38 | 2019-09-17 | 91.4 | 65.9% | 84 | 103 | 83 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3483 | 2861 | 2861 | 2793 | 2882 | 40 | 0 | 39 | 0 | 60 | 0 | 89 | -68 | 122 | 98.43% | 145.125 | 80.19% | 100% | 86.33% | 3.925 | 135.54 | 531.9945 | 23.7698 | 992.4874 | 23591.225 | 8637.0281 | 119.2083 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 952 | 942 | 988 | -10 | 8643.6421 | 41.1667 | 0 | 0 | 23.61 | 20.78 | 11.91 | 50.13 | 0.9341 | 87.59 | 87.07 | 0 | 11658 | 11561 | 5.9
| 2019-09-18 | 92 | 63.9% | 83.3 | 105 | 82 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3478 | 2866 | 2866 | 2798 | 2882 | 40 | 0 | 39 | 0 | 60 | 0 | 84 | -68 | 123 | 97.63% | 144.9167 | 80.45% | 100% | 86.33% | 3.9 | 142.42 | 555.438 | 23.7626 | 994.3971 | 23629.4727 | 8643.6421 | 119.4167 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 952 | 939 | 991 | -13 | 8649.1871 | 41.2917 | 0 | 0 | 23.61 | 20.77 | 11.72 | 50.1 | 0.9319 | 87.64 | 87.03 | 0 | 11650 | 11579 | 0
| 2019-09-19 | 89.63 | 70.1% | 84.8 | 99.8 | 82.8 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3503 | 2860 | 2860 | 2801 | 2885 | 40 | 0 | 39 | 0 | 60 | 0 | 84 | -59 | 122 | 98.53% | 145.9583 | 79.96% | 100% | 86.33% | 3.904 | 145.2 | 566.8608 | 23.6846 | 998.9401 | 23659.5123 | 8649.1871 | 119.1667 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 950 | 944 | 991 | -6 | 8649.1871 | 41.2917 | 0 | 0 | 23.54 | 20.66 | 12.15 | 50.12 | 0.9308 | 87.56 | 87.25 | 0 | 11625 | 11488 | 5.58
| 2019-09-20 | 87.15 | 71.1% | 82.75 | 95.86 | 80.4 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3529 | 2884 | 2884 | 2827 | 2912 | 40 | 0 | 40 | 0 | 60 | 0 | 85 | -57 | 123 | 98.64% | 147.0417 | 80.11% | 100% | 87.14% | 3.88 | 141.31 | 548.2828 | 23.823 | 1000.6381 | 23838.2342 | 8626.2883 | 120.1667 | 0 | 0 | 0 | 0 | 18 | 1440 | 0 | 961 | 951 | 1000 | -10 | 8626.2883 | 41.6667 | 0 | 0 | 23.74 | 20.84 | 12 | 50.1 | 0.932 | 87.62 | 87.4 | 0 | 11598 | 11482 | 0
| 2019-09-21 | 87.88 | 67.62% | 81.8 | 96.65 | 80.4 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3520 | 2898 | 2898 | 2834 | 2915 | 40 | 0 | 40 | 0 | 60 | 0 | 81 | -64 | 123 | 98.75% | 146.6667 | 80.51% | 100% | 87.14% | 3.883 | 141.99 | 551.3472 | 23.8281 | 1002.4618 | 23886.7535 | 8623.183 | 120.75 | 0 | 0 | 0 | 0 | 18 | 1440 | 0 | 962 | 953 | 1000 | -9 | 8623.183 | 41.6667 | 0 | 0 | 23.75 | 20.84 | 11.9 | 50.1 | 0.9321 | 87.56 | 87.33 | 0 | 11586 | 11455 | 5.75
| 2019-09-22 | 88.64 | 65% | 81 | 99 | 81 | 16 | 5 | 24 | 0 | 7 | 21 | 0 | 0 | 0 | 0 | 3511 | 3054 | 2400 | 2363 | 2445 | 40 | 0 | 40 | 0 | 60 | 0 | 82 | -37 | 122 | 83.5% | 146.2917 | 67.3% | 100% | 81.91% | 3.648 | 143.74 | 524.3635 | 20.128 | 1002.25 | 20173.2547 | 8759.0428 | 127.25 | 14 | 34 | 0 | 0 | 25 | 1440 | 0 | 658 | 956 | 831 | 298 | 8759.0428 | 34.625 | 0 | 0 | 16.38 | 20.8 | 11.58 | 50.1 | 0.9313 | 87.51 | 87.29 | 0 | 11563 | 11384 | 5.3
| 2019-09-23 | 87.93 | 66.11% | 80.8 | 99 | 79 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3522 | 2904 | 2904 | 2839 | 2922 | 40 | 0 | 40 | 0 | 60 | 0 | 83 | -65 | 123 | 98.98% | 146.75 | 80.61% | 100% | 86.43% | 3.739 | 142.32 | 532.1345 | 24.0138 | 1001.3344 | 24045.844 | 8657.2661 | 121 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 965 | 956 | 1001 | -9 | 8657.2661 | 41.7083 | 0 | 0 | 23.81 | 20.94 | 11.49 | 50.09 | 0.9318 | 87.48 | 87.29 | 0 | 11589 | 11429 | 0
Week 39 | 2019-09-24 | 87.5 | 67.5% | 81.1 | 99 | 80 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 3523 | 3108 | 3108 | 3039 | 3132 | 39 | 0 | 40 | 0 | 59 | 0 | 93 | -69 | 139 | 93.88% | 146.7917 | 86.26% | 100% | 93.48% | 3.814 | 144.56 | 551.3518 | 26.2462 | 999.9368 | 26244.57 | 8817.3484 | 129.5 | 0 | 0 | 0 | 0 | 18 | 720 | 0 | 961 | 956 | 1215 | -5 | 8817.3484 | 50.625 | 1.181 | 1.149 | 23.72 | 20.89 | 11.42 | 50.07 | 0.931 | 87.36 | 87.26 | 2.33 | 11590 | 11432 | 6
| 2019-09-25 | 88.4 | 66.5% | 81.5 | 97 | 81 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 3518 | 3106 | 3106 | 3040 | 3128 | 40 | 0 | 40 | 0 | 60 | 0 | 88 | -66 | 140 | 93.1% | 146.5833 | 86.41% | 100% | 93.57% | 3.79 | 147.91 | 560.5789 | 26.1509 | 1002.9567 | 26228.26 | 8812.1181 | 129.4167 | 0 | 0 | 0 | 0 | 18 | 720 | 0 | 959 | 952 | 1217 | -7 | 8812.1181 | 50.7083 | 1.171 | 1.112 | 23.63 | 20.82 | 11.23 | 50.03 | 0.9299 | 87.48 | 87.24 | 2.283 | 11571 | 11401 | 5.58
| 2019-09-26 | 88.6 | 66.9% | 81.7 | 99 | 81 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3515 | 2906 | 2906 | 2828 | 2910 | 40 | 0 | 40 | 0 | 60 | 0 | 82 | -78 | 123 | 98.58% | 146.4583 | 80.46% | 100% | 86.43% | 3.798 | 141.54 | 537.5689 | 23.8291 | 1005.1747 | 23952.359 | 8659.8048 | 121.0833 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 961 | 951 | 998 | -10 | 8659.8048 | 41.5833 | 0 | 0 | 23.68 | 20.87 | 11.34 | 50.1 | 0.9322 | 87.49 | 87.03 | 0 | 11566 | 11442 | 1
| 2019-09-27 | 89.58 | 65.44% | 81.7 | 100 | 81 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3502 | 2881 | 2881 | 2820 | 2905 | 40 | 0 | 39 | 0 | 60 | 0 | 85 | -61 | 123 | 98.41% | 145.9167 | 80.53% | 100% | 86.33% | 3.738 | 143.37 | 535.9171 | 23.5956 | 1009.9125 | 23829.461 | 8640.205 | 120.0417 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 959 | 950 | 996 | -9 | 8640.205 | 41.5 | 0 | 0 | 23.4 | 20.61 | 11.25 | 50.12 | 0.9314 | 87.44 | 86.97 | 0 | 11475 | 11333 | 5.1
| 2019-09-28 | 88.7 | 67.1% | 82.1 | 103 | 82 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 3510 | 3083 | 3083 | 3015 | 3103 | 40 | 0 | 40 | 0 | 60 | 0 | 88 | -68 | 143 | 90.41% | 146.25 | 85.9% | 100% | 92.5% | 3.69 | 147.63 | 544.7547 | 25.7967 | 1008.3108 | 26011.07 | 8807.9021 | 128.4583 | 0 | 0 | 0 | 0 | 18 | 840 | 0 | 954 | 949 | 1200 | -5 | 8807.9021 | 50 | 1.053 | 1.053 | 23.39 | 20.53 | 11.15 | 50.1 | 0.9299 | 87.4 | 86.91 | 2.106 | 11507 | 11303 | 5.45
| 2019-09-29 | 80.1 | 76.7% | 73.1 | 89 | 69 | 24 | 0 | 4 | 36 | 0 | 0 | 19 | 3 | 0 | 0 | 3597 | 3177 | 1692 | 1687 | 1753 | 40 | 0 | 40 | 0 | 60 | 0 | 66 | -5 | 124 | 58.9% | 149.875 | 46.9% | 100% | 74.15% | 0.501 | 145.39 | 72.8404 | 14.7901 | 1010.4239 | 14944.29 | 8901.6778 | 132.375 | 0 | 0 | 13 | 21 | 36 | 1440 | 0 | 982 | 192 | 579 | -790 | 8901.6778 | 24.125 | 0 | 0 | 23.83 | 20.89 | 11.77 | 50.12 | 0.9302 | 87.22 | 86.87 | 0 | 11394 | 11183 | 0
| 2019-09-30 | 83 | 74.6% | 81.32 | 93 | 77 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 3568 | 3488 | 1386 | 1377 | 1449 | 40 | 0 | 40 | 0 | 60 | 0 | 72 | -9 | 62 | 97.38% | 148.6667 | 38.59% | 100% | 71.43% | 0 | 0 | 0 | 12.328 | 1014.8808 | 12511.43 | 9086.0058 | 145.3333 | 0 | 0 | 0 | 0 | 40 | 1440 | 0 | 978 | 0 | 471 | -978 | 9086.0058 | 19.625 | 0 | 0 | 23.66 | 0 | 0 | 50.1 | 0 | 87.31 | 0 | 0 | 11412 | 0 | 5.5
Week 40 | 2019-10-01 | 84.1 | 72% | 81.3 | 92 | 78 | 17 | 55 | 0 | 0 | 5 | 52 | 24 | 0 | 0 | 0 | 3557 | 3492 | 1045 | 1024.42 | 1076 | 40 | 0 | 40 | 0 | 60 | 0 | 57.58 | -20.58 | 61 | 73.5% | 148.2083 | 28.8% | 100% | 78.36% | 0 | 0 | 0 | 9.359 | 1008.12 | 9434.9951 | 9210.0848 | 145.5 | 14 | 13 | 0 | 0 | 40 | 1086 | 6 | 724 | 0 | 352 | -724 | 9210.0848 | 14.6667 | 0 | 0 | 23.71 | 0 | 0 | 50.09 | 0 | 87.28 | 0 | 0 | 11449 | 0 | 0
| 2019-10-02 | 83.5 | 69% | 78.9 | 93.9 | 75.9 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3562 | 3512 | 0 | 0 | 0 | 40 | 0 | 40 | 0 | 60 | 0 | 16 | 0 | 0 | no data | 148.4167 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 146.3333 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 50.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-10-03 | 82.34 | 66.29% | 76.1 | 94.97 | 72.76 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3547 | 3511 | 0 | 0 | 0 | 40 | 0 | 40 | 0 | 60 | 0 | 14 | 0 | 0 | no data | 147.7917 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 146.2917 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-10-04 | 79.02 | 68.8% | 74.64 | 89 | 72 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3597 | 3521 | 0 | 0 | 0 | 40 | 0 | 40 | 0 | 60 | 0 | 11 | 0 | 0 | no data | 149.875 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 146.7083 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 50.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-10-05 | 81 | 67.1% | 75.3 | 92 | 73 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3588 | 3521 | 0 | 0 | 0 | 40 | 0 | 40 | 0 | 60 | 0 | 9 | 0 | 0 | no data | 149.5 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 146.7083 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 50.09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1
| 2019-10-06 | 73.4 | 76.6% | 73.3 | 79 | 70 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3652 | 3525 | 0 | 0 | 0 | 40 | 0 | 40 | 0 | 60 | 0 | 8 | 0 | 0 | no data | 152.1667 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 146.875 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 50.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-10-07 | 76.4 | 70% | 71.1 | 94 | 67.4 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3632 | 3528 | 0 | 0 | 0 | 40 | 0 | 40 | 0 | 60 | 0 | 10 | 0 | 0 | no data | 151.3333 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 147 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 50.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Week 41 | 2019-10-08 | 79.6 | 63.2% | 66.9 | 96.7 | 68.8 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3610 | 3528 | 0 | 0 | 0 | 40 | 0 | 40 | 0 | 60 | 0 | 8 | 0 | 0 | no data | 150.4167 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 147 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 50.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-10-09 | 81.3 | 62.9% | 68.3 | 93 | 71 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3578 | 3532 | 0 | 0 | 0 | 40 | 0 | 40 | 0 | 60 | 0 | 9 | 0 | 0 | no data | 149.0833 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 147.1667 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 50.11 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2
| 2019-10-10 | 81.4 | 61.8% | 72.95 | 97 | 71 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3580 | 3533 | 0 | 0 | 0 | 40 | 0 | 40 | 0 | 60 | 0 | 7 | 0 | 0 | no data | 149.1667 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 147.2083 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-10-11 | 82.4 | 63% | 77.6 | 98 | 73 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3566 | 3533 | 0 | 0 | 0 | 40 | 0 | 40 | 0 | 60 | 0 | 6 | 0 | 0 | no data | 148.5833 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 147.2083 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-10-12 | 83.1 | 62.7% | 75.1 | 96 | 73 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3566 | 3534 | 0 | 0 | 0 | 40 | 0 | 40 | 0 | 60 | 0 | 6 | 0 | 0 | no data | 148.5833 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 147.25 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5
| 2019-10-13 | 82.89 | 64.84% | 75.64 | 94 | 73.5 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3567 | 3535 | 0 | 0 | 0 | 40 | 0 | 40 | 0 | 60 | 0 | 7 | 0 | 0 | no data | 148.625 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 147.2917 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-10-14 | 82 | 63.4% | 73.7 | 96 | 73 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3576 | 3531 | 0 | 0 | 0 | 40 | 0 | 40 | 0 | 60 | 0 | 8 | 0 | 0 | no data | 149 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 147.125 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Week 42 | 2019-10-15 | 82.17 | 59.02% | 72.27 | 96.4 | 71.65 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3572 | 3531 | 0 | 0 | 0 | 40 | 0 | 40 | 0 | 60 | 0 | 6 | 0 | 0 | no data | 148.8333 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 147.125 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-10-16 | 82 | 59% | 71.8 | 94 | 72 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3575 | 3531 | 0 | 0 | 0 | 40 | 0 | 40 | 0 | 60 | 0 | 8 | 0 | 0 | no data | 148.9583 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 147.125 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-10-17 | 82 | 63.6% | 73.8 | 94 | 73 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3579 | 3534 | 0 | 0 | 0 | 40 | 0 | 40 | 0 | 60 | 0 | 6 | 0 | 0 | no data | 149.125 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 147.25 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-10-18 | 76.6 | 61.9% | 68.7 | 85 | 70 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3628 | 3534 | 0 | 0 | 0 | 40 | 0 | 40 | 0 | 60 | 0 | 6 | 0 | 0 | no data | 151.1667 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 147.25 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-10-19 | 75.3 | 63.4% | 68.4 | 89 | 66 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3638 | 3539 | 0 | 0 | 0 | 40 | 0 | 40 | 0 | 60 | 0 | 5 | 0 | 0 | no data | 151.5833 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 147.4583 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1
| 2019-10-20 | 77 | 61.4% | 68.9 | 90 | 67 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3625 | 3542 | 0 | 0 | 0 | 40 | 0 | 40 | 0 | 60 | 0 | 5 | 0 | 0 | no data | 151.0417 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 147.5833 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-10-21 | 77.5 | 61.8% | 69.8 | 91 | 67 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3623 | 3546 | 0 | 0 | 0 | 40 | 0 | 40 | 0 | 60 | 0 | 7 | 0 | 0 | no data | 150.9583 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 147.75 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Week 43 | 2019-10-22 | 77.93 | 61.42% | 69.69 | 93.26 | 67.89 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3615 | 3550 | 0 | 0 | 0 | 40 | 0 | 40 | 0 | 60 | 0 | 5 | 0 | 0 | no data | 150.625 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 147.9167 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-10-23 | 78.5 | 57.98% | 67.98 | 91 | 69 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3612 | 3554 | 0 | 0 | 0 | 40 | 0 | 40 | 0 | 60 | 0 | 6 | 0 | 0 | no data | 150.5 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 148.0833 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 2
| 2019-10-24 | 78.7 | 62.4% | 70.4 | 90 | 70 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3605 | 3557 | 0 | 0 | 0 | 40 | 0 | 40 | 0 | 60 | 0 | 5 | 0 | 0 | no data | 150.2083 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 148.2083 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-10-25 | 78.5 | 62.5% | 70.8 | 90 | 70 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3608 | 3557 | 0 | 0 | 0 | 40 | 0 | 40 | 0 | 60 | 0 | 5 | 0 | 0 | no data | 150.3333 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 148.2083 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-10-26 | 77.9 | 63.5% | 70.5 | 90 | 68 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3616 | 3559 | 0 | 0 | 0 | 40 | 0 | 40 | 0 | 60 | 0 | 6 | 0 | 0 | no data | 150.6667 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 148.2917 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-10-27 | 76.7 | 65.9% | 70.7 | 88 | 69 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3625 | 3560 | 0 | 0 | 0 | 40 | 0 | 40 | 0 | 60 | 0 | 5 | 0 | 0 | no data | 151.0417 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 148.3333 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-10-28 | 76.9 | 63.7% | 69.7 | 92 | 66 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3626 | 3561 | 0 | 0 | 0 | 40 | 0 | 40 | 0 | 60 | 0 | 6 | 0 | 0 | no data | 151.0833 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 148.375 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Week 44 | 2019-10-29 | 75.7 | 64.8% | 69.1 | 88 | 70 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3638 | 3588 | 0 | 0 | 0 | 40 | 0 | 40 | 0 | 60 | 0 | 4 | 0 | 0 | no data | 151.5833 | no data | 100% | no data | 0 | 0 | 0 |  |  |  | no data | 149.5 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-10-30 | 75.6 | 67.6% | 70.2 | 84 | 68 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3642 | 3592 | 0 | 0 | 0 | 40 | 0 | 40 | 0 | 60 | 0 | 5 | 0 | 0 | no data | 151.75 | no data | 100% | no data | 0 | 0 | 0 |  |  |  | no data | 149.6667 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-10-31 | 78 | 57.8% | 66.42 | 94 | 67 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3614 | 3569 | 0 | 0 | 0 | 40 | 0 | 40 | 0 | 60 | 0 | 5 | 0 | 0 | no data | 150.5833 | no data | 100% | no data | 0 | 0 | 0 |  |  |  | no data | 148.7083 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-11-01 | 75.7 | 64.8% | 69.04 | 88 | 70 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3638 | 3588 | 0 | 0 | 0 | 40 | 0 | 40 | 0 | 60 | 0 | 4 | 0 | 0 | no data | 151.5833 | no data | 100% | no data | 0 | 0 | 0 |  |  |  | no data | 149.5 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-11-02 | 75.6 | 67.4% | 69.96 | 84 | 68 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3642 | 3592 | 0 | 0 | 0 | 40 | 0 | 40 | 0 | 60 | 0 | 5 | 0 | 0 | no data | 151.75 | no data | 100% | no data | 0 | 0 | 0 |  |  |  | no data | 149.6667 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-11-03 | 76.14 | 61.9% | 68.32 | 90 | 67 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3631 | 3593 | 0 | 0 | 0 | 40 | 0 | 40 | 0 | 60 | 0 | 5 | 0 | 0 | no data | 151.2917 | no data | 100% | no data | 0 | 0 | 0 |  |  |  | no data | 149.7083 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-11-04 | 75.9 | 64.5% | 69.4 | 89 | 66 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3635 | 3592 | 0 | 0 | 0 | 40 | 0 | 40 | 0 | 60 | 0 | 4 | 0 | 0 | no data | 151.4583 | no data | 100% | no data | 0 | 0 | 0 |  |  |  | no data | 149.6667 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
Week 45 | 2019-11-05 | 75.4 | 61% | 67.5 | 92 | 65 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3639 | 3594 | 0 | 0 | 0 | 40 | 0 | 40 | 0 | 60 | 0 | 5 | 0 | 0 | no data | 151.625 | no data | 100% | no data | 0 | 0 | 0 |  |  |  | no data | 149.75 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-11-06 | 73.1 | 58.1% | 64.3 | 87 | 64.6 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3662 | 3599 | 0 | 0 | 0 | 40 | 0 | 40 | 0 | 60 | 0 | 5 | 0 | 0 | no data | 152.5833 | no data | 100% | no data | 0 | 0 | 0 |  |  |  | no data | 149.9583 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-11-07 | 65.33 | 66.96% | 61.5 | 72 | 59 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3712 | 3618 | 0 | 0 | 0 | 40 | 0 | 40 | 0 | 60 | 0 | 4 | 0 | 0 | no data | 154.6667 | no data | 100% | no data | 0 | 0 | 0 |  |  |  | no data | 150.75 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-11-08 | 64.3 | 69.4% | 60.9 | 77.85 | 55.86 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3705 | 3642 | 0 | 0 | 0 | 40 | 0 | 40 | 0 | 60 | 0 | 5 | 0 | 0 | no data | 154.375 | no data | 100% | no data | 0 | 0 | 0 |  |  |  | no data | 151.75 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-11-09 | 67.2 | 61.7% | 60.4 | 86 | 57 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3691 | 3644 | 0 | 0 | 0 | 42 | 0 | 42 | 0 | 60 | 0 | 4 | 0 | 0 | no data | 153.7917 | no data | 100% | no data | 0 | 0 | 0 |  |  |  | no data | 151.8333 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-11-10 | 68.4 | 56.5% | 59.7 | 86 | 56 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3680 | 3642 | 0 | 0 | 0 | 42 | 0 | 42 | 0 | 60 | 0 | 4 | 0 | 0 | no data | 153.3333 | no data | 100% | no data | 0 | 0 | 0 |  |  |  | no data | 151.75 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-11-11 | 68.6 | 58.6% | 60.3 | 78 | 59 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3689 | 3642 | 0 | 0 | 0 | 42 | 0 | 42 | 0 | 60 | 0 | 8 | 0 | 0 | no data | 153.7083 | no data | 100% | no data | 0.697 | 992 | 691.424 |  |  |  | no data | 151.75 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
Week 46 | 2019-11-12 | 68.8 | 60.5% | 61.3 | 87 | 59 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3687 | 3643 | 0 | 0 | 0 | 42 | 0 | 42 | 0 | 60 | 0 | 7 | 0 | 0 | no data | 153.625 | no data | 100% | no data | 0 | 0 | 0 |  |  |  | no data | 151.7917 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-11-13 | 66.4 | 71.9% | 64.1 | 71 | 63 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3713 | 3662 | 0 | 0 | 0 | 42 | 0 | 42 | 0 | 60 | 0 | 5 | 0 | 0 | no data | 154.7083 | no data | 100% | no data | 0 | 0 | 0 |  |  |  | no data | 152.5833 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-11-14 | 65.5 | 76.8% | 65.2 | 76 | 60 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3709 | 3689 | 0 | 0 | 0 | 42 | 0 | 42 | 0 | 60 | 0 | 4 | 0 | 0 | no data | 154.5417 | no data | 100% | no data | 0 | 0 | 0 |  |  |  | no data | 153.7083 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-11-15 | 67 | 77% | 66.4 | 74 | 61 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3699 | 3688 | 0 | 0 | 0 | 42 | 0 | 42 | 0 | 60 | 0 | 5 | 0 | 0 | no data | 154.125 | no data | 100% | no data | 0 | 0 | 0 |  |  |  | no data | 153.6667 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-11-16 | 69 | 74% | 66.8 | 82 | 63 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3691 | 3687 | 0 | 0 | 0 | 42 | 0 | 42 | 0 | 60 | 0 | 4 | 0 | 0 | no data | 153.7917 | no data | 100% | no data | 0 | 0 | 0 |  |  |  | no data | 153.625 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-11-17 | 68.5 | 68.4% | 64 | 83.5 | 60 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3690 | 3682 | 0 | 0 | 0 | 42 | 0 | 42 | 0 | 60 | 0 | 4 | 0 | 0 | no data | 153.75 | no data | 100% | no data | 0 | 0 | 0 |  |  |  | no data | 153.4167 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-11-18 | 69.5 | 66.5% | 63.7 | 82 | 59 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3678 | 3678 | 0 | 0 | 0 | 42 | 0 | 42 | 0 | 60 | 0 | 5 | 0 | 0 | no data | 153.25 | no data | 100% | no data | 0 | 0 | 0 |  |  |  | no data | 153.25 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
Week 47 | 2019-11-19 | 68.5 | 64.7% | 62.7 | 84 | 58 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3682 | 3671 | 0 | 0 | 0 | 42 | 0 | 42 | 0 | 60 | 0 | 4 | 0 | 0 | no data | 153.4167 | no data | 100% | no data | 0 | 0 | 0 |  |  |  | no data | 152.9583 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-11-20 | 68.83 | 61.25% | 62 | 82 | 60 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3682 | 3668 | 0 | 0 | 0 | 42 | 0 | 42 | 0 | 60 | 0 | 5 | 0 | 0 | no data | 153.4167 | no data | 100% | no data | 0 | 0 | 0 |  |  |  | no data | 152.8333 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 50 | 0 | 0 | 0
| 2019-11-21 | 67.5 | 65.4% | 62.3 | 76 | 61 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3696 | 3669 | 0 | 0 | 0 | 42 | 0 | 42 | 0 | 60 | 0 | 4 | 0 | 0 | no data | 154 | no data | 100% | no data | 0 | 0 | 0 |  |  |  | no data | 152.875 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 50 | 0 | 0 | 0
| 2019-11-22 | 63.1 | 77% | 63 | 67 | 61 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3720 | 3669 | 0 | 0 | 0 | 42 | 0 | 42 | 0 | 60 | 0 | 5 | 0 | 0 | no data | 155 | no data | 100% | no data | 0 | 0 | 0 |  |  |  | no data | 152.875 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-11-23 | 64.67 | 71.92% | 62 | 80.37 | 57 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3705 | 3672 | 0 | 0 | 0 | 42 | 0 | 42 | 0 | 60 | 0 | 4 | 0 | 0 | no data | 154.375 | no data | 100% | no data | 0 | 0 | 0 |  |  |  | no data | 153 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-11-24 | 65.9 | 64.3% | 60.4 | 83 | 57 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3696 | 3676 | 0 | 0 | 0 | 42 | 0 | 42 | 0 | 60 | 0 | 5 | 0 | 0 | no data | 154 | no data | 100% | no data | 0 | 0 | 0 |  |  |  | no data | 153.1667 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-11-25 | 65.8 | 62.6% | 59.8 | 82 | 55 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3698 | 3677 | 0 | 0 | 0 | 42 | 0 | 42 | 0 | 60 | 0 | 5 | 0 | 0 | no data | 154.0833 | no data | 100% | no data | 0 | 0 | 0 |  |  |  | no data | 153.2083 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
Week 48 | 2019-11-26 | 66.4 | 59.5% | 59.5 | 76 | 59 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3699 | 3682 | 0 | 0 | 0 | 42 | 0 | 42 | 0 | 60 | 0 | 4 | 0 | 0 | no data | 154.125 | no data | 100% | no data | 0 | 0 | 0 |  |  |  | no data | 153.4167 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-11-27 | 64 | 68% | 60.4 | 80 | 55 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3702 | 3686 | 0 | 0 | 0 | 42 | 0 | 42 | 0 | 60 | 0 | 5 | 0 | 0 | no data | 154.25 | no data | 100% | no data | 0 | 0 | 0 |  |  |  | no data | 153.5833 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-11-28 | 64 | 70% | 61.1 | 76 | 46 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3708 | 3686 | 0 | 0 | 0 | 42 | 0 | 42 | 0 | 60 | 0 | 5 | 0 | 0 | no data | 154.5 | no data | 100% | no data | 0 | 0 | 0 |  |  |  | no data | 153.5833 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-11-29 | 62.3 | 64.5% | 57.7 | 79 | 53 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3707 | 3689 | 0 | 0 | 0 | 42 | 0 | 42 | 0 | 60 | 0 | 5 | 0 | 0 | no data | 154.4583 | no data | 100% | no data | 0 | 0 | 0 |  |  |  | no data | 153.7083 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-11-30 | 62.2 | 55% | 54 | 84 | 52 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3702 | 3696 | 0 | 0 | 0 | 42 | 0 | 42 | 0 | 60 | 0 | 5 | 0 | 0 | no data | 154.25 | no data | 100% | no data | 0 | 0 | 0 |  |  |  | no data | 154 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-12-01 | 63 | 53.57% | 54.34 | 86 | 51.4 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3701 | 3696 | 0 | 0 | 0 | 42 | 0 | 42 | 0 | 60 | 0 | 4 | 0 | 0 | no data | 154.2083 | no data | 100% | no data | 0 | 0 | 0 |  |  |  | no data | 154 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-12-02 | 62.72 | 57.69% | 55.21 | 80 | 51 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3700 | 3696 | 0 | 0 | 0 | 42 | 0 | 42 | 0 | 60 | 0 | 5 | 0 | 0 | no data | 154.1667 | no data | 100% | no data | 0 | 0 | 0 |  |  |  | no data | 154 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
Week 49 | 2019-12-03 | 62.3 | 63.7% | 56.9 | 80 | 51 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3700 | 3695 | 0 | 0 | 0 | 42 | 0 | 42 | 0 | 60 | 0 | 4 | 0 | 0 | no data | 154.1667 | no data | 100% | no data | 0 | 0 | 0 |  |  |  | no data | 153.9583 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-12-04 | 62.3 | 61.7% | 56.3 | 79 | 51 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3700 | 3695 | 0 | 0 | 0 | 43 | 0 | 43 | 0 | 60 | 0 | 5 | 0 | 0 | 0% | 154.1667 | no data | 100% | no data | 0 | 0 | 0 |  |  |  | no data | 153.9583 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-12-05 | 61.6 | 60.3% | 55.3 | 85 | 51 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3703 | 3695 | 0 | 0 | 0 | 43 | 0 | 43 | 0 | 60 | 0 | 5 | 0 | 0 | no data | 154.2917 | no data | 100% | no data | 0 | 0 | 0 |  |  |  | no data | 153.9583 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-12-06 | 61.3 | 58% | 54.3 | 85 | 50 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3709 | 3696 | 0 | 0 | 0 | 43 | 0 | 43 | 0 | 60 | 0 | 5 | 0 | 0 | no data | 154.5417 | no data | 100% | no data | 0 | 0 | 0 |  |  |  | no data | 154 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-12-07 | 60.61 | 59.25% | 53.8 | 83 | 49.75 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3708 | 3696 | 0 | 0 | 0 | 44 | 0 | 44 | 0 | 60 | 0 | 4 | 0 | 0 | no data | 154.5 | no data | 100% | no data | 0 | 0 | 0 |  |  |  | no data | 154 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-12-08 | 60.2 | 61.3% | 54.3 | 81 | 49 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3707 | 3697 | 0 | 0 | 0 | 44 | 0 | 44 | 0 | 60 | 0 | 5 | 0 | 0 | no data | 154.4583 | no data | 100% | no data | 0 | 0 | 0 |  |  |  | no data | 154.0417 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-12-09 | 61.7 | 62.4% | 56 | 74 | 51 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3708 | 3699 | 0 | 0 | 0 | 44 | 0 | 44 | 0 | 60 | 0 | 4 | 0 | 0 | no data | 154.5 | no data | 100% | no data | 0 | 0 | 0 |  |  |  | no data | 154.125 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
Week 50 | 2019-12-10 | 61.25 | 64.38% | 56.5 | 80 | 53 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3710 | 3699 | 0 | 0 | 0 | 44 | 0 | 44 | 0 | 60 | 0 | 5 | 0 | 0 | no data | 154.5833 | no data | 100% | no data | 0 | 0 | 0 |  |  |  | no data | 154.125 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-12-11 | 60.2 | 67% | 55.8 | 67 | 53 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3720 | 3704 | 0 | 0 | 0 | 44 | 0 | 44 | 0 | 60 | 0 | 5 | 0 | 0 | no data | 155 | no data | 100% | no data | 0 | 0 | 0 |  |  |  | no data | 154.3333 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-12-12 | 56.1 | 83.7% | 58.3 | 59 | 54 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3720 | 3717 | 0 | 0 | 0 | 44 | 0 | 44 | 0 | 60 | 0 | 5 | 0 | 0 | no data | 155 | no data | 100% | no data | 0 | 0 | 0 |  |  |  | no data | 154.875 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-12-13 | 54.5 | 83.7% | 56.5 | 60.9 | 48.8 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3720 | 3719 | 0 | 0 | 0 | 46 | 0 | 46 | 0 | 60 | 0 | 5 | 0 | 0 | no data | 155 | no data | 100% | no data | 0 | 0 | 0 |  |  |  | no data | 154.9583 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-12-14 | 53.17 | 88.67% | 55.88 | 57 | 48.8 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3720 | 3720 | 0 | 0 | 0 | 46 | 0 | 46 | 0 | 60 | 0 | 6 | 0 | 0 | no data | 155 | no data | 100% | no data | 0 | 0 | 0 |  |  |  | no data | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-12-15 | 53.7 | 84.7% | 56.2 | 57 | 52 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3720 | 3720 | 0 | 0 | 0 | 45 | 0 | 45 | 0 | 60 | 0 | 5 | 0 | 0 | no data | 155 | no data | 100% | no data | 0 | 0 | 0 |  |  |  | no data | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-12-16 | 54.4 | 80.7% | 56 | 67 | 51 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3720 | 3720 | 0 | 0 | 0 | 45 | 0 | 45 | 0 | 60 | 0 | 6 | 0 | 0 | no data | 155 | no data | 100% | no data | 0 | 0 | 0 |  |  |  | no data | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
Week 51 | 2019-12-17 | 53.7 | 79.9% | 54 | 67 | 43 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3720 | 3720 | 0 | 0 | 0 | 45 | 0 | 45 | 0 | 60 | 0 | 6 | 0 | 0 | no data | 155 | no data | 100% | no data | 0 | 0 | 0 |  |  |  | no data | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-12-18 | 55.3 | 73.8% | 53.6 | 75 | 42 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3719 | 3720 | 0 | 0 | 0 | 45 | 0 | 45 | 0 | 60 | 0 | 5 | 0 | 0 | no data | 154.9583 | no data | 100% | no data | 0 | 0 | 0 |  |  |  | no data | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-12-19 | 56.7 | 74.9% | 56.1 | 66.6 | 48.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 3718 | 3718 | 0 | 0 | 45 | 0 | 45 | 0 | 60 | 0 | 5 | -3718 | 0 | no data | 155 | no data | 100% | no data | 0 | 0 | 0 |  |  |  | no data | 154.9167 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-12-20 | 54.9 | 76.7% | 54.6 | 68 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 3716 | 3716 | 0 | 0 | 45 | 0 | 45 | 0 | 60 | 0 | 6 | -3716 | 0 | no data | 155 | no data | 100% | no data | 0 | 0 | 0 |  |  |  | no data | 154.8333 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-12-21 | 51.7 | 84% | 53.8 | 60 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 3720 | 3720 | 0 | 0 | 45 | 0 | 45 | 0 | 60 | 0 | 5 | -3720 | 0 | no data | 155 | no data | 100% | no data | 0 | 0 | 0 |  |  |  | no data | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-12-22 | 47.9 | 90.6% | 50.9 | 52 | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 3720 | 3720 | 0 | 0 | 45 | 0 | 45 | 0 | 60 | 0 | 5 | -3720 | 0 | no data | 155 | no data | 100% | no data | 0 | 0 | 0 |  |  |  | no data | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-12-23 | 48.17 | 85.5% | 51.42 | 52.45 | 44.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 3720 | 3720 | 0 | 0 | 48 | 0 | 48 | 0 | 60 | 0 | 6 | -3720 | 0 | no data | 155 | no data | 100% | no data | 0 | 0 | 0 |  |  |  | no data | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
Week 52 | 2019-12-24 | 47.88 | 88.46% | 51 | 50 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 3720 | 3720 | 0 | 0 | 48 | 0 | 48 | 0 | 60 | 0 | 6 | -3720 | 0 | no data | 155 | no data | 100% | no data | 0 | 0 | 0 |  |  |  | no data | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-12-25 | 47.3 | 79.2% | 47.5 | 54 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 3720 | 3720 | 0 | 0 | 48 | 0 | 48 | 0 | 60 | 0 | 5 | -3720 | 0 | no data | 155 | no data | 100% | no data | 0 | 0 | 0 |  |  |  | no data | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-12-26 | 43.71 | 89.33% | 46.63 | 47 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 3720 | 3720 | 0 | 0 | 48 | 0 | 48 | 0 | 60 | 0 | 6 | -3720 | 0 | no data | 155 | no data | 100% | no data | 0 | 0 | 0 |  |  |  | no data | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-12-27 | 43.9 | 86.3% | 46.7 | 46 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 3720 | 3720 | 0 | 0 | 48 | 0 | 48 | 0 | 60 | 0 | 5 | -3720 | 0 | no data | 155 | no data | 100% | no data | 0 | 0 | 0 |  |  |  | no data | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 49.97 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-12-28 | 45.8 | 75.7% | 47.2 | 47 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 3720 | 3720 | 0 | 0 | 48 | 0 | 48 | 0 | 60 | 0 | 5 | -3720 | 0 | no data | 155 | no data | 100% | no data | 0 | 0 | 0 |  |  |  | no data | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 49.9 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-12-29 | 46.6 | 73.6% | 47.1 | 51 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 3720 | 3720 | 0 | 0 | 48 | 0 | 48 | 0 | 60 | 0 | 5 | -3720 | 0 | no data | 155 | no data | 100% | no data | 0 | 0 | 0 |  |  |  | no data | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 49.98 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-12-30 | 42.3 | 80.8% | 44.4 | 44 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 3720 | 3720 | 0 | 0 | 48 | 0 | 48 | 0 | 60 | 0 | 6 | -3720 | 0 | no data | 155 | no data | 100% | no data | 0 | 0 | 0 |  |  |  | no data | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-12-31 | 45.2 | 73.7% | 45.9 | 49 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 3720 | 3720 | 0 | 0 | 48 | 0 | 48 | 0 | 60 | 0 | 7 | -3720 | 0 | no data | 155 | no data | 100% | no data | 0 | 0 | 0 |  |  |  | no data | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
Note on BN181: ops.e: assumed due to problem of GC of OGDCL.
Note on BN216: ops.e: assumed due to problem of GC of OGDCL.
Note on BN244: ops.e: assumed due to problem of GC of OGDCL.

## Feb
Monthly Operational Returns Kabirwala
2019-02-01
| Date | Site Avg. Ambient Temp.F | Site Avg. Relative Humidty % | Site Avg. Ambient Wetbulb Temp.F | Site Ambient Temp |  | Base load hours |  |  |  | Standby hours |  |  |  | Plant ambient corrected Max Load |  | Corrected Plant Capacity | Ambient Corrected Daclared Avail'y (MWH) | Plant WAPDA Dispatch (MWH) | Net Plant Export (MWH) | Gross Generation | CT1 Average Cap (MW) | CT1 Unavail minutes | CT2 Average Cap (MW) | CT2 Unavail minutes | ST Average Cap (MW) | ST Unavail minutes | Plant Aux Load including Colony Load MWH | Differenece (+/-) MW | Maximum Daily Generation | Daily Load Factor | Avg. Corrected Plant Capacity | Plant Capacity Factor | Plant Availability Factor | Equivalent Plant Availability | LBtu gas flow (mmscf/day) | 1 LBtu gas (Average Btu/scf) | LBTU MMBTU | 1 HBtu gas flow (mmscf/day) | 1 HBtu gas (Average Btu/scf) | HBTU MMBTU | HHV Net Heat Rate (Btu/Kwh) | Avg. declared availability | CT1 Derated MW | CT1 derated mintutes | CT-2 derated MW | CT-2 derated mintutes | ST derated MW | ST derated mintutes | WAPDA Backfeed (MWH) | CT-1 Gross Generation (MWH) | CT-2 Gross Generation (MWH) | STG Gross Generation (MWH) | CT-1 & CT-2 MWH difference | Base load Heat Rate | STG load | DB1 | DB2 | CT1 | CT1 Gas flow | CT2 Gas flow |  | Pamb | Freq. Hz | LBTU Gas Specific gravity | CT-1 compressor efficiency(%) | CT-2 compressor efficiency(%) |  | CT-1 Heat Rate (Btu/Kwh) | CT-2 Heat Rate (Btu/Kwh) |  | DB(1+2) | DB-1 Ops Hours | DB-2 Ops Hours | CT-1 Wetcomprssion Ops Hours | RO Operation Hours | CT1 T/G Brg |  | CT2 T/G Brg
[7 empty] | CT1 |  | CT2 |  | CT1 |  | CT2 | [43 empty] | mmscf/d | mmscf/d | WetC flow | HBTU KPPH | HBTU KPPH | LBTU KPPH | mbar | Hz | [7 empty] | mmscf/d |  |  |  |  | Supply air pressure | Seal air pressure | Supply air pressure | Seal air pressure
[5 empty] | Max | Min | hrs | min | hrs | min | hrs | min | hrs | min | hrs | min | [42 empty] | gpm | [17 empty] | Psi | "WC | Psi | "WC
Week 5 | 2019-01-29 | 56.3 | 65.8% | 47.7 | 71 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 6 | 0 | 0 | 0% | 155 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1004.54 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-01-30 | 55.3 | 69.2% | 48.1 | 59 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 5 | 0 | 0 | 0% | 155 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1003.5 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-01-31 | 51.8 | 83% | 49.7 | 54.7 | 50.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 6 | 0 | 0 | 0% | 155 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1004 | 50.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-02-01 | 54.3 | 76.6% | 49.7 | 67 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 6 | 0 | 0 | 0% | 155 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1003 | 50.08 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-02-02 | 56.2 | 70.9% | 49.5 | 72 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 5 | 0 | 0 | 0% | 155 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1003 | 50.1 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-02-03 | 58.4 | 65.9% | 49.9 | 76 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3715 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 5 | 0 | 0 | 0% | 154.7917 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1004 | 50 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-02-04 | 60.1 | 66.7% | 51 | 73.9 | 48.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3714 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 6 | 0 | 0 | 0% | 154.75 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1003.7 | 50 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Week 6 | 2019-02-05 | 62.87 | 64.6% | 53.27 | 75 | 53.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3712 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 5 | 0 | 0 | 0% | 154.6667 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1000.8 | 50 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-02-06 | 58.1 | 66.6% | 50.1 | 67 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 6 | 0 | 0 | 0% | 155 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 996.1 | 50 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-02-07 | 54.1 | 75.5% | 48.8 | 65 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 5 | 0 | 0 | 0% | 155 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 993.8 | 50 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-02-08 | 52.8 | 67.8% | 45.7 | 63 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 5 | 0 | 0 | 0% | 155 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1001.3 | 50 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-02-09 | 55.8 | 65.4% | 47.2 | 74 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3719 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 4 | 0 | 0 | 0% | 154.9583 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1003.9 | 50 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-02-10 | 57.8 | 64.8% | 48.8 | 72 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 4 | 0 | 0 | 0% | 155 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1004.3 | 50 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-02-11 | 59.9 | 64.9% | 51.1 | 69.9 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3716 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 6 | 0 | 0 | 0% | 154.8333 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1004.9 | 50 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Week 7 | 2019-02-12 | 61.3 | 66.9% | 52.9 | 70 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3717 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 5 | 0 | 0 | 0% | 154.875 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1004 | 50 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-02-13 | 61.2 | 66.6% | 52.5 | 70 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3717 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 4 | 0 | 0 | 0% | 154.875 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1003 | 50 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-02-14 | 61 | 69.5% | 53.6 | 74 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3719 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 5 | 0 | 0 | 0% | 154.9583 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1003 | 50 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-02-15 | 58.44 | 69.79% | 50.53 | 73.5 | 49.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3716 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 5 | 0 | 0 | 0% | 154.8333 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1001 | 50 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-02-16 | 60.36 | 57.65% | 48.65 | 72.85 | 48.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3712 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 5 | 0 | 0 | 0% | 154.6667 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1002 | 50 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-02-17 | 61.52 | 59.92% | 50.87 | 72 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3710 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 5 | 0 | 0 | 0% | 154.5833 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 998 | 50 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-02-18 | 58.17 | 74.33% | 53.12 | 62 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 5 | 0 | 0 | 0% | 155 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 998 | 50 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Week 8 | 2019-02-19 | 57 | 76% | 52 | 66 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 5 | 0 | 0 | 0% | 155 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 998 | 50 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-02-20 | 56 | 82% | 53 | 58 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 5 | 0 | 0 | 0% | 155 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1001 | 50 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-02-21 | 58.5 | 78.8% | 54.2 | 68.5 | 53.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 5 | 0 | 0 | 0% | 155 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1001.3 | 50.05 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
| 2019-02-22 | 59.9 | 70.6% | 52 | 74 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3716 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 4 | 0 | 0 | 0% | 154.8333 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1003.1 | 50.05 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1
| 2019-02-23 | 60.9 | 60.9% | 50.2 | 75 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3709 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 4 | 0 | 0 | 0% | 154.5417 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 50.05 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
| 2019-02-24 | 61.5 | 67.7% | 50.05 | 76 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3709 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 4 | 0 | 0 | 0% | 154.5417 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 995 | 50.05 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9
| 2019-02-25 | 60.7 | 65.5% | 50.08 | 73 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3710 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 5 | 0 | 0 | 0% | 154.5833 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 995 | 50.05 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1
Week 9 | 2019-02-26 | 56.6 | 71% | 50 | 66 | 46 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 6 | 0 | 0 | 0% | 155 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 995.5 | 50.04 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2
| 2019-02-27 | 57.96 | 66.2% | 49.72 | 69 | 49.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 6 | 0 | 0 | 0% | 155 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 995 | 50.05 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2
| 2019-02-28 | 60 | 65.1% | 51 | 70 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3716 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 5 | 0 | 0 | 0% | 154.8333 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999.2 | 50 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9
| 2019-03-01 | [27 empty] | 0 |  |  |  |  | #DIV/0! |  |  |  | 0 |  |  | 0 | no data | 0 | [11 empty] | no data | 0 | [11 empty] | 0 |  |  | 0 | 0 | [8 empty] | 3.8
| 2019-03-02 | [27 empty] | 0 |  |  |  |  | #DIV/0! |  |  |  | 0 |  |  | 0 | no data | 0 | [10 empty] | 0 | no data | 0 | [11 empty] | 0 |  |  | 0 | 0
| 2019-03-03 | [27 empty] | 0 |  |  |  |  | #DIV/0! |  |  |  | 0 |  |  | 0 | no data | 0 | [10 empty] | 0 | no data | 0 | [11 empty] | 0 |  |  | 0 | 0
| 2019-03-04 | [27 empty] | 0 |  |  |  |  | #DIV/0! |  |  |  | 0 |  |  | 0 | no data | 0 | [10 empty] | 0 | no data | 0 | [11 empty] | 0 |  |  | 0 | 0
| Monthly | 58.22 | 68.91% | 50.4835 | 69.3339 | 50.3748 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115227 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 124 | 0 | 0 | 0% | 154.875 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! |  | 0 | 0 | 0 | 0 | 0 | 0 | 124 | 0 | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1000.036 | 50.0136 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| Totals | Avg.F | % Avg. |  | M Avg | m Avg | hrs | min | hrs | min | hrs | min | hrs | min | Avg Int Avi | Avg Ext Avi | MWhr Total | MWhr Total | MWhr Total | MWhr Total | MWhr Total | MW Avg | Total min | Avg MW | Total min | Avg MW | Total min | MWhr | Total MW | Av Max D/Gen | Av. DailyLF | Avg. | Avg. |  | Avg. | Total | Avg. |  | Total | Avg. |  | Avg. | [7 empty] | Total |  |  |  |  | Avg.
| Weeks data | Site Avg. Amb. Temp F | Site Avg. Relative humidity % | Site Avg. Ambient Wetbulb Temp.F | M Avg: Site Maximum/Minumum Temperature; hrs: CT-1 Base Load Hours; hrs: CT-2 Base Load Hours; hrs: CT-1 stand by hours / min; hrs: CT-2 standby hours / min | Plant ambient Corrected maximum Load hours/min |  | Average Corrected Plant Capacity | Ambient Corrected Declared Avail'y (MWH) | Av Plant WAPDA Dispatch | Net Plant Export (MWH) | Gross Generation | CT1 Av Cap (MW) | CT1 Unavail minutes | CT2 Av Cap (MW) | CT2 Unavail minutes | ST Unavail minutes | ST Average Cap (MW) | Plant Aux Load including Colony Load MWH | Differenece (+/-) MW | Maximum Daily Generation | Daily Load Factor | Avg. Corrected Plant | Plant Capacity Facto | Plant Availability Factor | Equivalent Plant Availability | LBtu gas flow mmscf | 1 LBtu gas (Average Btu/scf) | LBTU MMBTU | PL gas flow (mscf/week) | 1 PL gas (Average Btu/scf) | HBTU MMBTU | Plant Net Heat Rate (Btu/Kwh) | [11 empty] | 0
| Week 1 | 56.0571 | 71.16% | 49.3714 | 67.6571 | 48.6143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3718.4286 | no data | no data | no data | no data | 44 | No outage | 48 | No outage | 420 | no data | no data | no data | no data | no data | 154.9345 | no data | 100% | no data | no data | no data | #VALUE! | no data | no data | #VALUE! | #DIV/0!
| Week 2 | 57.3386 | 67.09% | 50.1671 | 69.4143 | 48.9871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3718.1429 | no data | no data | no data | no data | 44 | No outage | 336 | no data | 420 | no data | 35 | no data | no data | no data | 154.9226 | no data | 100% | no data | no data | no data | #VALUE! | no data | no data | #VALUE! | #DIV/0! | [5 empty] | 0.27381
| Week 3 | 60.2843 | 66.38% | 51.7386 | 70.6214 | 52.7071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3715.8571 | no data | no data | no data | no data | 44 | No outage | 336 | no data | 420 | no data | 34 | no data | no data | no data | 154.8274 | no data | 100% | no data | no data | no data | #VALUE! | no data | no data | #VALUE! | #DIV/0! | [5 empty] | 0.26672
| Week 4 | 59.2143 | 71.64% | 51.7386 | 70.0714 | 52.0286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3714.8571 | no data | no data | no data | no data | 44 | No outage | 336 | no data | 420 | no data | 32 | no data | no data | no data | 154.7857 | no data | 100% | no data | no data | no data | #VALUE! | no data | no data | #VALUE! | #DIV/0!
| Week 5 | 58.1867 | 0.67433 | 50.24 | 68.3333 | 48.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3718.6667 | no data | no data | no data | no data | 44 | #REF! | #REF! | no data | #REF! | no data | 17 | no data | no data | no data | 154.9444 | no data | #DIV/0! | no data | no data | no data | #VALUE! | no data | no data | #VALUE! | #DIV/0!
| Date | Plant Status Whether Normal Operation or Tripping (State full detail for trippings/return to normal).
| 2019-02-01 | Plant remained shutdown due to suspension of HBTU gas by M/S SNGPL.
| 2019-02-02 | Plant remained shutdown due to suspension of HBTU gas by M/S SNGPL.
| 2019-02-03 | Plant remained shutdown due to suspension of HBTU gas by M/S SNGPL.
| 2019-02-04 | Plant remained shutdown due to suspension of HBTU gas by M/S SNGPL.
| 2019-02-05 | Plant remained shutdown due to suspension of HBTU gas by M/S SNGPL.
| 2019-02-06 | Plant remained shutdown due to suspension of HBTU gas by M/S SNGPL.
| 2019-02-07 | Plant remained shutdown due to suspension of HBTU gas by M/S SNGPL.
| 2019-02-08 | Plant remained shutdown due to suspension of HBTU gas by M/S SNGPL.
| 2019-02-09 | Plant remained shutdown due to suspension of HBTU gas by M/S SNGPL.
| 2019-02-10 | Plant remained shutdown due to suspension of HBTU gas by M/S SNGPL.
| 2019-02-11 | Plant remained shutdown due to suspension of HBTU gas by M/S SNGPL.
| 2019-02-12 | Plant remained shutdown due to suspension of HBTU gas by M/S SNGPL.
| 2019-02-13 | Plant remained shutdown due to suspension of HBTU gas by M/S SNGPL.
| 2019-02-14 | Plant remained shutdown due to suspension of HBTU gas by M/S SNGPL.
| 2019-02-15 | Plant remained shutdown due to suspension of HBTU gas by M/S SNGPL.
| 2019-02-16 | Plant remained shutdown due to suspension of HBTU gas by M/S SNGPL.
| 2019-02-17 | Plant remained shutdown due to suspension of HBTU gas by M/S SNGPL.
| 2019-02-18 | Plant remained shutdown due to suspension of HBTU gas by M/S SNGPL.
| 2019-02-19 | Plant remained shutdown due to suspension of HBTU gas by M/S SNGPL.
| 2019-02-20 | Plant remained shutdown due to suspension of HBTU gas by M/S SNGPL.
| 2019-02-21 | Plant remained shutdown due to suspension of HBTU gas by M/S SNGPL.
| 2019-02-22 | Plant remained shutdown due to suspension of HBTU gas by M/S SNGPL.
| 2019-02-23 | Plant remained shutdown due to suspension of HBTU gas by M/S SNGPL.
| 2019-02-24 | Plant remained shutdown due to suspension of HBTU gas by M/S SNGPL.
| 2019-02-25 | Plant remained shutdown due to suspension of HBTU gas by M/S SNGPL.
| 2019-02-26 | Plant remained shutdown due to suspension of HBTU gas by M/S SNGPL.
| 2019-02-27 | Plant remained shutdown due to suspension of HBTU gas by M/S SNGPL.
| 2019-02-28 | Plant remained shutdown due to suspension of HBTU gas by M/S SNGPL.

## Mar
Monthly Operational Returns Kabirwala
2019-03-01
| Date | Site Avg. Ambient Temp.F | Site Avg. Relative Humidty % | Site Avg. Ambient Wetbulb Temp.F | Site Ambient Temp |  | Base load hours |  |  |  | Standby hours |  |  |  | Plant ambient corrected Max Load |  | Corrected Plant Capacity | Ambient Corrected Daclared Avail'y (MWH) | Plant WAPDA Dispatch (MWH) | Net Plant Export (MWH) | Gross Generation | CT1 Average Cap (MW) | CT1 Unavail minutes | CT2 Average Cap (MW) | CT2 Unavail minutes | ST Average Cap (MW) | ST Unavail minutes | Plant Aux Load including Colony Load MWH | Differenece (+/-) MW | Maximum Daily Generation | Daily Load Factor | Avg. Corrected Plant Capacity | Plant Capacity Factor | Plant Availability Factor | Equivalent Plant Availability | LBtu gas flow (mmscf/day) | 1 LBtu gas (Average Btu/scf) | LBTU MMBTU | 1 HBtu gas flow (mmscf/day) | 1 HBtu gas (Average Btu/scf) | HBTU MMBTU | HHV Net Heat Rate (Btu/Kwh) | Avg. declared availability | CT1 Derated MW | CT1 derated mintutes | CT-2 derated MW | CT-2 derated mintutes | ST derated MW | ST derated mintutes | WAPDA Backfeed (MWH) | CT-1 Gross Generation (MWH) | CT-2 Gross Generation (MWH) | STG Gross Generation (MWH) | CT-1 & CT-2 MWH difference | Base load Heat Rate | STG load | DB1 | DB2 | CT1 | CT1 Gas flow | CT2 Gas flow |  | Pamb | Freq. Hz | LBTU Gas Specific gravity | CT-1 compressor efficiency(%) | CT-2 compressor efficiency(%) |  | CT-1 Heat Rate (Btu/Kwh) | CT-2 Heat Rate (Btu/Kwh) |  | DB(1+2) | DB-1 Ops Hours | DB-2 Ops Hours | CT-1 Wetcomprssion Ops Hours | RO Operation Hours | CT1 T/G Brg |  | CT2 T/G Brg
[7 empty] | CT1 |  | CT2 |  | CT1 |  | CT2 | [43 empty] | mmscf/d | mmscf/d | WetC flow | HBTU KPPH | HBTU KPPH | LBTU KPPH | mbar | Hz | [7 empty] | mmscf/d |  |  |  |  | Supply air pressure | Seal air pressure | Supply air pressure | Seal air pressure
[5 empty] | Max | Min | hrs | min | hrs | min | hrs | min | hrs | min | hrs | min | [42 empty] | gpm | [17 empty] | Psi | "WC | Psi | "WC
Week 9 | 2019-02-26 | 56.6 | 71% | 50 | 66 | 46 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 6 | 0 | 0 | 0% | 155 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 995.5 | 50.04 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-02-27 | 57.96 | 66.2% | 49.72 | 69 | 49.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 6 | 0 | 0 | 0% | 155 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 995 | 50.05 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-02-28 | 60 | 65.1% | 51 | 70 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3716 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 6 | 0 | 0 | 0% | 154.8333 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999.2 | 50 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-03-01 | 60.9 | 67.04% | 52 | 65 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 5 | 0 | 0 | no data | 155 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-03-02 | 56.3 | 82.1% | 53.8 | 57 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 5 | 0 | 0 | no data | 155 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 50.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-03-03 | 58.5 | 80.1% | 55.2 | 64 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 6 | 0 | 0 | no data | 155 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 998.4 | 50.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-03-04 | 61.5 | 69.8% | 53.4 | 72 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3713 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 5 | 0 | 0 | no data | 154.7083 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 995 | 50.03 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Week 10 | 2019-03-05 | 64 | 62.6% | 53.3 | 84 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3702 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 5 | 0 | 0 | no data | 154.25 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 995.3 | 50.06 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-03-06 | 65.5 | 59.9% | 54 | 84 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3693 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 5 | 0 | 0 | no data | 153.875 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 995.8 | 50.05 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-03-07 | 67.3 | 58.9% | 54.5 | 81 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3687 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 4 | 0 | 0 | no data | 153.625 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 995.5 | 50.1 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-03-08 | 62.5 | 68.7% | 55.5 | 73 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3715 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 4 | 0 | 0 | no data | 154.7917 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 50.1 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-03-09 | 65.4 | 60.5% | 53.8 | 84 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3689 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 4 | 0 | 0 | no data | 153.7083 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 50.08 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-03-10 | 67.1 | 57.8% | 54.7 | 83 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3682 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 4 | 0 | 0 | no data | 153.4167 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 997 | 50.06 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-03-11 | 62.42 | 71.98% | 55.77 | 75 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3714 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 4 | 0 | 0 | no data | 154.75 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 998 | 50.06 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Week 11 | 2019-03-12 | 63.79 | 66.81% | 54.99 | 79 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3706 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 4 | 0 | 0 | no data | 154.4167 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 50.07 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-03-13 | 65.43 | 64.33% | 55.53 | 84 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3694 | 0 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 4 | 0 | 0 | no data | 153.9167 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 998 | 50.12 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-03-14 | 65.4 | 64.6% | 55.8 | 79 | 57 | 0 | 0 | 0 | 0 | 4 | 45 | 4 | 45 | 0 | 0 | 3697 | 766 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 6 | 0 | 0 | no data | 154.0417 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 31.9167 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 50.09 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-03-15 | 67 | 59.6% | 55.2 | 81 | 56 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3688 | 3676 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 10 | 0 | 0 | no data | 153.6667 | no data | 100% | no data | 0 | 0 | 0 | 0.283 | 1000 | 283 | no data | 153.1667 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0.6 | 0 | 1003.6 | 50.08 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0
| 2019-03-16 | 68 | 59% | 56 | 80 | 58 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3685 | 3676 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 6 | 0 | 0 | no data | 153.5417 | no data | 100% | no data | 0 | 0 | 0 | 0.25 | 990 | 247.5 | no data | 153.1667 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0.5 | 0 | 0 | 1001 | 50.09 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-03-17 | 71.1 | 57.1% | 57.3 | 83 | 59 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3667 | 3658 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 6 | 0 | 0 | no data | 152.7917 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 152.4167 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 998.5 | 50.1 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-03-18 | 69.6 | 64.2% | 59 | 83 | 60 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3680 | 3658 | 0 | 0 | 0 | 44 | 0 | 48 | 0 | 60 | 0 | 6 | 0 | 0 | no data | 153.3333 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 152.4167 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 997.7 | 50.02 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Week 12 | 2019-03-19 | 71.3 | 62.2% | 59.8 | 88 | 61 | 0 | 0 | 0 | 0 | 8 | 0 | 8 | 0 | 0 | 0 | 3666 | 1240 | 0 | 0 | 0 | 44 | 960 | 48 | 960 | 60 | 960 | 5 | 0 | 0 | no data | 152.75 | no data | 33.33% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 51.6667 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 993 | 50.05 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-03-20 | 68.2 | 67.5% | 59.1 | 82 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3692 | 0 | 0 | 0 | 0 | 44 | 1440 | 48 | 1440 | 60 | 1440 | 3 | 0 | 0 | no data | 153.8333 | no data | 0% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 995 | 50.04 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-03-21 | 71.4 | 58.3% | 58.3 | 91 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3666 | 0 | 0 | 0 | 0 | 44 | 1440 | 48 | 1440 | 60 | 1440 | 3 | 0 | 0 | no data | 152.75 | no data | 0% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 998 | 50 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-03-22 | 74 | 55.9% | 59.4 | 88 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3649 | 0 | 0 | 0 | 0 | 44 | 1440 | 48 | 1440 | 60 | 1440 | 4 | 0 | 0 | no data | 152.0417 | no data | 0% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 50.09 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-03-23 | 72.3 | 63.2% | 61.3 | 87 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3673 | 0 | 0 | 0 | 0 | 44 | 1440 | 48 | 1440 | 60 | 1440 | 4 | 0 | 0 | no data | 153.0417 | no data | 0% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 50.04 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-03-24 | 68.75 | 70.74% | 61.41 | 85.77 | 62.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3695 | 0 | 0 | 0 | 0 | 44 | 1440 | 48 | 1440 | 60 | 1440 | 4 | 0 | 0 | no data | 153.9583 | no data | 0% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 998.24 | 50.05 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-03-25 | 74.6 | 57.9% | 60.8 | 93 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3642 | 0 | 0 | 0 | 0 | 44 | 1440 | 48 | 1440 | 60 | 1440 | 4 | 0 | 0 | no data | 151.75 | no data | 0% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 997.1 | 50.04 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Week 13 | 2019-03-26 | 76.4 | 57.7% | 62 | 90 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3627 | 0 | 0 | 0 | 0 | 43 | 1440 | 47 | 1440 | 60 | 1440 | 5 | 0 | 0 | no data | 151.125 | no data | 0% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 997 | 49.98 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-03-27 | 79.5 | 52.8% | 62.3 | 93 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3600 | 0 | 0 | 0 | 0 | 43 | 1440 | 47 | 1440 | 60 | 1440 | 5 | 0 | 0 | no data | 150 | no data | 0% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 997 | 50.02 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-03-28 | 79.7 | 57.2% | 64 | 91 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3601 | 3638 | 3638 | 0 | 0 | 43 | 0 | 47 | 0 | 60 | 0 | 6 | -3638 | 0 | no data | 150.0417 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 151.5833 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 995 | 50.07 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-03-29 | 81.6 | 60.7% | 67.7 | 98 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3581 | 3620 | 3620 | 0 | 0 | 43 | 0 | 47 | 0 | 60 | 0 | 6 | -3620 | 0 | no data | 149.2083 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 150.8333 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 992.7 | 50.1 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 | 0
| 2019-03-30 | 81.6 | 51.5% | 63.8 | 100 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3582 | 3579 | 3579 | 0 | 0 | 43 | 0 | 47 | 0 | 60 | 0 | 4 | -3579 | 0 | no data | 149.25 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 149.125 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 993.3 | 50.05 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-03-31 | 77.5 | 44.3% | 57.4 | 93 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3619 | 3567 | 3567 | 0 | 0 | 43 | 0 | 47 | 0 | 60 | 0 | 4 | -3567 | 0 | no data | 150.7917 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 148.625 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 994.8 | 50.05 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-04-01 | [27 empty] | 0 |  | no data | no data | no data | #DIV/0! | no data |  |  | 0 |  |  | 0 | no data | 0 | [11 empty] | no data | 0 | [15 empty] | 0
| Monthly | 68.9868 | 0.62419 | 57.6484 | 82.9281 | 59.2516 | 0 | 0 | 0 | 0 | 48 | 45 | 48 | 45 | 0 | 0 | 113865 | 31078 | 14404 | 0 | 0 | 43.8065 | 12480 | 47.8065 | 12480 | 60 | 12480 | 150 | -14404 | 0 | #DIV/0! | 153.0444 | 0% | 72.04% | #DIV/0! | 0 | 0 | 0 | 0.533 | 64.1935 | 530.5 | #DIV/0! |  | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0 | 0.5 | 0.6 | 0 | 997.4174 | 50.0587 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 6.5
| Totals | Avg.F | % Avg. |  | M Avg | m Avg | hrs | min | hrs | min | hrs | min | hrs | min | Avg Int Avi | Avg Ext Avi | MWhr Total | MWhr Total | MWhr Total | MWhr Total | MWhr Total | MW Avg | Total min | Avg MW | Total min | Avg MW | Total min | MWhr | Total MW | Av Max D/Gen | Av. DailyLF | Avg. | Avg. |  | Avg. | Total | Avg. |  | Total | Avg. |  | Avg. | [7 empty] | Total |  |  |  |  | Avg.
| Weeks data | Site Avg. Amb. Temp F | Site Avg. Relative humidity % | Site Avg. Ambient Wetbulb Temp.F | M Avg: Site Maximum/Minumum Temperature; hrs: CT-1 Base Load Hours; hrs: CT-2 Base Load Hours; hrs: CT-1 stand by hours / min; hrs: CT-2 standby hours / min | Plant ambient Corrected maximum Load hours/min |  | Average Corrected Plant Capacity | Ambient Corrected Declared Avail'y (MWH) | Av Plant WAPDA Dispatch | Net Plant Export (MWH) | Gross Generation | CT1 Av Cap (MW) | CT1 Unavail minutes | CT2 Av Cap (MW) | CT2 Unavail minutes | ST Unavail minutes | ST Average Cap (MW) | Plant Aux Load including Colony Load MWH | Differenece (+/-) MW | Maximum Daily Generation | Daily Load Factor | Avg. Corrected Plant | Plant Capacity Facto | Plant Availability Factor | Equivalent Plant Availability | LBtu gas flow mmscf | 1 LBtu gas (Average Btu/scf) | LBTU MMBTU | PL gas flow (mscf/week) | 1 PL gas (Average Btu/scf) | HBTU MMBTU | Plant Net Heat Rate (Btu/Kwh) | [11 empty] | 0
| Week 9 | 58.8229 | 71.62% | 52.16 | 66.1429 | 51.8943 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3718.4286 | no data | no data | no data | no data | 44 | No outage | 48 | No outage | 420 | no data | no data | no data | no data | no data | 154.9345 | no data | 100% | no data | no data | no data | #VALUE! | no data | no data | #VALUE! | #DIV/0!
| Week 10 | 64.8886 | 62.91% | 52.6314 | 80.5714 | 55.1429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3697.4286 | no data | no data | no data | no data | 44 | No outage | 336 | no data | 420 | no data | 30 | no data | no data | #DIV/0! | 154.0595 | #DIV/0! | 100% | #DIV/0! | no data | no data | #VALUE! | no data | no data | #VALUE! | #DIV/0! | [5 empty] | 0.27381
| Week 11 | 67.1886 | 62.23% | 56.26 | 81.2857 | 57.1429 | 0 | 0 | 0 | 0 | 100 | 45 | 100 | 45 | 0 | 0 | 3688.1429 | no data | no data | no data | no data | 44 | No outage | 336 | no data | 420 | no data | 42 | no data | no data | #DIV/0! | 153.6726 | #DIV/0! | 100% | #DIV/0! | no data | no data | #VALUE! | no data | no data | #VALUE! | #DIV/0! | [5 empty] | 0.26672
| Week 12 | 71.5071 | 62.25% | 56.26 | 87.8243 | 62.4 | 0 | 0 | 0 | 0 | 8 | 0 | 8 | 0 | 0 | 0 | 3669 | 177.1429 | no data | no data | no data | 44 | 9600 | 336 | 1371.4286 | 420 | 1371.4286 | 27 | no data | no data | #DIV/0! | 152.875 | #DIV/0! | 4.762% | #DIV/0! | no data | no data | #VALUE! | no data | no data | #VALUE! | #DIV/0!
| Week 13 | 79.3833 | 0.54033 | 62.8667 | 94.1667 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3601.6667 | no data | no data | no data | no data | 43 | #REF! | #REF! | 480 | #REF! | 480 | 30 | no data | no data | #DIV/0! | 150.0694 | #DIV/0! | no data | #DIV/0! | no data | no data | #VALUE! | no data | no data | #VALUE! | #DIV/0!
| Date | Plant Status Whether Normal Operation or Tripping (State full detail for trippings/return to normal).
| 2019-03-01 | Plant remained shutdown due to suspension of HBTU gas by M/S SNGPL.
| 2019-03-02 | Plant remained shutdown due to suspension of HBTU gas by M/S SNGPL.
| 2019-03-03 | Plant remained shutdown due to suspension of HBTU gas by M/S SNGPL.
| 2019-03-04 | Plant remained shutdown due to suspension of HBTU gas by M/S SNGPL.
| 2019-03-05 | Plant remained shutdown due to suspension of HBTU gas by M/S SNGPL.
| 2019-03-06 | Plant remained shutdown due to suspension of HBTU gas by M/S SNGPL.
| 2019-03-07 | Plant remained shutdown due to suspension of HBTU gas by M/S SNGPL.
| 2019-03-08 | Plant remained shutdown due to suspension of HBTU gas by M/S SNGPL.
| 2019-03-09 | Plant remained shutdown due to suspension of HBTU gas by M/S SNGPL.
| 2019-03-10 | Plant remained shutdown due to suspension of HBTU gas by M/S SNGPL.
| 2019-03-11 | Plant remained shutdown due to suspension of HBTU gas by M/S SNGPL.
| 2019-03-12 | Plant remained shutdown due to suspension of HBTU gas by M/S SNGPL.
| 2019-03-13 | Plant remained shutdown due to suspension of HBTU gas by M/S SNGPL.
| 2019-03-14 | Plant remained shutdown from 0000~1915hrs due to suspension of HBTU gas by M/S SNGPL. Plant remained in Standby mode from 1915~2400hrs as per NPCC demand after restoration of full HBTU gas quota by SNGPL.
| 2019-03-15 | Plant remained shutdown and in standby mode from 0000~2400 hrs as per NPCC demand.
| 2019-03-16 | Plant remained shutdown and in standby mode from 0000~2400 hrs as per NPCC demand.
| 2019-03-17 | Plant remained shutdown and in standby mode from 0000~2400 hrs as per NPCC demand.
| 2019-03-18 | Plant remained shutdown and in standby mode from 0000~2400 hrs as per NPCC demand.
| 2019-03-19 | FKPCL complex remained shutdown and in standby mode from 0000 ~ 0800 hrs as per NPCC demand and remained shutdown from 0800 ~ 2400 hrs for "Scheduled Outage of 2019".
| 2019-03-20 | FKPCL complex remained shutdown from 0000 ~ 2400 hrs for "Scheduled Outage of 2019".
| 2019-03-21 | FKPCL complex remained shutdown from 0000 ~ 2400 hrs for "Scheduled Outage of 2019".
| 2019-03-22 | FKPCL complex remained shutdown from 0000 ~ 2400 hrs for "Scheduled Outage of 2019".
| 2019-03-23 | FKPCL complex remained shutdown from 0000 ~ 2400 hrs for "Scheduled Outage of 2019".
| 2019-03-24 | FKPCL complex remained shutdown from 0000 ~ 2400 hrs for "Scheduled Outage of 2019".
| 2019-03-25 | FKPCL complex remained shutdown from 0000 ~ 2400 hrs for "Scheduled Outage of 2019".
| 2019-03-26 | FKPCL complex remained shutdown from 0000 ~ 2400 hrs for "Scheduled Outage of 2019".
| 2019-03-27 | FKPCL complex remained shutdown from 0000 ~ 2400 hrs for "Scheduled Outage of 2019".
| 2019-03-28 | Plant remained shutdown from 0000~ 2400hrs due to unavailability of HBTU gas by M/S SNGPL.
| 2019-03-29 | Plant remained shutdown from 0000~ 2400hrs due to unavailability of HBTU gas by M/S SNGPL.
| 2019-03-30 | Plant remained shutdown from 0000~ 2400hrs due to unavailability of HBTU gas by M/S SNGPL.
| 2019-03-31 | Plant remained shutdown from 0000~ 2400hrs due to unavailability of HBTU gas by M/S SNGPL.

## April
Monthly Operational Returns Kabirwala
2019-04-01
| Date | Site Avg. Ambient Temp.F | Site Avg. Relative Humidty % | Site Avg. Ambient Wetbulb Temp.F | Site Ambient Temp |  | Base load hours |  |  |  | Standby hours |  |  |  | Plant ambient corrected Max Load |  | Corrected Plant Capacity | Ambient Corrected Daclared Avail'y (MWH) | Plant WAPDA Dispatch (MWH) | Net Plant Export (MWH) | Gross Generation | CT1 Average Cap (MW) | CT1 Unavail minutes | CT2 Average Cap (MW) | CT2 Unavail minutes | ST Average Cap (MW) | ST Unavail minutes | Plant Aux Load including Colony Load MWH | Differenece (+/-) MW | Maximum Daily Generation | Daily Load Factor | Avg. Corrected Plant Capacity | Plant Capacity Factor | Plant Availability Factor | Equivalent Plant Availability | LBtu gas flow (mmscf/day) | 1 LBtu gas (Average Btu/scf) | LBTU MMBTU | 1 HBtu gas flow (mmscf/day) | 1 HBtu gas (Average Btu/scf) | HBTU MMBTU | HHV Net Heat Rate (Btu/Kwh) | Avg. declared availability | CT1 Derated MW | CT1 derated mintutes | CT-2 derated MW | CT-2 derated mintutes | ST derated MW | ST derated mintutes | WAPDA Backfeed (MWH) | CT-1 Gross Generation (MWH) | CT-2 Gross Generation (MWH) | STG Gross Generation (MWH) | CT-1 & CT-2 MWH difference | Base load Heat Rate | STG load | DB1 | DB2 | CT1 | CT1 Gas flow | CT2 Gas flow |  | Pamb | Freq. Hz | LBTU Gas Specific gravity | CT-1 compressor efficiency(%) | CT-2 compressor efficiency(%) |  | CT-1 Heat Rate (Btu/Kwh) | CT-2 Heat Rate (Btu/Kwh) |  | DB(1+2) | DB-1 Ops Hours | DB-2 Ops Hours | CT-1 Wetcomprssion Ops Hours | RO Operation Hours | CT1 T/G Brg |  | CT2 T/G Brg
[7 empty] | CT1 |  | CT2 |  | CT1 |  | CT2 | [43 empty] | mmscf/d | mmscf/d | WetC flow | HBTU KPPH | HBTU KPPH | LBTU KPPH | mbar | Hz | [7 empty] | mmscf/d |  |  |  |  | Supply air pressure | Seal air pressure | Supply air pressure | Seal air pressure
[5 empty] | Max | Min | hrs | min | hrs | min | hrs | min | hrs | min | hrs | min | [42 empty] | gpm | [17 empty] | Psi | "WC | Psi | "WC
Week 13 | 2019-03-26 | 76.4 | 57.7% | 62 | 90 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3627 | 0 | 0 | 0 | 0 | 43 | 1440 | 47 | 1440 | 60 | 1440 | 5 | 0 | 0 | 0% | 151.125 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 997 | 49.98 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-03-27 | 79.5 | 52.8% | 62.3 | 93 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3600 | 0 | 0 | 0 | 0 | 43 | 1440 | 47 | 1440 | 60 | 1440 | 5 | 0 | 0 | 0% | 150 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 997 | 50.02 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-03-28 | 79.7 | 57.2% | 64 | 91 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3601 | 3638 | 3638 | 0 | 0 | 43 | 0 | 47 | 0 | 60 | 0 | 6 | -3638 | 0 | 0% | 150.0417 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | no data | 151.5833 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 995 | 50.07 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-03-29 | 81.6 | 60.7% | 67.7 | 98 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3581 | 3620 | 3620 | 0 | 0 | 43 | 0 | 47 | 0 | 60 | 0 | 6 | -3620 | 0 | no data | 149.2083 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 150.8333 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 992.7 | 50.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 | 0
| 2019-03-30 | 81.6 | 51.5% | 63.8 | 100 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3582 | 3579 | 3579 | 0 | 0 | 43 | 0 | 47 | 0 | 60 | 0 | 4 | -3579 | 0 | no data | 149.25 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 149.125 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 993.3 | 50.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-03-31 | 77.5 | 44.3% | 57.4 | 93 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3619 | 3567 | 3567 | 0 | 0 | 43 | 0 | 47 | 0 | 60 | 0 | 4 | -3567 | 0 | no data | 150.7917 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 148.625 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 994.8 | 50.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-04-01 | 79 | 47.1% | 59.4 | 93 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3605 | 3550 | 3550 | 0 | 0 | 43 | 0 | 47 | 0 | 60 | 0 | 6 | -3550 | 0 | no data | 150.2083 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 147.9167 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 994 | 50.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Week 14 | 2019-04-02 | 80.9 | 45.4% | 60.4 | 96 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3581 | 2736 | 3526 | 83 | 92 | 43 | 239 | 47 | 337 | 60 | 420 | 9 | -3443 | 29 | 13.22% | 149.2083 | 2.318% | 76.24% | 72.92% | 0.104 | 171.84 | 17.8714 | 1.408 | 1005 | 1415.04 | 17263.9923 | 114 | 25 | 181 | 32 | 83 | 0 | 0 | 9 | 68 | 24 | 0 | 44 | 17263.9923 | 0 | 0 | 0 | 0 | 15.29 | 11.52 | 0 | 993 | 50.02 | 0.9229 | 87.86 | 85.5 | 2.36 | 14848 | 10864 | -3984 | 0 | 0 | 0 | 0 | 1.8 | 2 | 4.5 | 0 | 0
| 2019-04-03 | 82.5 | 62.6% | 48.9 | 98 | 71 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3567 | 1680 | 3514 | 1646 | 1716 | 43 | 0 | 47 | 1440 | 60 | 42 | 70 | -1868 | 76 | 94.08% | 148.625 | 46.15% | 67.5% | 46.92% | 0 | 0 | 0 | 14.747 | 995.9992 | 14688 | 8923.4508 | 70 | 0 | 0 | 0 | 0 | 31.8 | 1398 | 0 | 1040 | 0 | 676 | 0 | 8923.4508 | 28.1667 | 2.432 | 0 | 0 | 24.2 | 0 | 0 | 992 | 50.06 | 0 | 87.35 | 0 | 87.35 | 10946 | 0 | -10946 | 2.432 | 22.1 | 0 | 0 | 3.9 | 2 | 4.5 | 0 | 0
| 2019-04-04 | 83.95 | 50.33% | 64.76 | 96 | 71 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3551 | 1656 | 3519 | 1637 | 1708 | 43 | 0 | 47 | 1440 | 60 | 0 | 71 | -1882 | 75 | 94.89% | 147.9583 | 46.1% | 68.67% | 47.33% | 0 | 0 | 0 | 14.529 | 1008.1905 | 14648 | 8948.0757 | 69 | 0 | 0 | 0 | 0 | 32 | 1440 | 0 | 1031 | 0 | 677 | 0 | 8948.0757 | 28.2083 | 2.147 | 0 | 0 | 24.26 | 0 | 0 | 992.38 | 50.04 | 0 | 87.15 | 0 | 87.15 | 11057 | 0 | -11057 | 2.147 | 24 | 0 | 0 | 0 | 2.1 | 4.5 | 0 | 0
| 2019-04-05 | 85.9 | 51.9% | 66.6 | 99 | 72 | 24 | 0 | 14 | 8 | 0 | 0 | 0 | 0 | 13 | 45 | 3537 | 2707 | 2707 | 2663 | 2758 | 42 | 0 | 42 | 508 | 61 | 0 | 95 | -44 | 149 | 77.13% | 147.375 | 75.29% | 89.78% | 78.47% | 2.42 | 133.02 | 321.9084 | 23.348 | 1006.1247 | 23491 | 8942.1361 | 112.7917 | 0 | 0 | 25 | 84 | 35 | 615 | 0 | 1015 | 615 | 1128 | -400 | 8942.1361 | 47 | 2.179 | 1.44 | 0 | 24.12 | 13.03 | 9.75 | 991.8 | 50.05 | 0.9351 | 87.09 | 86.73 | 0.36 | 11155 | 11160 | 5 | 3.619 | 24 | 14.08 | 0 | 5.62 | 2.2 | 4.5 | 2.1 | 0
| 2019-04-06 | 87.2 | 51.5% | 67.6 | 100 | 75 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3520 | 3467 | 3467 | 3397 | 3506 | 42 | 0 | 42 | 0 | 62 | 0 | 109 | -70 | 148 | 98.7% | 146.6667 | 96.51% | 100% | 100% | 5.1 | 129.38 | 659.838 | 28.935 | 1006.048 | 29110 | 8763.5673 | 144.4583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1005 | 1009 | 1492 | 4 | 8763.5673 | 62.1667 | 2.44 | 2.467 | 0 | 23.93 | 19.96 | 19.77 | 990.67 | 49.99 | 0.9365 | 87.05 | 86.75 | 0.3 | 11172 | 11018 | -154 | 0 | 24 | 24 | 0 | 0 | 2.1 | 4.5 | 2.1 | 0
| 2019-04-07 | 86 | 53% | 67 | 99 | 76 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3542 | 3477 | 3477 | 3409 | 3516 | 42 | 0 | 42 | 0 | 62 | 0 | 107 | -68 | 150 | 97.67% | 147.5833 | 96.25% | 100% | 100% | 5.987 | 135.63 | 812.0168 | 28.818 | 1010.4102 | 29118 | 8779.7057 | 144.875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1008 | 1014 | 1494 | 6 | 8779.7057 | 62.25 | 2.526 | 2.425 | 0 | 23.97 | 19.92 | 20.35 | 989 | 50.07 | 0.9355 | 86.95 | 86.77 | 0.18 | 11174 | 11002 | -172 | 0 | 24 | 24 | 0 | 0 | 2.1 | 4.5 | 2.1 | -0.4
| 2019-04-08 | 83.2 | 52% | 65 | 95 | 70 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3562 | 3518 | 3518 | 3448 | 3557 | 42 | 0 | 43 | 0 | 63 | 0 | 109 | -70 | 151 | 98.15% | 148.4167 | 96.8% | 100% | 100% | 6.92 | 138.81 | 960.5652 | 28.987 | 1007.91 | 29216.2872 | 8751.9873 | 146.5833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1023 | 1027 | 1507 | 4 | 8751.9873 | 62.7917 | 2.507 | 2.4111 | 0 | 24.24 | 20.06 | 20.98 | 990.9 | 50.06 | 0.9342 | 86.86 | 86.61 | 0.25 | 11128 | 10961 | -167 | 0 | 24 | 24 | 0 | 6.4 | 2.1 | 4.5 | 2.1 | -0.6
Week 15 | 2019-04-09 | 85 | 53% | 67 | 98 | 73 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 22 | 42 | 3549 | 3494 | 3464 | 3394 | 3499 | 42 | 0 | 42 | 0 | 62 | 0 | 105 | -70 | 150 | 97.19% | 147.875 | 95.63% | 100% | 99.41% | 7.8 | 139.61 | 1088.958 | 28.5312 | 1007.8675 | 28755.65 | 8793.3435 | 145.5833 | 0 | 0 | 0 | 0 | 16 | 78 | 0 | 1009 | 1016 | 1474 | 7 | 8793.3435 | 61.4167 | 2.297 | 2.219 | 0 | 24.07 | 19.9 | 21.01 | 990.4 | 50.07 | 0.9341 | 86.85 | 86.71 | 0.14 | 11188 | 11013 | -175 | 0 | 24 | 24 | 0 | 0 | 2.2 | 4.7 | 2.1 | -0.5
| 2019-04-10 | 83.3 | 53.8% | 66.6 | 94 | 72 | 18 | 32 | 24 | 0 | 4 | 45 | 0 | 0 | 18 | 25 | 3563 | 3503 | 3088 | 3047 | 3140 | 43 | 0 | 43 | 0 | 63 | 0 | 93 | -41 | 150 | 87.22% | 148.4583 | 85.52% | 100% | 94.35% | 7.79 | 137.11 | 1068.0869 | 25.7489 | 1006.4608 | 25915.3 | 8855.7226 | 145.9583 | 17 | 43 | 0 | 0 | 34 | 335 | 0 | 793 | 1023 | 1324 | 230 | 8855.7226 | 55.1667 | 2 | 2.371 | 0 | 19.28 | 20.06 | 20.9 | 993.54 | 50.06 | 0.9354 | 87.22 | 86.71 | 0.51 | 11351 | 11027 | -324 | 0 | 18.6 | 24 | 0 | 4.3 | 2.1 | 4 | 2.1 | -0.8
| 2019-04-11 | 84.2 | 51.5% | 65.5 | 97 | 73 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3556 | 3479 | 3479 | 3423 | 3524 | 42 | 0 | 43 | 0 | 62 | 0 | 101 | -56 | 150 | 97.89% | 148.1667 | 96.26% | 100% | 100% | 7.795 | 136.14 | 1061.2113 | 28.7611 | 1006.6986 | 28953.78 | 8768.6215 | 144.9583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1004 | 1027 | 1493 | 23 | 8768.6215 | 62.2083 | 2.442 | 2.328 | 0 | 24.21 | 20.1 | 20.67 | 993.33 | 50.11 | 0.9356 | 87.13 | 86.66 | 0.47 | 11344 | 10985 | -359 | 0 | 24 | 24 | 0 | 0 | 2.1 | 3.8 | 2.1 | -0.8
| 2019-04-12 | 81.3 | 58.7% | 67.2 | 92 | 70 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3582 | 3478 | 3478 | 3414 | 3506 | 42 | 0 | 43 | 0 | 62 | 0 | 92 | -64 | 149 | 98.04% | 149.25 | 95.31% | 100% | 100% | 7.84 | 137.29 | 1076.3536 | 29.0033 | 997.0824 | 28918.68 | 8785.8915 | 144.9167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1005 | 1025 | 1476 | 20 | 8785.8915 | 61.5 | 2.358 | 2.318 | 0 | 24.44 | 19.97 | 21.47 | 994.04 | 50.08 | 0.9351 | 87.16 | 86.76 | 0.4 | 11418 | 10978 | -440 | 0 | 24 | 24 | 0 | 6.1 | 2.1 | 3.9 | 2.1 | -0.8
| 2019-04-13 | 80.3 | 61.3% | 67.7 | 91 | 70 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3595 | 3472 | 3472 | 3401 | 3499 | 42 | 0 | 43 | 0 | 61 | 0 | 98 | -71 | 149 | 97.85% | 149.7917 | 94.6% | 100% | 100% | 7.774 | 135.66 | 1054.6208 | 29.0363 | 989.5352 | 28732.48 | 8758.336 | 144.6667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1008 | 1027 | 1464 | 19 | 8758.336 | 61 | 2.293 | 2.234 | 0 | 24.5 | 20.12 | 21.43 | 995 | 50.1 | 0.935 | 87.13 | 86.79 |  | 11420 | 11017 | -403 | 0 | 24 | 24 | 0 | 2.9 | 2.1 | 4 | 2.1 | -0.8
| 2019-04-14 | 82.8 | 58.7% | 69 | 94 | 72 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3570 | 3038 | 3038 | 2973 | 3058 | 42 | 0 | 43 | 0 | 61 | 0 | 85 | -65 | 130 | 98.01% | 148.75 | 83.28% | 100% | 87.67% | 7.856 | 142.43 | 1118.9301 | 24.2906 | 989.4412 | 24034.14 | 8460.5012 | 126.5833 | 0 | 0 | 0 | 0 | 18 | 1440 | 0 | 1000 | 1020 | 1038 | 20 | 8460.5012 | 43.25 | 0 | 0 | 0 | 24.35 | 20.21 | 21.01 | 995 | 50.04 | 0.9334 | 87.14 | 86.76 |  | 11436 | 11109 | -327 | 0 | 0 | 0 | 0 | 0 | 2.1 | 4.5 | 2.1 | -0.8
| 2019-04-15 | 77.22 | 62.42% | 65.27 | 93.3 | 67.9 | 20 | 20 | 24 | 0 | 3 | 19 | 0 | 0 | 9 | 7 | 3622 | 3294 | 3006 | 2956 | 3039 | 42 | 0 | 43 | 0 | 61 | 0 | 83 | -50 | 146 | 86.73% | 150.9167 | 81.61% | 100% | 83.34% | 7.981 | 135.69 | 1082.9419 | 24.5501 | 990.3104 | 24312.19 | 8591.046 | 137.25 | 9 | 21 | 0 | 0 | 39 | 893 | 0 | 872 | 1039 | 1128 | 167 | 8591.046 | 47 | 0.846 | 0.804 | 0 | 24.65 | 20.59 | 21.09 | 993.3 | 50.15 | 0.936 | 87.04 | 86.77 |  | 11375 | 11073 | -302 | 0 | 9.2 | 13 | 0 | 4.1 | 2.1 | 4.9 | 2.1 | 0.9
Week 16 | 2019-04-16 | 71.87 | 74.73% | 65.58 | 85.81 | 65.15 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 3671 | 3506 | 1504 | 1504 | 1565 | 43 | 0 | 44 | 0 | 61 | 0 | 61 | 0 | 66 | 98.8% | 152.9583 | 40.97% | 100% | 73.65% | 7.792 | 138.89 | 1082.2309 | 12.2376 | 990.7614 | 12124.5683 | 8781.1165 | 146.0833 | 0 | 0 | 0 | 0 | 39 | 1440 | 0 | 0 | 1047 | 518 | 1047 | 8781.1165 | 21.5833 | 0 | 0.223 | 0 | 0 | 20.56 | 21.01 | 991.04 | 50.15 | 0.9349 | 0 | 86.89 |  | 0 | 10960 | 10960 | 0.223 | 0 | 24 | 0 | 0.6 | 0 | 0 | 2.1 | -0.9
| 2019-04-17 | 69.06 | 75.5% | 64.11 | 74.4 | 64.2 | 10 | 48 | 24 | 0 | 12 | 20 | 0 | 0 | 10 | 40 | 3693 | 3554 | 2433 | 2403 | 2484 | 44 | 0 | 44 | 0 | 61 | 0 | 81 | -30 | 149 | 69.46% | 153.875 | 65.07% | 100% | 85.27% | 7.726 | 136.47 | 1054.3672 | 20.1664 | 989.2937 | 19950.4849 | 8741.0953 | 148.0833 | 23 | 52 | 0 | 0 | 38 | 800 | 0 | 494 | 1055 | 935 | 561 | 8741.0953 | 38.9583 | 0.869 | 1.044 | 0 | 25.15 | 20.94 | 21.21 | 995.42 | 50.07 | 0.9352 | 87.66 | 86.86 |  | 11229 | 11055 | -174 | 1.913 | 11.0833 | 24 | 0 | 0 | 2.1 | 4.7 | 2.1 | -1
| 2019-04-18 | 73.9 | 65.1% | 63.3 | 84 | 63 | 19 | 6 | 24 | 0 | 3 | 58 | 0 | 0 | 0 | 0 | 3649 | 3226 | 2825 | 2782 | 2861 | 44 | 0 | 44 | 0 | 61 | 0 | 79 | -43 | 134 | 88.96% | 152.0417 | 76.24% | 100% | 85.38% | 7.848 | 133.85 | 1050.4548 | 23.1884 | 984.3747 | 22826.0881 | 8582.51 | 134.4167 | 20 | 56 | 0 | 0 | 21 | 1440 | 0 | 854 | 1055 | 952 | 201 | 8582.51 | 39.6667 | 0 | 0.067 | 0 | 25.5 | 21.35 | 21.1 | 997.7 | 50.1 | 0.936 | 87.64 | 86.8 |  | 11843 | 11494 | -349 | 0.067 | 0 | 8.45 | 0 | 5.97 | 2.1 | 4.8 | 2.1 | -1
| 2019-04-19 | 80 | 54% | 64 | 92 | 66 | 8 | 9 | 13 | 15 | 15 | 13 | 10 | 28 | 0 | 0 | 3597 | 3151 | 1402 | 1377 | 1418 | 43 | 0 | 44 | 0 | 61 | 0 | 50 | -25 | 132 | 44.76% | 149.875 | 38.28% | 100% | 92.15% | 4.321 | 131.09 | 566.4399 | 11.3733 | 982.9985 | 11179.9095 | 8530.3917 | 131.2917 | 19 | 38 | 18 | 17 | 25 | 628 | 9 | 368 | 586 | 464 | 218 | 8530.3917 | 19.3333 | 0 | 0 | 0 | 9 | 11.76 | 11.8 | 993.9 | 50.04 | 0.9369 | 87.37 | 86.78 |  | 11303 | 11134 |  | 0 | 0 | 0 | 0 | 0 | 2.1 | 4.8 | 2.2 | -0.9
| 2019-04-20 | 84 | 49% | 64 | 97 | 72 | 4 | 12 | 4 | 44 | 19 | 2 | 15 | 46 | 0 | 0 | 3553 | 3271 | 674 | 661 | 686 | 42 | 0 | 43 | 0 | 61 | 0 | 35 | -13 | 127 | 22.51% | 148.0417 | 18.6% | 100% | 94.78% | 2.682 | 152.45 | 408.8709 | 5.9445 | 996.6952 | 5924.8224 | 9581.9868 | 136.2917 | 21 | 46 | 18 | 210 | 20 | 311 | 10 | 193 | 298 | 195 | 105 | 9581.9868 | 8.125 | 0 | 0 | 0 | 4.8 | 6.2 | 6.63 | 990.3 | 50.04 | 0.9314 | 87.3 | 86.97 |  | 11194 | 10890 |  | 0 | 0 | 0 | 0 | 7.2 | 2 | 4.8 | 2.1 | -0.8
| 2019-04-21 | 87.1 | 48% | 66 | 99 | 75 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3525 | 3524 | 0 | 0 | 0 | 42 | 0 | 43 | 0 | 60 | 0 | 14 | 0 | 0 | no data | 146.875 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 146.8333 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 989.4 | 50.07 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-04-22 | 91.4 | 43.6% | 67 | 106 | 77 | 12 | 2 | 13 | 25 | 11 | 25 | 9 | 14 | 0 | 0 | 3480 | 3244 | 1615 | 1584 | 1637 | 42 | 0 | 43 | 0 | 60 | 0 | 58 | -31 | 129 | 52.87% | 145 | 45.52% | 100% | 92.27% | 4.616 | 144 | 664.704 | 13.1482 | 1006.5121 | 13233.8336 | 8774.3293 | 135.1667 | 25 | 33 | 17 | 81 | 18 | 774 | 5 | 510 | 605 | 522 | 95 | 8774.3293 | 21.75 | 0 | 0 | 0 | 12.34 | 12.03 | 12.1 | 988.96 | 50.12 | 0.9339 | 87.21 | 87.01 |  | 11187 | 10954 |  | 0 | 0 | 0 | 0 | 0 | 2.2 | 4.9 | 2.1 | -0.8
Week 17 | 2019-04-23 | 92.3 | 45% | 67.6 | 105 | 79 | 14 | 23 | 24 | 0 | 8 | 42 | 0 | 0 | 0 | 0 | 3475 | 3157 | 2393 | 2369 | 2447 | 42 | 0 | 43 | 0 | 60 | 0 | 78 | -24 | 128 | 79.65% | 144.7917 | 68.17% | 100% | 80.85% | 7.969 | 134.89 | 1074.9384 | 19.1917 | 1009.2608 | 19369.465 | 8629.9719 | 131.5417 | 20 | 55 | 0 | 0 | 27 | 1440 | 0 | 613 | 1019 | 815 | 406 | 8629.9719 | 33.9583 | 0 | 0 | 0 | 14.85 | 19.8 | 20.6 | 988.54 | 50.1 | 0.9364 | 86.86 | 86.93 |  | 11245 | 10927 |  | 0 | 0 | 0 | 0 | 4.83 | 2.1 | 4.9 | 2.1 | -0.9
| 2019-04-24 | 84.3 | 51.5% | 66 | 92 | 77 | 15 | 14 | 24 | 0 | 7 | 51 | 0 | 0 | 0 | 0 | 3559 | 3183 | 2459 | 2424 | 2502 | 42 | 0 | 43 | 0 | 60 | 0 | 78 | -35 | 129 | 80.81% | 148.2917 | 68.11% | 100% | 81.84% | 7.919 | 131.33 | 1040.0023 | 19.68 | 1000.662 | 19693.0282 | 8553.2304 | 132.625 | 18 | 26 | 0 | 0 | 26 | 1440 | 0 | 648 | 1027 | 827 | 379 | 8553.2304 | 34.4583 | 0 | 0 | 0 | 15.63 | 20.16 | 20.79 | 993 | 50.07 | 0.9371 | 87.08 | 87.04 |  | 11248 | 11012 |  | 0 | 0 | 0 | 0 | 1.15 | 2.1 | 4.9 | 2.1 | -0.9
| 2019-04-25 | 82.7 | 56% | 66.8 | 96 | 72 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3571 | 3049 | 3049 | 2985 | 3071 | 42 | 0 | 43 | 0 | 60 | 0 | 86 | -64 | 130 | 98.43% | 148.7917 | 83.59% | 100% | 88.28% | 7.904 | 136.78 | 1081.1091 | 24.109 | 1001.42 | 24143.2348 | 8450.3665 | 127.0417 | 0 | 0 | 0 | 0 | 17 | 1440 | 0 | 1011 | 1027 | 1033 | 16 | 8450.3665 | 43.0417 | 0 | 0 | 0 | 24.23 | 20.12 | 20.99 | 993 | 50.04 | 0.9352 | 87.25 | 87.05 |  | 11261 | 10993 |  | 0 | 0 | 0 | 0 | 4 | 2.2 | 4.8 | 2.1 | -0.9
| 2019-04-26 | 86.6 | 51% | 67.7 | 100 | 72 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3530 | 3035 | 3035 | 2978 | 3063 | 42 | 0 | 43 | 0 | 60 | 0 | 85 | -57 | 129 | 98.93% | 147.0833 | 84.36% | 100% | 88.28% | 7.768 | 135.28 | 1050.855 | 23.961 | 1004.8829 | 24078 | 8438.1649 | 126.4583 | 0 | 0 | 0 | 0 | 17 | 1440 | 0 | 1007 | 1025 | 1031 | 18 | 8438.1649 | 42.9583 | 0 | 0 | 0 | 24.12 | 20.07 | 20.49 | 993 | 50.09 | 0.9362 | 87.16 | 86.98 |  | 11254 | 10989 |  | 0 | 0 | 0 | 0 | 3.94 | 2.1 | 4.7 | 2.1 | -0.8
| 2019-04-27 | 90.7 | 43.1% | 66.6 | 103 | 78 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3494 | 3017 | 3017 | 2961 | 3044 | 42 | 0 | 42 | 0 | 60 | 0 | 83 | -56 | 128 | 99.09% | 145.5833 | 84.75% | 100% | 88.19% | 7.805 | 137.59 | 1073.8899 | 23.906 | 1004.392 | 24010.9952 | 8471.7613 | 125.7083 | 0 | 0 | 0 | 0 | 17 | 1440 | 0 | 999 | 1018 | 1027 | 19 | 8471.7613 | 42.7917 | 0 | 0 | 0 | 24.06 | 19.98 | 20.3 | 991.8 | 50.03 | 0.9355 | 86.94 | 86.94 |  | 11317 | 11006 |  | 0 | 0 | 0 | 0 | 0.38 | 2.2 | 4.8 | 2.1 | -0.8
| 2019-04-28 | 91.7 | 39.93% | 65.8 | 104 | 77 | 22 | 7 | 24 | 0 | 1 | 37 | 0 | 0 | 0 | 0 | 3482 | 2912 | 2912 | 2856 | 2936 | 42 | 0 | 43 | 0 | 60 | 0 | 80 | -56 | 129 | 94.83% | 145.0833 | 82.02% | 100% | 86.77% | 7.934 | 134.16 | 1064.4254 | 23.092 | 1002.252 | 23144.0032 | 8476.3406 | 121.3333 | 17 | 16 | 0 | 0 | 19 | 1440 | 0 | 926 | 1019 | 991 | 93 | 8476.3406 | 41.2917 | 0 | 0 | 0 | 22.36 | 20.05 | 20.19 | 990.17 | 50.06 | 0.9367 | 86.82 | 86.88 |  | 11318 | 10998 |  | 0 | 0 | 0 | 0 | 1.05 | 2.2 | 4.8 | 2.1 | -1
| 2019-04-29 | 91.9 | 38.9% | 65.5 | 105 | 77 | 16 | 18 | 24 | 0 | 6 | 58 | 0 | 0 | 0 | 0 | 3479 | 3210 | 2525 | 2480 | 2559 | 42 | 0 | 43 | 0 | 60 | 0 | 79 | -45 | 129 | 82.66% | 144.9583 | 71.28% | 100% | 82.3% | 7.851 | 133.61 | 1048.9721 | 20.179 | 1001.98 | 20218.9544 | 8575.7768 | 133.75 | 22 | 44 | 0 | 0 | 25 | 1440 | 0 | 689 | 1020 | 850 | 331 | 8575.7768 | 35.4167 | 0 | 0 | 0 | 16.78 | 19.971 | 20.33 | 987.5 | 50.08 | 0.9367 | 86.76 | 86.85 |  | 11324 | 10983 |  | 0 | 0 | 0 | 0 | 4.2 | 2.2 | 4.8 | 2.1 | -0.8
Week 18 | 2019-04-30 | 88.9 | 38.6% | 64.3 | 98 | 80 | 0 | 0 | 21 | 3 | 24 | 0 | 2 | 42 | 0 | 0 | 3513 | 3454 | 1284 | 1271 | 1326 | 42 | 0 | 43 | 0 | 60 | 0 | 58 | -13 | 64 | 86.33% | 146.375 | 36.18% | 100% | 75.41% | 7.07 | 137.99 | 975.5893 | 9.98 | 1000.66 | 9986.5868 | 8624.8435 | 143.9167 | 0 | 0 | 18 | 15 | 40 | 1277 | 3 | 0 | 902 | 424 | 902 | 8624.8435 | 17.6667 | 0 | 0 | 0 | 0 | 17.71 | 17.96 | 986.5 | 50.09 | 0.935 | 0 | 86.85 |  | 0 | 10977 |  | 0 | 0 | 0 | 0 | 5.22 | 0 | 0 | 2.1 | -0.8
| 2019-05-01 | [26 empty] | 0 | 0 |  | no data | no data | no data | #DIV/0! | no data |  |  | 0 |  |  | 0 | no data | 0 | [11 empty] | no data
| 2019-05-02 | [26 empty] | 0 | 0 |  | no data | no data | no data | #DIV/0! | no data |  |  | 0 |  |  | 0 | no data | 0 | [11 empty] | no data
| 2019-05-03 | [26 empty] | 0 | 0 |  | no data | no data | no data | #DIV/0! | no data |  |  | 0 |  |  | 0 | no data | 0 | [11 empty] | no data
| 2019-05-04 | [26 empty] | 0 | 0 |  | no data | no data | no data | #DIV/0! | no data |  |  | 0 |  |  | 0 | no data | 0 | [11 empty] | no data
| 2019-05-05 | [26 empty] | 0 | 0 |  | no data | no data | no data | #DIV/0! | no data |  |  | 0 |  |  | 0 | no data | 0 | [11 empty] | no data
| 2019-05-06 | [26 empty] | 0 | 0 |  | no data | no data | no data | #DIV/0! | no data |  |  | 0 |  |  | 0 | no data | 0 | [11 empty] | no data | 0 | [15 empty] | 0
| Monthly | 83.64 | 52.63% | 64.8265 | 95.8837 | 72.0417 | 497 | 11 | 546 | 35 | 167 | 10 | 62 | 10 | 218 | 39 | 106773 | 95042 | 81430 | 69522.83 | 71717 | 42.4242 | 239 | 43.8182 | 3725 | 60.7576 | 462 | 2264.17 | -22670 | 106.2121 | 0.83388 | 148.2958 | 65.11% | #DIV/0! | 85.92% | 172.572 | 119.6997 | 23560.1517 | 580.8507 | 933.4408 | 581192.5215 | 8698.6199 |  | 236 | 611 | 128 | 490 | 554.8 | 22949 | 70 | 21193 | 23569 | 26955 | 2376 | 8698.6199 | 1123.125 | 27.336 | 22.3511 | 0 | 544.33 | 476.141 | 473.93 | 992.1027 | 50.0706 | 0.73654 | 68.6676 | 68.3742 |  | 8991.9697 | 8684.2121 |  | 10.401 | 276.9833 | 275.53 | 0 | 74.16
| Totals | Avg.F | % Avg. |  | M Avg | m Avg | hrs | min | hrs | min | hrs | min | hrs | min | Avg Int Avi | Avg Ext Avi | MWhr Total | MWhr Total | MWhr Total | MWhr Total | MWhr Total | MW Avg | Total min | Avg MW | Total min | Avg MW | Total min | MWhr | Total MW | Av Max D/Gen | Av. DailyLF | Avg. | Avg. |  | Avg. | Total | Avg. |  | Total | Avg. |  | Avg. | [7 empty] | Total |  |  |  |  | Avg.
| Weeks data | Site Avg. Amb. Temp F | Site Avg. Relative humidity % | Site Avg. Ambient Wetbulb Temp.F | M Avg: Site Maximum/Minumum Temperature; hrs: CT-1 Base Load Hours; hrs: CT-2 Base Load Hours; hrs: CT-1 stand by hours / min; hrs: CT-2 standby hours / min | Plant ambient Corrected maximum Load hours/min |  | Average Corrected Plant Capacity | Ambient Corrected Declared Avail'y (MWH) | Av Plant WAPDA Dispatch | Net Plant Export (MWH) | Gross Generation | CT1 Av Cap (MW) | CT1 Unavail minutes | CT2 Av Cap (MW) | CT2 Unavail minutes | ST Unavail minutes | ST Average Cap (MW) | Plant Aux Load including Colony Load MWH | Differenece (+/-) MW | Maximum Daily Generation | Daily Load Factor | Avg. Corrected Plant | Plant Capacity Facto | Plant Availability Factor | Equivalent Plant Availability | LBtu gas flow mmscf | 1 LBtu gas (Average Btu/scf) | LBTU MMBTU | PL gas flow (mscf/week) | 1 PL gas (Average Btu/scf) | HBTU MMBTU | Plant Net Heat Rate (Btu/Kwh) | [11 empty] | 271.25
| Week 13 | 79.3286 | 53.04% | 62.3714 | 94 | 66.2857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3602.1429 | no data | no data | no data | no data | 43 | 2880 | 47 | 2880 | 420 | 411.4286 | 36 | no data | no data | no data | 150.0893 | no data | no data | no data | no data | no data | #VALUE! | no data | no data | #VALUE! | #DIV/0!
| Week 14 | 84.2357 | 52.39% | 0 | 97.5714 | 71.5714 | 144 | -1 | 86 | 8 | 0 | 0 | 0 | -60 | 85 | 0 | 3551.4286 | 2748.7143 | 3389.7143 | 16283 | 16853 | 42.4286 | 239 | 310 | 532.1429 | 428 | 66 | 570 | -7445 | 111.1429 | 81.98% | 147.9762 | 65.63% | 86.03% | 77.95% | 20.531 | 101.24 | 2078.5584 | 140.772 | 1005.6689 | 141570.0289 | 10053.2736 | [5 empty] | 0.27381
| Week 15 | 82.0171 | 57.06% | 66.8957 | 94.1857 | 71.1286 | 158 | 52 | 168 | 0 | 8 | 4 | 0 | 0 | 122 | 14 | 3576.7143 | 3394 | 3289.2857 | 22608 | 23265 | 42.1429 | No outage | 300 | no data | 432 | no data | 657 | -417 | 146.2857 | 94.71% | 149.0298 | 90.32% | 100% | 94.97% | 54.836 | 137.7043 | 7551.1522 | 165.3715 | 999.5143 | 165291.1786 | 8716.2089 | [5 empty] | 0.26672
| Week 16 | 79.6186 | 58.56% | 66.8957 | 91.1729 | 68.9071 | 54 | 17 | 103 | 24 | 109 | 58 | 59 | 28 | 10 | 40 | 3595.4286 | 3353.7143 | 1493.2857 | 10311 | 10651 | 42.8571 | No outage | 305 | no data | 425 | no data | 378 | no data | 105.2857 | 62.89% | 149.8095 | 47.45% | 100% | 87.25% | 34.985 | 119.5357 | 4181.957 | 86.0584 | 850.0908 | 73157.4403 | 8831.9049
| Week 17 | 82.5371 | 54.31% | 66.6929 | 93.9143 | 70.8857 | 68 | 40 | 103 | 24 | 94 | 40 | 59 | 28 | 10 | 40 | 3567.4286 | 3303.8571 | 1620.2857 | 11176 | 11533 | 42.7143 | No outage | 304 | no data | 424 | no data | 395 | -166 | 114.1429 | 59.7% | 148.6429 | 51.98% | 100% | 88.45% | 35.162 | 118.9643 | 4183.0222 | 93.0125 | 852.7336 | 79314.8736 | 8806.7142
| Week 18 | 88.9 | 0.386 | 64.3 | 98 | 80 | 0 | 0 | 21 | 3 | 24 | 0 | 2 | 42 | 0 | 0 | 3513 | 3454 | 1284 | 1271 | 1326 | 42 | #REF! | #REF! | no data | #REF! | no data | 58 | -13 | 64 | 86.33% | 146.375 | 36.18% | #DIV/0! | 75.41% | 7.07 | 137.99 | 975.5893 | 9.98 | 1000.66 | 9986.5868 | 8624.8435
| Date | Plant Status Whether Normal Operation or Tripping (State full detail for trippings/return to normal).
| 2019-04-01 | Plant remained shutdown from 0000~ 2400hrs due to unavailability of HBTU gas by M/S SNGPL.
| 2019-04-02 | After restoration of HBTU gas quota at 1700 hrs by M/S SNGPL, CT2 synchronized @ 1749 hrs and tripped @ 1825 hrs again CT2 synchronized @ 1915 hrs and tripped @ 2002 hrs due to internal faults and CT-2 synchronized @ 2059 hrs.
| 2019-04-03 | Steam turbine Synch @ 0042 hrs, CT-1 was already on bar and CT-2 remained shutdown due to water carryover problem of LBTU gas.
| 2019-04-04 | Plant load restricted to 72~65 MW as CT-2 remained shutdown due to water carryover problem of LBTU gas.
| 2019-04-05 | CT-2 synch @ 0828 hrs after rectification of water carryover issue in LBTU gas.
| 2019-04-06 | Normal operation.Plant remained at maximum load from 0000 to 2400 hrs.
| 2019-04-07 | Normal operation.Plant remained at maximum load from 0000 to 2400 hrs.
| 2019-04-08 | Normal operation.Plant remained at maximum load from 0000 to 2400 hrs.
| 2019-04-09 | Plant load reduced to 127 MW from 2242 hrs as per NPCC demand.
| 2019-04-10 | CT-1 Desynch @ 0014 hrs against 70 MW WAPDA Despatch and CT-1 again Synch @ 0459 hrs against 149 MW (Max.) WAPDA Despatch.
| 2019-04-11 | Normal operation.Plant remained at maximum load from 0000 to 2400 hrs.
| 2019-04-12 | Normal operation.Plant remained at maximum load from 0000 to 2400 hrs.
| 2019-04-13 | Normal operation.Plant remained at maximum load from 0000 to 2400 hrs.
| 2019-04-14 | Plant load restricted 121~126 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2019-04-15 | Plant load increased from 123 to 141 MW by increasing duct burners firing at 1100 hrs to achieve maximum export. CT-1 de-synch @ 2041 hrs to achieve NPCC demand of 63 MW.
| 2019-04-16 | Plant load remained 61~64 MW due to shutdown of CT-1 at NPCC demand.
| 2019-04-17 | CT-1 synch @ 1220 hrs to achieve maximum load as per NPCC demand.
| 2019-04-18 | CT-1 de-synch @0054hrs & again synch @0425 hrs on NPCC demand. Plant load restricted 127~130 MW from 0425~2333hrs to remain within contractual heatrate.CT-1 again de-synch @ 2333 hrs to achieve NPCC demand of 45% of complex export.
| 2019-04-19 | CT-1 synch @ 0428 hrs as per NPCC demand. CT-1 de-synch @ 1315 hrs, CT-2 de-synch @ 1332 hrs and STG de-synch @ 1332 hrs and put on standby mode as per NPCC demand of 0 MW.
| 2019-04-20 | CT-2 synch @ 1204 hrs, STG synch @ 1505 hrs and CT-1 synch @ 1514hrs as per NPCC demand. CT-1 de-synch @ 2012 hrs, CT-2 de-synch @ 2018 hrs and STG de-synch @ 2016 hrs and put on standby mode as per NPCC demand of 0 MW.
| 2019-04-21 | Plant remained shutdown and in standby mode throughout the day as per NPCC demand of 0 MW.
| 2019-04-22 | Plant remained shutdown and in standby mode 0000~0914 hrs. CT-2 synch @ 0914 hrs, STG synch @ 1106 hrs and CT-1 synch @ 1125 hrs as per NPCC demand of Max. load.
| 2019-04-23 | CT-1 de-synch @ 0021 hrs & again synch @ 0830 hrs on NPCC Maximum load demand. CT-1 again de-synch @ 2327 hrs to achieve NPCC demand of 45% of complex export.
| 2019-04-24 | CT-1 synch @ 0820 hrs against NPCC demand of maximum load.
| 2019-04-25 | Plant load restricted 121~126 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2019-04-26 | Plant load restricted 122~126 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2019-04-27 | Plant load restricted 122~125 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2019-04-28 | Plant load restricted 122~125 MW from 0000~2207 hrs as both DBs kept off to remain within contractual heatrate. CT-1 desynch @2223hrs to achieve NPCC demand of 45% of complex export.
| 2019-04-29 | CT-1 synch @ 0548 hrs to achieve NPCC demand of maximum load. Plant load restricted to 121~124 MW from 0630~2235 hrs as both DBs kept off to remain within contractual heatrate. CT-1 de-synch @ 2250 hrs to achieve NPCC demand of 45% of complex export.
| 2019-04-30 | Plant load restricted to 59~61 MW as CT-1 remained shut down and in standby mode as per NPCC demand. CT-2 de-synch @ 2118 hrs and STG de-synch @ 2117 hrs and put on standby mode as per NPCC demand of 0 MW.
CT-2 Load Comparison
[10 empty] | Date/Time | Amb Temp.F | R.H% | Load | Freq
[9 empty] | Before washing | 09/07/20/0600 | 86.3 | 74.9 | 37.28 | 50.13
[9 empty] | After Washing | 16/07/20/0527 | 86.5 | 70.5 | 38.17 | 50.13
[10 empty] | Difference | 0.2 | -4.4 | 0.89 | 0

## May
Monthly Operational Returns Kabirwala
2019-05-01
| Date | Site Avg. Ambient Temp.F | Site Avg. Relative Humidty % | Site Avg. Ambient Wetbulb Temp.F | Site Ambient Temp |  | Base load hours |  |  |  | Standby hours |  |  |  | Plant ambient corrected Max Load |  | Corrected Plant Capacity | Ambient Corrected Daclared Avail'y (MWH) | Plant WAPDA Dispatch (MWH) | Net Plant Export (MWH) | Gross Generation | CT1 Average Cap (MW) | CT1 Unavail minutes | CT2 Average Cap (MW) | CT2 Unavail minutes | ST Average Cap (MW) | ST Unavail minutes | Plant Aux Load including Colony Load MWH | Differenece (+/-) MW | Maximum Daily Generation | Daily Load Factor | Avg. Corrected Plant Capacity | Plant Capacity Factor | Plant Availability Factor | Equivalent Plant Availability | LBtu gas flow (mmscf/day) | 1 LBtu gas (Average Btu/scf) | LBTU MMBTU | 1 HBtu gas flow (mmscf/day) | 1 HBtu gas (Average Btu/scf) | HBTU MMBTU | HHV Net Heat Rate (Btu/Kwh) | Avg. declared availability | CT1 Derated MW | CT1 derated mintutes | CT-2 derated MW | CT-2 derated mintutes | ST derated MW | ST derated mintutes | WAPDA Backfeed (MWH) | CT-1 Gross Generation (MWH) | CT-2 Gross Generation (MWH) | STG Gross Generation (MWH) | CT-1 & CT-2 MWH difference | Base load Heat Rate | STG load | DB1 | DB2 | CT1 Gas flow | CT2 Gas flow |  | Freq. Hz | LBTU Gas Specific gravity | CT-1 compressor efficiency(%) | CT-2 compressor efficiency(%) |  | CT-1 Heat Rate (Btu/Kwh) | CT-2 Heat Rate (Btu/Kwh) |  | RO Operation Hours
[7 empty] | CT1 |  | CT2 |  | CT1 |  | CT2 | [43 empty] | mmscf/d | mmscf/d | HBTU KPPH | HBTU KPPH | LBTU KPPH | Hz
[5 empty] | Max | Min | hrs | min | hrs | min | hrs | min | hrs | min | hrs | min
Week 18 | 2019-04-30 | 88.9 | 38.6% | 64.3 | 98 | 80 | 0 | 0 | 21 | 3 | 24 | 0 | 2 | 42 | 0 | 0 | 3513 | 3454 | 1284 | 1271 | 1326 | 42 | 0 | 43 | 0 | 60 | 0 | 58 | -13 | 64 | 86.33% | 146.375 | 36.18% | 100% | 75.41% | 7.07 | 137.99 | 975.5893 | 9.98 | 1000.66 | 9986.5868 | 8624.8435 | 143.9167 | 0 | 0 | 18 | 15 | 40 | 1277 | 3 | 0 | 902 | 424 | 902 | 8624.8435 | 17.6667 | 0 | 0 | 0 | 17.71 | 17.96 | 50.09 | 0.935 | 0 | 86.85 | -86.85 | 0 | 10977 | 10977 | 5.22 | 0
| 2019-05-01 | 89 | 39% | 64 | 101 | 75 | 3 | 44 | 10 | 37 | 19 | 7 | 11 | 36 | 0 | 0 | 3506 | 3471 | 968 | 957 | 995 | 42 | 0 | 43 | 0 | 60 | 0 | 47 | -11 | 128 | 32.39% | 146.0833 | 27.3% | 100% | 88.6% | 3.941 | 140.06 | 551.9765 | 8.1314 | 1002.3317 | 8150.318 | 9093.3066 | 144.625 | 22 | 69 | 16 | 107 | 32 | 643 | 9 | 181 | 507 | 307 | 326 | 9093.3066 | 12.7917 | 0 | 0 | 4.6 | 10.47 | 9.76 | 50.1 | 0.9346 | 86.94 | 86.91 | 0.03 | 11271 | 11035 | -236 | 0 | 0
| 2019-05-02 | 87.5 | 38% | 62 | 101 | 75 | 0 | 0 | 6 | 5 | 24 | 0 | 15 | 42 | 0 | 0 | 3522 | 3466 | 434 | 432 | 453 | 42 | 0 | 43 | 0 | 60 | 0 | 37 | -2 | 64 | 29.49% | 146.75 | 12.27% | 100% | 91.24% | 2.517 | 140.82 | 354.4439 | 3.8308 | 1002.227 | 3839.283 | 9707.7013 | 144.4167 | 0 | 0 | 16 | 133 | 40 | 404 | 16 | 0 | 322 | 131 | 322 | 9707.7013 | 5.4583 | 0 | 0 | 0 | 6.8 | 6 | 50.08 | 0.9346 | 0 | 86.55 | -86.55 | 0 | 11024 | 11024 | 4.2 | 0
| 2019-05-03 | 87 | 40% | 63 | 99 | 74 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3526 | 3470 | 0 | 0 | 0 | 42 | 0 | 43 | 0 | 60 | 0 | 17 | 0 | 0 | no data | 146.9167 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 144.5833 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 50.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-05-04 | 90.3 | 38.1% | 64.1 | 102 | 77 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3496 | 3466 | 0 | 0 | 0 | 42 | 0 | 43 | 0 | 60 | 0 | 14 | 0 | 0 | no data | 145.6667 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 144.4167 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 50.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-05-05 | 91.5 | 33.7% | 62.8 | 107 | 76 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3486 | 3452 | 0 | 0 | 0 | 42 | 0 | 43 | 0 | 60 | 0 | 12 | 0 | 0 | no data | 145.25 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 143.8333 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 50.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-05-06 | 93 | 32.3% | 63 | 108 | 78 | 11 | 2 | 12 | 21 | 12 | 16 | 10 | 6 | 10 | 45 | 3465 | 3463 | 1686 | 1692 | 1752 | 42 | 0 | 43 | 0 | 62 | 0 | 66 | 6 | 150 | 48.67% | 144.375 | 48.83% | 100% | 97.65% | 4.202 | 133.25 | 559.9165 | 14.8366 | 999.2303 | 14825.21 | 9092.8643 | 144.2917 | 23 | 42 | 19 | 93 | 34 | 66 | 6 | 477 | 566 | 709 | 89 | 9092.8643 | 29.5417 | 1.187 | 1.29 | 11.6 | 12.14 | 0.81 | 50.06 | 0.9376 | 87.24 | 86.62 | 0.62 | 11237 | 11487 | 250 | 8.55 | 2.477
Week 19 | 2019-05-07 | 93.4 | 32.7% | 65.6 | 109 | 77 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3464 | 3476.5 | 3476.5 | 3445 | 3545 | 43 | 0 | 43 | 0 | 62 | 0 | 9 | -31.5 | 154 | 95.91% | 144.3333 | 99.45% | 100% | 100% | 7.909 | 137.99 | 1091.3629 | 28.9683 | 998.9547 | 28938.0293 | 8716.8047 | 144.8542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1024 | 1036 | 1485 | 12 | 8716.8047 | 61.875 | 2.326 | 2.276 | 24.38 | 21.62 | 20.06 | 50.09 | 0.9355 | 87.15 | 86.65 | 0.5 | 11178 | 11436 | 258 | 0 | 4.602
| 2019-05-08 | 93.6 | 37.4% | 66.2 | 107 | 78 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 20 | 56 | 3462 | 3398 | 3360 | 3286 | 3392 | 42 | 0 | 42 | 0 | 60 | 0 | 106 | -74 | 146 | 96.8% | 144.25 | 94.92% | 100% | 98.67% | 7.835 | 136.85 | 1072.2197 | 27.6665 | 999.6241 | 27656.0801 | 8742.6354 | 141.5833 | 0 | 0 | 0 | 0 | 15 | 184 | 0 | 1000 | 1014 | 1378 | 0 | 8742.6354 | 57.4167 | 1.815 | 1.861 | 24.05 | 21.38 | 19.91 | 50.08 | 0.9359 | 87.15 | 86.85 | 0.3 | 11306 | 11546 | 240 | 4.08 | 3.676
| 2019-05-09 | 94.7 | 37.4% | 67.2 | 107 | 83 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 10 | 59 | 3450 | 3389 | 3149 | 3144 | 3237 | 42 | 0 | 42 | 0 | 60 | 0 | 93 | -5 | 143 | 94.32% | 143.75 | 91.13% | 100% | 94.35% | 7.827 | 133.62 | 1045.8437 | 26.0551 | 999.9969 | 26055.051 | 8619.8775 | 141.2083 | 0 | 0 | 0 | 0 | 15 | 781 | 0 | 999 | 1012 | 1226 | 0 | 8619.8775 | 51.0833 | 1.025 | 0.971 | 23.94 | 21.23 | 19.83 | 50.09 | 0.937 | 87.32 | 86.95 | 0.37 | 11259 | 11518 | 259 | 1.05 | 1.996
| 2019-05-10 | 93.78 | 37.39% | 66.06 | 106.26 | 79.44 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 20 | 54 | 3456 | 3393 | 3335 | 3289 | 3390 | 42 | 0 | 42 | 0 | 60 | 0 | 95 | -46 | 147 | 96.09% | 144 | 95.17% | 100% | 98.74% | 7.853 | 137.35 | 1078.6095 | 27.7765 | 1002.8038 | 27854.42 | 8796.9077 | 141.375 | 0 | 0 | 0 | 0 | 14 | 186 | 0 | 1005 | 1013 | 1372 | 8 | 8796.9077 | 57.1667 | 1.802 | 1.792 | 24 | 21.23 | 19.83 | 50.1 | 0.9356 | 87.26 | 86.78 | 0.48 | 11225 | 11493 | 268 | 5 | 3.594
| 2019-05-11 | 90.55 | 41.69% | 66.33 | 100.24 | 82.54 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 2 | 40 | 3493 | 3425 | 3056 | 3064 | 3153 | 42 | 0 | 42 | 0 | 60 | 0 | 89 | 8 | 147 | 89.37% | 145.5417 | 87.72% | 100% | 90.74% | 7.808 | 135.06 | 1054.5485 | 25.0698 | 1008.4285 | 25281.09 | 8595.1823 | 142.7083 | 0 | 0 | 0 | 0 | 15 | 1280 | 0 | 1009 | 1016 | 1128 | 7 | 8595.1823 | 47 | 0.533 | 0.438 | 24.06 | 21.27 | 19.72 | 50.09 | 0.9361 | 87.33 | 86.8 | 0.53 | 11207 | 11461 | 254 | 0 | 0.971
| 2019-05-12 | 92.08 | 45.18% | 67.7 | 103.12 | 78.51 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 9 | 44 | 3474 | 3415 | 3161 | 3144 | 3235 | 42 | 0 | 42 | 0 | 60 | 0 | 91 | -17 | 144 | 93.61% | 144.75 | 90.5% | 100% | 93.81% | 7.931 | 136.3 | 1080.9953 | 25.9365 | 1012.3848 | 26257.689 | 8695.5103 | 142.2917 | 0 | 0 | 0 | 0 | 15 | 856 | 0 | 1000 | 1011 | 1224 | 11 | 8695.5103 | 51 | 1.061 | 0.985 | 23.88 | 21.18 | 19.51 | 50.07 | 0.9358 | 87.41 | 86.79 | 0.62 | 11220 | 11457 | 237 | 5.25 | 2.046
| 2019-05-13 | 93.1 | 43% | 68 | 105 | 81 | 17 | 9 | 24 | 0 | 6 | 35 | 0 | 0 | 0 | 0 | 3464 | 3411 | 2590 | 2572 | 2654 | 41 | 0 | 42 | 0 | 59 | 0 | 82 | -18 | 130 | 85.06% | 144.3333 | 74.25% | 100% | 85.08% | 7.925 | 137.26 | 1087.7855 | 21.0128 | 1013.3481 | 21293.23 | 8701.7945 | 142.125 | 17 | 16 | 0 | 0 | 21 | 1440 | 0 | 713 | 1009 | 932 | 296 | 8701.7945 | 38.8333 | 0.276 | 0.305 | 17.2 | 21.15 | 19.9 | 50.11 | 0.9356 | 87.4 | 86.96 | 0.44 | 11273 | 11492 | 219 | 0 | 0.581
Week 20 | 2019-05-14 | 87.6 | 48% | 67 | 98 | 76 | 14 | 22 | 24 | 0 | 8 | 59 | 0 | 0 | 14 | 9 | 3522 | 3429 | 2631 | 2593 | 2685 | 42 | 0 | 43 | 0 | 60 | 0 | 92 | -38 | 144 | 77.69% | 146.75 | 73.62% | 100% | 88.62% | 7.831 | 134.03 | 1049.5889 | 21.868 | 1012.3463 | 22138.01 | 8942.3829 | 142.875 | 18 | 39 | 0 | 0 | 39 | 591 | 0 | 612 | 1016 | 1057 | 404 | 8942.3829 | 44.0417 | 1.298 | 1.398 | 14.78 | 21.32 | 19.63 | 50.07 | 0.9365 | 87.5 | 86.95 | 0.55 | 11236 | 11460 | 224 | 5.7 | 2.696
| 2019-05-15 | 84.1 | 57.5% | 67.9 | 95 | 74 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 8 | 26 | 3561 | 3433 | 3150 | 3148 | 3240 | 42 | 0 | 43 | 0 | 60 | 0 | 92 | -2 | 143 | 94.41% | 148.375 | 88.4% | 100% | 93.29% | 7.807 | 135.35 | 1056.6774 | 26.03 | 1010.56 | 26304.8768 | 8691.7263 | 143.0417 | 0 | 0 | 0 | 0 | 15 | 934 | 0 | 1013 | 1023 | 1204 | 10 | 8691.7263 | 50.1667 | 0.897 | 0.741 | 24.2 | 21.47 | 20.15 | 50.12 | 0.9357 | 87.59 | 86.97 | 0.62 | 11250 | 11481 | 231 | 0 | 1.638
| 2019-05-16 | 86 | 51.5% | 70.5 | 97 | 74 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3537 | 3446 | 3024 | 3032 | 3118 | 42 | 0 | 43 | 0 | 60 | 0 | 86 | 8 | 132 | 98.42% | 147.375 | 85.72% | 100% | 89.66% | 7.83 | 138.79 | 1086.7257 | 24.862 | 1004.1298 | 24964.705 | 8592.1605 | 143.5833 | 0 | 0 | 0 | 0 | 15 | 1440 | 0 | 1008 | 1022 | 1088 | 14 | 8592.1605 | 45.3333 | 0.4 | 0.181 | 24.281 | 21.566 | 19.892 | 50.09 | 0.9351 | 87.55 | 86.93 | 0.62 | 11321 | 11523 | 202 | 4.95 | 0.581
| 2019-05-17 | 80.3 | 66.7% | 69 | 88 | 72 | 14 | 28 | 20 | 46 | 9 | 16 | 2 | 57 | 0 | 0 | 3595 | 3479 | 2227 | 2240 | 2307 | 42 | 0 | 43 | 0 | 60 | 0 | 71 | 13 | 132 | 72.82% | 149.7917 | 62.31% | 100% | 83.86% | 6.678 | 132.66 | 885.9035 | 18.6742 | 997.4424 | 18626.421 | 8710.8591 | 144.9583 | 16 | 16 | 19 | 17 | 23 | 1440 | 4 | 618 | 891 | 798 | 273 | 8710.8591 | 33.25 | 0.236 | 0.118 | 14.94 | 18.93 | 17.46 | 50.12 | 0.9371 | 87.75 | 86.92 | 0.83 | 11341 | 11547 | 206 | 0 | 0.354
| 2019-05-18 | 83.4 | 60.9% | 75.5 | 93 | 73 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3562 | 3520 | 0 | 0 | 0 | 42 | 0 | 43 | 0 | 60 | 0 | 14 | 0 | 0 | no data | 148.4167 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 146.6667 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 50.1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| 2019-05-19 | 89.5 | 51.5% | 70.3 | 102 | 77 | 0 | 0 | 2 | 42 | 24 | 0 | 19 | 8 | 0 | 0 | 3499 | 3477 | 211 | 209 | 223 | 42 | 0 | 43 | 0 | 60 | 0 | 27 | -2 | 62 | 14.99% | 145.7917 | 5.973% | 100% | 95.32% | 1.615 | 151.58 | 244.8017 | 2.1419 | 995.9484 | 2133.181 | 11377.9077 | 144.875 | 0 | 0 | 19 | 130 | 41 | 178 | 13 | 0 | 166 | 57 | 166 | 11377.9077 | 2.375 | 0 | 0 | 0 | 3.98 | 3.36 | 50.11 | 0.9306 | 0 | 87.21 |  | 0 | 11699 | 11699 | 0 | 0
| 2019-05-20 | 88.7 | 45.4% | 72.3 | 101 | 77 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3508 | 3494 | 0 | 0 | 0 | 42 | 0 | 43 | 0 | 60 | 0 | 17 | 0 | 0 | no data | 146.1667 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 145.5833 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 50.09 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
Week 21 | 2019-05-21 | 93.6 | 42.4% | 63.9 | 105 | 80 | 11 | 38 | 12 | 23 | 11 | 23 | 9 | 10 | 5 | 8 | 3464 | 3452 | 1674 | 1649 | 1706 | 42 | 0 | 43 | 0 | 60 | 0 | 61 | -25 | 145 | 49.02% | 144.3333 | 47.6% | 100% | 94.62% | 4.364 | 143.7 | 627.1068 | 14.4711 | 994.8462 | 14396.558 | 9110.7731 | 143.8333 | 23 | 59 | 16 | 147 | 17 | 443 | 4 | 495 | 584 | 627 | 89 | 8737.953 | 26.125 | 0.531 | 0.474 | 23.36 | 21.37 | 18.59 | 50.13 | 0.935 | 87.7 | 87.3 |  | 11406 | 11607 | 201 | 7.6 | 1.005
| 2019-05-22 | 93.3 | 44.8% | 74.9 | 104 | 83 | 15 | 36 | 24 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 3462 | 3137 | 2438 | 2400 | 2482 | 42 | 0 | 43 | 0 | 60 | 0 | 82 | -38 | 128 | 80.79% | 144.25 | 69.32% | 100% | 82.51% | 7.711 | 136.56 | 1053.0142 | 20.0076 | 995.5254 | 19918.073 | 8737.953 | 130.7083 | 22 | 24 | 0 | 0 | 25 | 1440 | 0 | 650 | 1010 | 822 | 360 | 8605.3389 | 34.25 | 0 | 0 | 15.86 | 21.47 | 18.61 | 50.1 | 0.9365 | 87.58 | 87.16 |  | 11371 | 11538 | 167 | 3.75 | 0
| 2019-05-23 | 91.28 | 46.1% | 74.33 | 102.4 | 79.84 | 23 | 1 | 24 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 3488 | 3025 | 2950 | 2886 | 2968 | 41 | 0 | 42 | 0 | 60 | 0 | 82 | -64 | 128 | 96.61% | 145.3333 | 82.74% | 100% | 87.3% | 7.66 | 138.9 | 1063.974 | 23.882 | 995.3551 | 23771.034 | 8605.3389 | 126.0417 | 15 | 16 | 0 | 0 | 18 | 1440 | 0 | 961 | 1007 | 1000 | 46 | 8605.3389 | 41.6667 | 0 | 0 | 24.09 | 21.4 | 18.95 | 50.1 | 0.936 | 87.65 | 87.16 |  | 11360 | 11534 | 174 | 0 | 0
| 2019-05-24 | 87.33 | 54.9% | 75.55 | 97.05 | 76.7 | 9 | 35 | 24 | 0 | 13 | 25 | 0 | 0 | 0 | 0 | 3525 | 3282 | 2090 | 2046 | 2124 | 41 | 0 | 42 | 0 | 60 | 0 | 78 | -44 | 126 | 70.24% | 146.875 | 58.04% | 100% | 77.74% | 7.597 | 131.56 | 999.4613 | 17.2302 | 994.7818 | 17140.3029 | 8865.9649 | 136.75 | 20 | 60 | 0 | 0 | 31 | 1440 | 0 | 417 | 1011 | 696 | 594 | 8865.9649 | 29 | 0 | 0 | 24 | 21.44 | 19.12 | 50.14 | 0.9382 | 87 | 87.07 |  | 11234 | 11551 |  | 5.9 | 0
| 2019-05-25 | 87 | 49.8% | 75.3 | 99 | 75 | 14 | 3 | 24 | 0 | 9 | 24 | 0 | 0 | 0 | 0 | 3529 | 3224 | 2384 | 2334 | 2411 | 42 | 0 | 42 | 0 | 60 | 0 | 77 | -50 | 127 | 79.1% | 147.0417 | 66.14% | 100% | 81.66% | 7.629 | 132 | 1007.028 | 19.4927 | 994.2431 | 19380.4661 | 8735.0018 | 134.3333 | 18 | 33 | 0 | 0 | 26 | 1440 | 0 | 597 | 1017 | 797 | 420 | 8735.0018 | 33.2083 | 0 | 0 | 24.13 | 21.65 | 18.93 | 50.15 | 0.9379 | 87.7 | 86.98 |  | 11377 | 11549 |  | 0 | 0
| 2019-05-26 | 91 | 44% | 73 | 103 | 78 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3481 | 3009 | 3009 | 2943 | 3030 | 42 | 0 | 42 | 0 | 60 | 0 | 87 | -66 | 128 | 98.63% | 145.0417 | 84.54% | 100% | 87.5% | 7.62 | 132.94 | 1013.0028 | 24.0746 | 1000.244 | 24080.4856 | 8526.4996 | 125.375 | 0 | 0 | 0 | 0 | 18 | 1440 | 0 | 1001 | 1007 | 1022 | 6 | 8526.4996 | 42.5833 | 0 | 0 | 24 | 21.34 | 18.52 | 50.11 | 0.9377 | 87.57 | 87.06 |  | 11282 | 11498 |  | 4.8 | 0
| 2019-05-27 | 94.9 | 35.7% | 72.3 | 107 | 83 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3447 | 3013 | 3013 | 2950 | 3036 | 42 | 0 | 42 | 0 | 60 | 0 | 86 | -63 | 129 | 98.06% | 143.625 | 85.58% | 100% | 88.19% | 7.635 | 130.6 | 997.131 | 23.8291 | 1012.3088 | 24122.4226 | 8515.1029 | 125.5417 | 0 | 0 | 0 | 0 | 17 | 1440 | 0 | 1000 | 1011 | 1025 | 11 | 8515.1029 | 42.7083 | 0 | 0 | 23.91 | 21.28 | 18.51 | 50.12 | 0.9386 | 87.39 | 87.04 |  | 11230 | 11441 |  | 0 | 0
Week 22 | 2019-05-28 | 97 | 34.5% | 72.9 | 109 | 83 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3429 | 3006 | 3006 | 2935 | 3024 | 41 | 0 | 42 | 0 | 60 | 0 | 89 | -71 | 129 | 97.67% | 142.875 | 85.59% | 100% | 87.41% | 7.674 | 141.11 | 1082.8781 | 23.7061 | 1014.9293 | 24060.059 | 8566.5885 | 125.25 | 0 | 0 | 0 | 0 | 18 | 1440 | 0 | 994 | 1007 | 1023 | 13 | 8566.5885 | 42.625 | 0 | 0 | 23.78 | 21.21 | 18.37 | 50.11 | 0.936 | 87.39 | 87.11 |  | 11243 | 11440 |  | 5.3 | 0
| 2019-05-29 | 97.9 | 36.7% | 74.7 | 112 | 84 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3417 | 2983 | 2983 | 2918 | 3004 | 41 | 0 | 42 | 0 | 60 | 0 | 86 | -65 | 127 | 98.56% | 142.375 | 85.4% | 100% | 87.41% | 7.576 | 135.67 | 1027.8359 | 23.5417 | 1014.0391 | 23872.173 | 8533.245 | 124.2917 | 0 | 0 | 0 | 0 | 18 | 1440 | 0 | 986 | 1000 | 1018 | 14 | 8533.245 | 42.4167 | 0 | 0 | 23.65 | 21 | 18.65 | 50.12 | 0.9371 | 87.53 | 86.76 |  | 11264 | 11414 |  | 0 | 0
| 2019-05-30 | 98.5 | 34.8% | 74.3 | 112 | 84 | 22 | 15 | 22 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 3409 | 2977 | 2977 | 2743 | 2827 | 41 | 70 | 42 | 55 | 60 | 100 | 86 | -234 | 128 | 92.02% | 142.0417 | 80.46% | 94.57% | 81.08% | 7.186 | 136.99 | 984.4101 | 22.5313 | 1015.2432 | 22874.7963 | 8698.216 | 124.0417 | 11 | 35 | 12 | 49 | 20 | 1340 | 2 | 936 | 952 | 939 | 16 | 8698.216 | 39.125 | 0 | 0 | 22.56 | 20.22 | 17.65 | 50.1 | 0.9369 | 87.33 | 86.7 |  | 11276 | 11482 |  | 0 | 0
| 2019-05-31 | 99 | 37.98% | 75.2 | 111 | 85 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3404 | 2961 | 2961 | 2893 | 2978 | 41 | 0 | 42 | 0 | 60 | 0 | 85 | -68 | 127 | 97.7% | 141.8333 | 84.99% | 100% | 87.41% | 7.583 | 134.99 | 1023.6292 | 23.5653 | 1007.7978 | 23749.0333 | 8562.9666 | 123.375 | 0 | 0 | 0 | 0 | 18 | 1440 | 0 | 983 | 988 | 1007 | 5 | 8562.9666 | 41.9583 | 0 | 0 | 23.65 | 20.96 | 18.39 | 50.1 | 0.9375 | 87.56 | 86.56 |  | 11302 | 11537 |  | 5.3 | 0
| 2019-06-01 | [26 empty] | 0 | 0 |  | no data | no data | no data | #DIV/0! | no data |  |  | 0 |  |  | 0 | no data | 0 | [10 empty] | 0 | no data | 0
| 2019-06-02 | [26 empty] | 0 | 0 |  | no data | no data | no data | #DIV/0! | no data |  |  | 0 |  |  | 0 | no data | 0 | [10 empty] | 0 | no data | 0
| 2019-06-03 | [26 empty] | 0 | 0 |  | no data | no data | no data | #DIV/0! | no data |  |  | 0 |  |  | 0 | no data | 0 | [10 empty] | 0 | no data | 0
| Monthly | 90.9652 | 43.19% | 69.1894 | 102.9377 | 78.3558 | 468 | 53 | 543 | 10 | 267 | 8 | 188 | 39 | 127 | 41 | 108103 | 103042.5 | 65943.5 | 64881.49 | 66969 | 41.8065 | 70 | 42.5161 | 55 | 60.0968 | 100 | 2215.51 | -986.5 | 109.2903 | 0.79941 | 145.2997 | 60.02% | 99.82% | 89.71% | 177.744 | 114.7094 | 24180.8708 | 539.1921 | 841.9055 | 541682.9979 | 8721.4993 |  | 205 | 409 | 117 | 676 | 560 | 25166 | 128 | 19679 | 23218 | 24072 | 3539 | 8721.4993 | 984.75 | 13.387 | 12.83 | 504.301 | 481.806 | 424.352 | 50.0993 | 0.77488 | 69.3466 | 71.9407 |  | 8731.2581 | 9620.9677 |  | 71.43
| Totals | Avg.F | % Avg. |  | M Avg | m Avg | hrs | min | hrs | min | hrs | min | hrs | min | Avg Int Avi | Avg Ext Avi | MWhr Total | MWhr Total | MWhr Total | MWhr Total | MWhr Total | MW Avg | Total min | Avg MW | Total min | Avg MW | Total min | MWhr | Total MW | Av Max D/Gen | Av. DailyLF | Avg. | Avg. |  | Avg. | Total | Avg. |  | Total | Avg. |  | Avg. | [7 empty] | Total |  |  |  |  | Avg.
| Weeks data | Site Avg. Amb. Temp F | Site Avg. Relative humidity % | Site Avg. Ambient Wetbulb Temp.F | M Avg: Site Maximum/Minumum Temperature; hrs: CT-1 Base Load Hours; hrs: CT-2 Base Load Hours; hrs: CT-1 stand by hours / min; hrs: CT-2 standby hours / min | Plant ambient Corrected maximum Load hours/min |  | Average Corrected Plant Capacity | Ambient Corrected Declared Avail'y (MWH) | Av Plant WAPDA Dispatch | Net Plant Export (MWH) | Gross Generation | CT1 Av Cap (MW) | CT1 Unavail minutes | CT2 Av Cap (MW) | CT2 Unavail minutes | ST Unavail minutes | ST Average Cap (MW) | Plant Aux Load including Colony Load MWH | Differenece (+/-) MW | Maximum Daily Generation | Daily Load Factor | Avg. Corrected Plant | Plant Capacity Facto | Plant Availability Factor | Equivalent Plant Availability | LBtu gas flow mmscf | 1 LBtu gas (Average Btu/scf) | LBTU MMBTU | PL gas flow (mscf/week) | 1 PL gas (Average Btu/scf) | HBTU MMBTU | Plant Net Heat Rate (Btu/Kwh) | [11 empty] | 301.8
| Week 18 | 89.6 | 37.1% | 63.3143 | 102.2857 | 76.4286 | 14 | 46 | 50 | 6 | 151 | 23 | 112 | 6 | 10 | 45 | 3502 | 3463.1429 | 624.5714 | 621.7143 | 646.5714 | 42 | No outage | 43 | No outage | 422 | no data | no data | -20 | 58 | 49.22% | 145.9167 | 31.14% | 100% | 88.22% | 17.73 | 78.8743 | 1398.4411 | 36.7787 | 572.0641 | 21039.7982 | 9129.6789
| Week 19 | 93.03 | 39.25% | 0 | 105.3743 | 79.9271 | 161 | 7 | 168 | 0 | 6 | 35 | 0 | -60 | 89 | -195 | 3466.1429 | 3415.3571 | 3161.0714 | 21944 | 22606 | 42 | No outage | 295 | no data | 421 | no data | 565 | -183.5 | 144.4286 | 93.02% | 144.4226 | 90.45% | 100% | 94.48% | 55.088 | 136.3471 | 7511.0914 | 182.4855 | 1005.0773 | 183411.9999 | 8695.5303 | [5 empty] | 0.27381
| Week 20 | 85.6571 | 54.5% | 70.3571 | 96.2857 | 74.7143 | 76 | 50 | 95 | 28 | 90 | 15 | 70 | 5 | 22 | 35 | 3540.5714 | 3468.2857 | 1606.1429 | 11222 | 11573 | 42 | No outage | 301 | no data | 420 | no data | 399 | -21 | 87.5714 | 71.67% | 147.5238 | 63.21% | 100% | 90.15% | 31.761 | 98.9157 | 3141.662 | 93.5761 | 836.7378 | 78298.6545 | 9263.0073 | [5 empty] | 0.26672
| Week 21 | 91.2014 | 45.39% | 70.3571 | 102.4929 | 79.3629 | 121 | 53 | 156 | 23 | 42 | 55 | 9 | 10 | 5 | 8 | 3485.1429 | 3163.1429 | 2508.2857 | 17208 | 17757 | 41.7143 | No outage | 296 | no data | 420 | no data | 553 | -350 | 130.1429 | 81.78% | 145.2143 | 70.57% | 100% | 85.64% | 50.216 | 135.18 | 6788.1989 | 142.9873 | 998.1863 | 142727.9948 | 8728.0906
| Week 22 | 91.6871 | 44.26% | 69.9143 | 103.0643 | 79.7914 | 134 | 15 | 168 | 0 | 31 | 32 | 0 | 0 | 0 | 0 | 3480.1429 | 3099.4286 | 2698.5714 | 18494 | 19075 | 41.5714 | No outage | 295 | no data | 420 | no data | 581 | -396 | 127.8571 | 88.73% | 145.006 | 75.99% | 100% | 84.62% | 53.526 | 134.81 | 7215.8401 | 152.2223 | 1001.0554 | 152382.9773 | 8650.3499
| Date | Plant Status Whether Normal Operation or Tripping (State full detail for trippings/return to normal).
| 2019-05-01 | CT-2 synch @ 1136 hrs, CT-1 synch @ 1312hrs and STG synch @ 1317 hrs as per NPCC demand. CT-1 de-synch @ 1805 hrs and put on standby mode as per NPCC demand.
| 2019-05-02 | STG de-synch @ 0122 hrs & CT-2 de-synch @ 0123 hrs as per NPCC demand of 0 MW. CT-2 synch @ 1324 hrs and STG synch @ 1456 hrs as per NPCC demand of half complex. STG de-synch @ 2018 hrs & CT-2 de-synch @ 2019 hrs as per NPCC demand of 0 MW.
| 2019-05-03 | Plant remained shutdown and in standby mode as per NPCC demand of 0 MW.
| 2019-05-04 | Plant remained shutdown and in standby mode as per NPCC demand of 0 MW.
| 2019-05-05 | Plant remained shutdown and in standby mode as per NPCC demand of 0 MW.
| 2019-05-06 | CT-2 @ 1006 hrs, STG synch @ 1209 hrs and CT-1 @ 1216 hrs Synch as per NPCC demand.
| 2019-05-07 | “Annual Dependable Capacity (ADC) Test” for the year 2019 carried out successfully and witnessed by CPPA and WAPDA metering teams.
| 2019-05-08 | NPCC load demand of 124 MW received from 0005 ~ 0153 hrs and again load demand of 125 MW received from 2303 hrs.
| 2019-05-09 | Plant load remained restricted to 125 MW from 0000~1024 hrs at NPCC demand and again load demand of 124 MW received at 2131 hrs from NPCC.
| 2019-05-10 | Plant load remained restricted to 125 MW from 0000~0212 hrs & from 2306~2400 hrs at NPCC demand.
| 2019-05-11 | Plant load remained restricted to 125 MW from 0000~2105hrs & 2345~2400hrs on NPCC demand whereas load remained maximum (ambient corrected) from 2105~2345 hrs.
| 2019-05-12 | Plant load remained restricted to 126 MW from 0000~1323 hrs & from 2307~2400 hrs at NPCC demand whereas load remained maximum (ambient corrected) from 1323~2307 hrs.
| 2019-05-13 | Plant load remained restricted to 126 MW from 0000~1709 hrs as per NPCC demand & Gas turbine CT-1 de-synch @ 1725 hrs as per NPCC demand of 61 MW.
| 2019-05-14 | Plant load remained restricted to 61 MW from 0000~0830 hrs as per NPCC demand. Gas turbine CT-1 synch @ 0859 hrs as per NPCC demand of maximum load.
| 2019-05-15 | Plant load remained restricted to 126 MW from 0047~1027 hrs, 1112~1520 hrs and 2256~2400 hrs as per NPCC demand.
| 2019-05-16 | Plant load remained restricted to 126 MW from 0000~2400 hrs as per NPCC demand.
| 2019-05-17 | CT-1 Desynch @ 1444 hrs as per NPCC demand of 61 MW. STG @ 2102 hrs & CT-2 @ 2103 hrs Desynch as per NPCC demand of 0 MW.
| 2019-05-18 | Plant remained shutdown and in standby mode as per NPCC demand of 0 MW.
| 2019-05-19 | CT-2 synch @ 1544 hrs and STG synch @ 1737 hrs as per NPCC demand of half complex. STG de-synch @ 2035 hrs & CT-2 de-synch @ 2036 hrs as per NPCC demand of 0 MW.
| 2019-05-20 | Plant remained shutdown and in standby mode as per NPCC demand of 0 MW.
| 2019-05-21 | CT-2 synch @ 0910 hrs, CT-1 synch @ 1119 hrs and STG synch @ 1129 hrs as per NPCC demand of maximum load. CT-1 de-synch @ 2356 hrs as per NPCC demand of 60 MW.
| 2019-05-22 | Plant load remained restricted to 60 MW from 0000~0725 hrs as per NPCC demand. CT-1 synch @ 0800 hrs as per NPCC demand of maximum load.
| 2019-05-23 | Plant load restricted 120~125 MW from 0000~2301 hrs as both DBs kept off to remain within contractual heatrate. CT-1 de-synch @ 2317 hrs as per NPCC demand of 62 MW.
| 2019-05-24 | CT-1 synch @1035 hrs to meet NPCC maximum load demand. Plant load restricted to 120~122 MW from 1137~2052 hrs to remain within contractual heatrate. CT-1 de-synch @ 2110 hrs as per NPCC demand of 62 MW.
| 2019-05-25 | CT-1 synch @ 0924 hrs to meet NPCC maximum load demand. Plant load restricted to 121~124 MW from 1000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2019-05-26 | Plant load restricted to 121~124 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2019-05-27 | Plant load restricted to 121~125 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2019-05-28 | Plant load restricted to 120~125 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2019-05-29 | Plant load restricted to 119~124 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2019-05-30 | FKPCL Plant tripped at 1447 hrs due to WAPDA supply failure. After restoration of WAPDA supply at 1456 hrs, CT-2 synch @ 1542 hrs, CT-1 synch @ 1557 hrs and STG synch @ 1627 hrs and plant load increased to 120 MW as both DBs kept off to remain within contractual heatrate .
| 2019-05-31 | Plant load restricted to 118~123 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
186
[16 empty] | 3.1 | 20.9
0.9
[5 empty] | min: 93.916 |  |  | 54
43.13
137.046
[12 empty] | 44.6404 |  | 3.07

## June
Monthly Operational Returns Kabirwala
2019-06-01
| Date | Site Avg. Ambient Temp.F | Site Avg. Relative Humidty % | Site Avg. Ambient Wetbulb Temp.F | Site Ambient Temp |  | Base load hours |  |  |  | Standby hours |  |  |  | Plant ambient corrected Max Load |  | Corrected Plant Capacity | Ambient Corrected Daclared Avail'y (MWH) | Plant WAPDA Dispatch (MWH) | Net Plant Export (MWH) | Gross Generation | CT1 Average Cap (MW) | CT1 Unavail minutes | CT2 Average Cap (MW) | CT2 Unavail minutes | ST Average Cap (MW) | ST Unavail minutes | Plant Aux Load including Colony Load MWH | Differenece (+/-) MW | Maximum Daily Generation | Daily Load Factor | Avg. Corrected Plant Capacity | Plant Capacity Factor | Plant Availability Factor | Equivalent Plant Availability | LBtu gas flow (mmscf/day) | 1 LBtu gas (Average Btu/scf) | LBTU MMBTU | 1 HBtu gas flow (mmscf/day) | 1 HBtu gas (Average Btu/scf) | HBTU MMBTU | HHV Net Heat Rate (Btu/Kwh) | Avg. declared availability | CT1 Derated MW | CT1 derated mintutes | CT-2 derated MW | CT-2 derated mintutes | ST derated MW | ST derated mintutes | WAPDA Backfeed (MWH) | CT-1 Gross Generation (MWH) | CT-2 Gross Generation (MWH) | STG Gross Generation (MWH) | CT-1 & CT-2 MWH difference | Base load Heat Rate | STG load | DB1 | DB2 | CT1 Gas flow | CT2 Gas flow |  | Freq. Hz | LBTU Gas Specific gravity | CT-1 compressor efficiency(%) | CT-2 compressor efficiency(%) | DB(1+2) | CT-1 Heat Rate (Btu/Kwh) | CT-2 Heat Rate (Btu/Kwh) | RO Operation Hours
[7 empty] | CT1 |  | CT2 |  | CT1 |  | CT2 | [43 empty] | mmscf/d | mmscf/d | HBTU KPPH | HBTU KPPH | LBTU KPPH | Hz |  |  |  | mmscf/d
[5 empty] | Max | Min | hrs | min | hrs | min | hrs | min | hrs | min | hrs | min
Week 22 | 2019-05-28 | 97 | 34.5% | 72.9 | 109 | 83 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3429 | 3006 | 3006 | 2935 | 3024 | 41 | 0 | 42 | 0 | 60 | 0 | 89 | -71 | 129 | 97.67% | 142.875 | 85.59% | 100% | 87.41% | 7.674 | 141.11 | 1082.8781 | 23.706 | 1014.93 | 24059.9306 | 8566.5447 | 125.25 | 0 | 0 | 0 | 0 | 18 | 1440 | 0 | 994 | 1007 | 1023 | 13 | 8566.5447 | 42.625 | 0 | 0 | 23.78 | 21.21 | 18.37 | 50.11 | 0.936 | 87.39 | 87.11 | 0 | 11243 | 11440 | 5.3
| 2019-05-29 | 97.9 | 36.7% | 74.7 | 112 | 84 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3417 | 2983 | 2983 | 2918 | 3004 | 41 | 0 | 42 | 0 | 60 | 0 | 86 | -65 | 127 | 98.56% | 142.375 | 85.4% | 100% | 87.41% | 7.576 | 135.67 | 1027.8359 | 23.541 | 1014.06 | 23871.9865 | 8533.1811 | 124.2917 | 0 | 0 | 0 | 0 | 18 | 1440 | 0 | 986 | 1000 | 1018 | 14 | 8533.1811 | 42.4167 | 0 | 0 | 23.65 | 21 | 18.65 | 50.12 | 0.9371 | 87.53 | 86.76 | 0 | 11264 | 11414 | 0
| 2019-05-30 | 98.5 | 34.8% | 74.3 | 112 | 84 | 22 | 15 | 22 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 3409 | 2977 | 2977 | 2743 | 2827 | 41 | 70 | 42 | 55 | 60 | 100 | 86 | -234 | 128 | 92.02% | 142.0417 | 80.46% | 94.57% | 81.08% | 7.186 | 136.99 | 984.4101 | 22.531 | 1015.223 | 22873.9894 | 8697.9218 | 124.0417 | 11 | 35 | 12 | 49 | 20 | 1340 | 2 | 936 | 952 | 939 | 16 | 8697.9218 | 39.125 | 0 | 0 | 22.56 | 20.22 | 17.65 | 50.1 | 0.9369 | 87.33 | 86.7 | 0 | 11276 | 11482 | 0
| 2019-05-31 | 99 | 37.98% | 75.2 | 111 | 85 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3404 | 2961 | 2961 | 2893 | 2978 | 41 | 0 | 42 | 0 | 60 | 0 | 85 | -68 | 127 | 97.7% | 141.8333 | 84.99% | 100% | 87.41% | 7.583 | 134.95 | 1023.3258 | 23.565 | 1007.8 | 23748.807 | 8562.7836 | 123.375 | 0 | 0 | 0 | 0 | 18 | 1440 | 0 | 983 | 988 | 1007 | 5 | 8562.7836 | 0 | 0 | 0 | 23.65 | 20.96 | 18.39 | 50.1 | 0.9375 | 87.56 | 86.56 | 0 | 11302 | 11537 | 5.3
| 2019-06-01 | 100.7 | 35% | 76.2 | 114 | 86 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3389 | 2953 | 2953 | 2885 | 2972 | 41 | 0 | 41 | 0 | 60 | 0 | 87 | -68 | 127 | 97.51% | 141.2083 | 85.13% | 100% | 87.32% | 7.57 | 134.32 | 1016.8024 | 23.5144 | 1007.2951 | 23685.97 | 8562.4861 | 123.0417 | 0 | 0 | 0 | 0 | 18 | 1440 | 0 | 978 | 984 | 1010 | 6 | 8562.4861 | 0 | 0 | 0 | 23.58 | 20.93 | 18.3 | 50.12 | 0.9384 | 87.56 | 86.79 | 0 | 11329 | 11574 | 0
| 2019-06-02 | 101.9 | 34.2% | 76.2 | 114 | 87 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3372 | 2957 | 2957 | 2895 | 2979 | 41 | 0 | 41 | 0 | 60 | 0 | 84 | -62 | 127 | 97.74% | 140.5 | 85.85% | 100% | 87.32% | 7.567 | 139.14 | 1052.8724 | 23.5133 | 1007.0292 | 23678.6 | 8542.8229 | 123.2083 | 0 | 0 | 0 | 0 | 18 | 1440 | 0 | 980 | 988 | 1011 | 8 | 8542.8229 | 0 | 0 | 0 | 23.63 | 20.9 | 18.59 | 50.12 | 0.9362 | 87.78 | 86.72 | 0 | 11335 | 11525 | 5.5
| 2019-06-03 | 102.2 | 30.78% | 74.73 | 115.24 | 87.23 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 3369 | 3145 | 3145 | 3092 | 3187 | 41 | 0 | 41 | 0 | 60 | 0 | 95 | -53 | 142 | 93.52% | 140.375 | 91.78% | 100% | 94.35% | 7.54 | 134.79 | 1016.3166 | 25.7112 | 1006.6749 | 25882.79 | 8699.5817 | 131.0417 | 0 | 0 | 0 | 0 | 17.5 | 660 | 0 | 982 | 989 | 1216 | 7 | 8699.5817 | 50.6667 | 1.061 | 1.12 | 23.65 | 21 | 18.14 | 50.14 | 0.9379 | 87.73 | 86.66 | 2.181 | 11327 | 11538 | 0
Week 23 | 2019-06-04 | 97.6 | 38.8% | 75.6 | 108 | 85 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 3421 | 3118 | 3118 | 3047 | 3136 | 41 | 0 | 41 | 0 | 60 | 0 | 89 | -71 | 143 | 91.38% | 142.5417 | 89.07% | 100% | 92.08% | 7.536 | 130.84 | 986.0102 | 25.3227 | 1004.0406 | 25425.03 | 8667.8832 | 129.9167 | 0 | 0 | 0 | 0 | 15 | 1080 | 0 | 985 | 985 | 1166 | 0 | 8667.8832 | 48.5833 | 0.861 | 0.661 | 23.78 | 20.99 | 18.35 | 50.11 | 0.9389 | 87.78 | 86.89 | 1.522 | 11345 | 11586 | 5.02
| 2019-06-05 | 95.7 | 42% | 76.1 | 107 | 86 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3439 | 3026 | 3026 | 2969 | 3050 | 41 | 0 | 41 | 0 | 60 | 0 | 81 | -57 | 130 | 97.76% | 143.2917 | 86.33% | 100% | 89.44% | 7.54 | 130.43 | 983.4422 | 24.3497 | 1007.1175 | 24523.01 | 8590.9236 | 126.0833 | 0 | 0 | 0 | 0 | 15 | 1440 | 0 | 984 | 984 | 1082 | 0 | 8590.9236 | 45.0833 | 0.465 | 0.297 | 23.74 | 20.95 | 18.3 | 50.1 | 0.9389 | 87.86 | 86.86 | 0.762 | 11337 | 11558 | 0
| 2019-06-06 | 95.9 | 34.7% | 72.7 | 109 | 83 | 20 | 2 | 24 | 0 | 3 | 20 | 0 | 0 | 4 | 0 | 3442 | 3185 | 2880 | 2825 | 2909 | 41 | 0 | 42 | 0 | 60 | 0 | 84 | -55 | 146 | 83.02% | 143.4167 | 82.07% | 100% | 88.05% | 7.509 | 133.78 | 1004.554 | 23.5486 | 1004.9536 | 23665.3 | 8732.6917 | 132.7083 | 16 | 38 | 0 | 0 | 20 | 1200 | 0 | 849 | 1000 | 1060 | 0 | 8732.6917 | 44.1667 | 0.682 | 0.667 | 20.66 | 21.31 | 18.22 | 50.12 | 0.9376 | 87.52 | 86.65 | 1.349 | 11367 | 11545 | 5.7
| 2019-06-07 | 97.6 | 37% | 74.7 | 109 | 84 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 7 | 20 | 3420 | 3160 | 3160 | 3093 | 3181 | 41 | 0 | 41 | 0 | 60 | 0 | 88 | -67 | 146 | 90.78% | 142.5 | 90.44% | 100% | 92.66% | 7.531 | 134.98 | 1016.5344 | 25.797 | 1001.4913 | 25835.5 | 8681.5501 | 131.6667 | 0 | 0 | 0 | 0 | 15 | 1000 | 0 | 993 | 990 | 1198 | -3 | 8681.5501 | 49.9167 | 1.011 | 0.935 | 24.02 | 21.17 | 18.24 | 50.11 | 0.9376 | 87.57 | 86.73 | 1.946 | 11370 | 11593 | 0
| 2019-06-08 | 99 | 37.4% | 74.8 | 108 | 86 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 3410 | 3057 | 3057 | 2990 | 3076 | 41 | 0 | 41 | 0 | 60 | 0 | 86 | -67 | 144 | 89% | 142.0833 | 87.68% | 100% | 89.88% | 7.474 | 130.66 | 976.5528 | 24.8078 | 997.708 | 24750.91 | 8604.5026 | 127.375 | 0 | 0 | 0 | 0 | 15 | 1380 | 0 | 991 | 987 | 1098 | -4 | 8604.5026 | 45.75 | 0.554 | 0.335 | 23.99 | 21.17 | 17.96 | 50.1 | 0.9391 | 87.56 | 86.7 | 0.889 | 11388 | 11622 | 5.25
| 2019-06-09 | 99.8 | 37% | 75.9 | 112 | 85 | 24 | 0 | 22 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 3395 | 2981 | 2981 | 2912 | 2999 | 41 | 0 | 41 | 0 | 60 | 0 | 87 | -69 | 130 | 96.12% | 141.4583 | 85.77% | 100% | 87.88% | 7.474 | 133.39 | 996.9569 | 24.2548 | 996.8357 | 24178.039 | 8645.2596 | 124.2083 | 0 | 0 | 19 | 92 | 16 | 1440 | 0 | 984 | 956 | 1059 | -28 | 8645.2596 | 44.125 | 0.434 | 0.244 | 23.95 | 20.78 | 17.22 | 50.12 | 0.9386 | 87.65 | 86.74 | 0.678 | 11441 | 11675 | 0
| 2019-06-10 | 101.2 | 37.1% | 76.2 | 113 | 87 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 3382 | 3146 | 3146 | 3086 | 3179 | 41 | 0 | 41 | 0 | 60 | 0 | 93 | -60 | 142 | 93.28% | 140.9167 | 91.25% | 100% | 94.28% | 7.4 | 130.3 | 964.22 | 26.0233 | 998.0429 | 25972.4 | 8728.652 | 131.0833 | 0 | 0 | 0 | 0 | 15 | 780 | 0 | 979 | 977 | 1223 | -2 | 8728.652 | 50.9583 | 1.267 | 1.192 | 23.84 | 21 | 18.03 | 50.14 | 0.9391 | 87.62 | 86.73 | 2.459 | 11435 | 11649 | 5.35
Week 24 | 2019-06-11 | 100.1 | 41.3% | 77 | 110 | 93 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 3394 | 3155 | 3155 | 3087 | 3181 | 40 | 0 | 41 | 0 | 60 | 0 | 94 | -68 | 141 | 94% | 141.4167 | 90.95% | 100% | 94.68% | 7.379 | 131.62 | 971.224 | 25.9337 | 1001.3642 | 25969.119 | 8727.0304 | 131.4583 | 0 | 0 | 0 | 0 | 15 | 720 | 0 | 968 | 972 | 1241 | 4 | 8727.0304 | 51.7083 | 1.335 | 1.263 | 23.44 | 20.71 | 18.04 | 50.1 | 0.9385 | 87.46 | 86.74 | 2.598 | 11367 | 11569 | 0
| 2019-06-12 | 94.73 | 41.47% | 75.6 | 104 | 86 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 8 | 3 | 3454 | 3174 | 3160 | 3060 | 3151 | 41 | 0 | 41 | 0 | 60 | 0 | 91 | -100 | 140 | 93.78% | 143.9167 | 88.59% | 100% | 92.98% | 7.382 | 132.36 | 977.0815 | 25.5395 | 1006.8686 | 25714.949 | 8722.8858 | 132.25 | 0 | 0 | 0 | 0 | 15 | 957 | 0 | 981 | 981 | 1189 | 0 | 8722.8858 | 49.5417 | 0.861 | 0.956 | 23.68 | 20.86 | 18.2 | 50.12 | 0.938 | 87.52 | 86.83 | 1.817 | 11345 | 11542 | 6.25
| 2019-06-13 | 95.95 | 36.3% | 73.5 | 109 | 83 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 12 | 55 | 3437 | 3357 | 3175 | 3144 | 3240 | 41 | 0 | 41 | 0 | 60 | 0 | 96 | -31 | 142 | 95.07% | 143.2083 | 91.48% | 100% | 95.12% | 7.449 | 135.31 | 1007.9242 | 26.5489 | 997.9043 | 26493.221 | 8747.1836 | 139.875 | 0 | 0 | 0 | 0 | 15 | 665 | 0 | 993 | 990 | 1257 | -3 | 8747.1836 | 52.375 | 1.352 | 1.314 | 23.97 | 21.08 | 18.03 | 50.11 | 0.9373 | 87.42 | 86.7 | 2.666 | 11359 | 11545 | 0
| 2019-06-14 | 100.55 | 35.17% | 75.11 | 112 | 86 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 3390 | 3168 | 3168 | 3109 | 3203 | 41 | 0 | 41 | 0 | 60 | 0 | 94 | -59 | 140 | 95.33% | 141.25 | 91.71% | 100% | 95.16% | 7.453 | 133.15 | 992.3669 | 26.2413 | 996.6999 | 26154.66 | 8731.7552 | 132 | 0 | 0 | 0 | 0 | 15 | 660 | 0 | 981 | 982 | 1240 | 1 | 8731.7552 | 51.6667 | 1.236 | 1.213 | 23.76 | 20.95 | 17.9 | 50.14 | 0.9381 | 87.39 | 86.66 | 2.449 | 11368 | 11553 | 6.02
| 2019-06-15 | 98.52 | 51.86% | 80.72 | 107 | 89 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 3409 | 3150 | 3150 | 3080 | 3174 | 40 | 0 | 40 | 0 | 60 | 0 | 94 | -70 | 140 | 94.46% | 142.0417 | 90.35% | 100% | 94.76% | 7.43 | 135.33 | 1005.5019 | 26.2364 | 996.8628 | 26154.1 | 8818.0526 | 131.25 | 0 | 0 | 0 | 0 | 16 | 660 | 0 | 962 | 961 | 1251 | -1 | 8818.0526 | 52.125 | 1.417 | 1.375 | 23.44 | 20.59 | 18.07 | 50.12 | 0.9373 | 87.85 | 86.96 | 2.792 | 11452 | 11635 | 0
| 2019-06-16 | 93.3 | 52.96% | 79.35 | 103.2 | 80.06 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3469 | 2984 | 2984 | 2918 | 3004 | 41 | 0 | 41 | 0 | 60 | 0 | 86 | -66 | 129 | 97.03% | 144.5417 | 84.12% | 100% | 88.73% | 7.405 | 134.4 | 995.232 | 24.266 | 998.3781 | 24226.6562 | 8643.5532 | 124.3333 | 0 | 0 | 0 | 0 | 16 | 1440 | 0 | 974 | 971 | 1059 | -3 | 8643.5532 | 44.125 | 0.354 | 0.227 | 23.64 | 20.68 | 18.22 | 50.15 | 0.9377 | 87.83 | 87.02 | 0.581 | 11404 | 11567 | 0
| 2019-06-17 | 95.23 | 54.43% | 80.26 | 102 | 88.96 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3448 | 2964 | 2964 | 2898 | 2987 | 40 | 0 | 40 | 0 | 60 | 0 | 89 | -66 | 129 | 96.48% | 143.6667 | 84.05% | 100% | 88.57% | 7.363 | 132.39 | 974.7876 | 24.0724 | 1001.7665 | 24114.9582 | 8657.6072 | 123.5 | 0 | 0 | 0 | 0 | 16 | 1440 | 0 | 967 | 966 | 1054 | -1 | 8657.6072 | 43.9167 | 0.354 | 0.202 | 23.51 | 20.62 | 18.05 | 50.13 | 0.9382 | 87.81 | 87.02 | 0.556 | 11418 | 11594 | 0
Week 25 | 2019-06-18 | 87.9 | 56.1% | 70.4 | 99 | 76 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3523 | 3027 | 3027 | 2963 | 3050 | 41 | 0 | 41 | 0 | 60 | 0 | 87 | -64 | 129 | 98.51% | 146.7917 | 84.1% | 100% | 89.44% | 7.329 | 133.54 | 978.7147 | 24.5064 | 1001.285 | 24537.906 | 8611.7518 | 126.125 | 0 | 0 | 0 | 0 | 15 | 1440 | 0 | 990 | 988 | 1072 | -2 | 8768.8346 | 44.6667 | 0.354 | 0.202 | 23.9 | 21.38 | 17.66 | 50.17 | 0.9375 | 87.7 | 86.89 | 0.556 | 11335 | 11626 | 4.8
| 2019-06-19 | 90.4 | 55% | 78 | 102 | 78 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 3490 | 3200 | 3200 | 3126 | 3220 | 41 | 0 | 41 | 0 | 60 | 0 | 94 | -74 | 141 | 95.15% | 145.4167 | 89.57% | 100% | 95.16% | 7.337 | 137.86 | 1011.4788 | 26.4014 | 999.9428 | 26399.898 | 8768.8346 | 133.3333 | 0 | 0 | 0 | 0 | 15 | 660 | 0 | 983 | 979 | 1258 | -4 | 8824.4469 | 52.4167 | 1.32 | 1.251 | 23.8 | 20.93 | 17.93 | 50.09 | 0.936 | 87.8 | 86.98 | 2.571 | 11413 | 11574 | 0
| 2019-06-20 | 91.4 | 62.1% | 81.9 | 105 | 73 | 19 | 11 | 24 | 0 | 4 | 33 | 0 | 0 | 7 | 5 | 3483 | 3181 | 2780 | 2719 | 2805 | 40 | 0 | 40 | 0 | 60 | 0 | 86 | -61 | 139 | 84.08% | 145.125 | 78.06% | 100% | 88.8% | 7.315 | 136.48 | 998.3512 | 22.9706 | 1001.0746 | 22995.3198 | 8824.4469 | 132.5417 | 15 | 16 | 0 | 0 | 22 | 1015 | 0 | 776 | 969 | 1060 | 193 | 8824.4469 | 44.1667 | 0.827 | 0.844 | 18.94 | 20.72 | 17.63 | 50.16 | 0.9364 | 87.91 | 87.1 | 1.671 | 11442 | 11574 | 0
| 2019-06-21 | 87.6 | 61.5% | 78.9 | 97 | 77 | 13 | 49 | 24 | 0 | 9 | 20 | 0 | 0 | 0 | 40 | 3517 | 3207 | 2367 | 2335 | 2412 | 40 | 0 | 41 | 0 | 60 | 0 | 77 | -32 | 133 | 75.56% | 146.5417 | 66.39% | 100% | 82.34% | 7.181 | 136.65 | 981.2836 | 19.7278 | 1000.4904 | 19737.4799 | 8873.1321 | 133.625 | 17 | 51 | 0 | 0 | 25 | 1400 | 0 | 579 | 980 | 853 | 401 | 8873.1321 | 35.5417 | 0.288 | 0.528 | 14.26 | 21.01 | 17.62 | 50.13 | 0.9364 | 87.95 | 87.02 | 0.816 | 11431 | 11552 | 0.75
| 2019-06-22 | 95.4 | 56% | 82.3 | 105 | 87 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3445 | 2961 | 2961 | 2897 | 2983 | 40 | 0 | 40 | 0 | 60 | 0 | 86 | -64 | 126 | 98.64% | 143.5417 | 84.09% | 100% | 88.57% | 7.29 | 138.01 | 1006.0929 | 24.2519 | 999.5069 | 24239.9317 | 8714.5408 | 123.375 | 0 | 0 | 0 | 0 | 16 | 1440 | 0 | 961 | 962 | 1060 | 1 | 8714.5408 | 44.1667 | 0.404 | 0.253 | 23.56 | 20.87 | 17.64 | 50.11 | 0.9364 | 88.05 | 87.29 | 0.657 | 11519 | 11722 | 5.38
| 2019-06-23 | 93.2 | 57.2% | 81 | 106 | 82 | 21 | 51 | 24 | 0 | 1 | 54 | 0 | 0 | 0 | 0 | 3467 | 3012 | 2845 | 2780 | 2864 | 40 | 0 | 40 | 0 | 60 | 0 | 84 | -65 | 127 | 93.96% | 144.4583 | 80.18% | 100% | 87.03% | 7.177 | 139 | 997.603 | 23.379 | 994.0145 | 23239.078 | 8718.2306 | 125.5 | 15 | 15 | 0 | 0 | 18 | 1440 | 0 | 883 | 967 | 1014 | 84 | 8718.2306 | 42.25 | 0.354 | 0.253 | 21.68 | 20.97 | 17.59 | 50.12 | 0.9356 | 87.97 | 87.3 | 0.607 | 11529 | 11706 | 0.75
| 2019-06-24 | 86.5 | 65.6% | 80.4 | 96.48 | 79 | 11 | 16 | 24 | 0 | 12 | 6 | 0 | 0 | 1 | 3 | 3535 | 3271 | 2193 | 2149 | 2232 | 40 | 0 | 41 | 0 | 60 | 0 | 83 | -44 | 140 | 66.43% | 147.2917 | 60.79% | 100% | 79.98% | 7.092 | 136.42 | 967.4906 | 18.306 | 996.2806 | 18237.912 | 8936.9021 | 136.2917 | 19 | 38 | 0 | 0 | 29 | 1377 | 0 | 471 | 982 | 779 | 511 | 8936.9021 | 32.4583 | 0.333 | 0.417 | 11.63 | 21.08 | 17.84 | 50.15 | 0.9366 | 88.17 | 87.17 | 0.75 | 11461 | 11601 | 4.8
Week 26 | 2019-06-25 | 92.2 | 61.8% | 82.6 | 102 | 83 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3474 | 2916 | 2916 | 2855 | 2939 | 40 | 0 | 41 | 0 | 60 | 0 | 84 | -61 | 126 | 97.19% | 144.75 | 82.18% | 100% | 87.23% | 7.255 | 136.42 | 989.7271 | 23.9047 | 994.7179 | 23778.4524 | 8675.3694 | 121.5 | 0 | 0 | 0 | 0 | 18 | 1440 | 0 | 965 | 964 | 1010 | -1 | 8675.3694 | 42.0833 | 0.131 | 0.099 | 23.61 | 20.89 | 17.6 | 50.15 | 0.9366 | 88.14 | 87.32 | 0.23 | 11495 | 11708 | 5.35
| 2019-06-26 | 93.7 | 57.5% | 81 | 106 | 82 | 14 | 2 | 24 | 0 | 9 | 8 | 0 | 0 | 0 | 0 | 3358 | 3106 | 2277 | 2231 | 2308 | 40 | 0 | 41 | 0 | 60 | 0 | 77 | -46 | 123 | 78.18% | 139.9167 | 66.44% | 100% | 79.7% | 7.071 | 135.4 | 957.4134 | 18.8639 | 1000.9695 | 18882.1862 | 8892.6937 | 129.4167 | 18 | 50 | 0 | 0 | 28 | 1440 | 0 | 576 | 963 | 769 | 387 | 8892.6937 | 32.0417 | 0 | 0 | 14.23 | 20.76 | 17.38 | 50.14 | 0.9366 | 87.99 | 87.25 | 0 | 11455 | 11617 | 0
| 2019-06-27 | 91 | 60.1% | 80 | 100 | 80 | 15 | 0 | 24 | 0 | 8 | 23 | 0 | 0 | 0 | 0 | 3485 | 3182 | 2313 | 2281 | 2360 | 40 | 0 | 40 | 0 | 60 | 0 | 79 | -32 | 122 | 80.6% | 145.2083 | 65.45% | 100% | 80.29% | 7.34 | 139.55 | 1024.297 | 19.3059 | 999.2454 | 19291.3331 | 8906.4577 | 132.5833 | 23 | 37 | 0 | 0 | 27 | 1440 | 0 | 609 | 961 | 790 | 352 | 8906.4577 | 32.9167 | 0 | 0 | 15.08 | 20.8 | 17.51 | 50.09 | 0.9346 | 88.27 | 87.12 | 0 | 11513 | 11674 | 6.57
| 2019-06-28 | 96.47 | 59.49% | 84.66 | 107 | 87 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3432 | 2863 | 2863 | 2794 | 2880 | 40 | 0 | 39 | 0 | 60 | 0 | 86 | -69 | 124 | 96.77% | 143 | 81.41% | 100% | 86.33% | 7.337 | 134.18 | 984.4787 | 23.3833 | 992.3606 | 23204.7115 | 8657.5484 | 119.2917 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 953 | 946 | 981 | -7 | 8657.5484 | 40.875 | 0 | 0 | 23.43 | 20.66 | 17.64 | 50.1 | 0.9366 | 88.35 | 87.19 | 0 | 11548 | 11820 | 3.42
| 2019-06-29 | 96.86 | 56.8% | 82 | 106.5 | 84.7 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3428 | 2880 | 2880 | 2810 | 2891 | 40 | 0 | 40 | 0 | 60 | 0 | 81 | -70 | 124 | 97.14% | 142.8333 | 81.97% | 100% | 86.43% | 7.342 | 133.64 | 981.1849 | 23.3734 | 995.5204 | 23268.7399 | 8629.8665 | 120 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 957 | 949 | 985 | -8 | 8629.8665 | 41.0417 | 0 | 0 | 23.36 | 20.6 | 17.52 | 50.13 | 0.9368 | 88.18 | 87.15 | 0 | 11463 | 11729 | 0
| 2019-06-30 | 95.5 | 53.1% | 80.5 | 104 | 95 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3443 | 2895 | 2895 | 2833 | 2919 | 40 | 0 | 40 | 0 | 60 | 0 | 86 | -62 | 124 | 98.08% | 143.4583 | 82.28% | 100% | 86.43% | 7.441 | 132.86 | 988.6113 | 23.5201 | 997.461 | 23460.3998 | 8630.078 | 120.625 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 968 | 959 | 992 | -9 | 8630.078 | 41.3333 | 0 | 0 | 23.47 | 20.68 | 17.63 | 50.12 | 0.9371 | 88.1 | 87.1 | 0 | 11415 | 11681 | 4.3
| 2019-07-01 | [26 empty] | 0 | 0 |  | no data | no data | no data | #DIV/0! | no data |  |  | 0 |  |  | 0 | no data | 0 | [10 empty] | 0 | no data | 0 | [9 empty] | 0
| Monthly | 95.6037 | 47.99% | 77.9443 | 106.414 | 84.1983 | 667 | 142 | 718 | 28 | 48 | 164 | 0 | 2 | 123 | 6 | 103120 | 92381 | 87696 | 85772.63 | 88471 | 40.5333 | 0 | 40.7 | 0 | 60 | 0 | 2698.37 | -1833 | 4016 | 0.91886 | 143.2222 | 83.18% | 100% | 89.03% | 221.509 | 4037.2 | 29805.1072 | 717.5757 | 1000.1301 | 717698.5607 | 8714.944 |  | 123 | 245 | 19 | 92 | 542.5 | 35814 | 0 | 27202 | 29232 | 32037 | 2030 | 8714.944 | 1250.6667 | 17.255 | 15.848 | 661.23 | 627.04 | 537.05 | 50.1229 | 0.93736 | 87.8081 | 86.9303 |  | 11399.0323 | 11596.0323 | 75.21
| Totals | Avg.F | % Avg. |  | M Avg | m Avg | hrs | min | hrs | min | hrs | min | hrs | min | Avg Int Avi | Avg Ext Avi | MWhr Total | MWhr Total | MWhr Total | MWhr Total | MWhr Total | MW Avg | Total min | Avg MW | Total min | Avg MW | Total min | MWhr | Total MW | Av Max D/Gen | Av. DailyLF | Avg. | Avg. |  | Avg. | Total | Avg. |  | Total | Avg. |  | Avg. | [7 empty] | Total |  |  |  |  | Avg.
| Weeks data | Site Avg. Amb. Temp F | Site Avg. Relative humidity % | Site Avg. Ambient Wetbulb Temp.F | M Avg: Site Maximum/Minumum Temperature; hrs: CT-1 Base Load Hours; hrs: CT-2 Base Load Hours; hrs: CT-1 stand by hours / min; hrs: CT-2 standby hours / min | Plant ambient Corrected maximum Load hours/min |  | Average Corrected Plant Capacity | Ambient Corrected Declared Avail'y (MWH) | Av Plant WAPDA Dispatch | Net Plant Export (MWH) | Gross Generation | CT1 Av Cap (MW) | CT1 Unavail minutes | CT2 Av Cap (MW) | CT2 Unavail minutes | ST Unavail minutes | ST Average Cap (MW) | Plant Aux Load including Colony Load MWH | Differenece (+/-) MW | Maximum Daily Generation | Daily Load Factor | Avg. Corrected Plant | Plant Capacity Facto | Plant Availability Factor | Equivalent Plant Availability | LBtu gas flow mmscf | 1 LBtu gas (Average Btu/scf) | LBTU MMBTU | PL gas flow (mscf/week) | 1 PL gas (Average Btu/scf) | HBTU MMBTU | Plant Net Heat Rate (Btu/Kwh) | [11 empty] | 117.8
| Week 18 | 99.6 | 34.85% | 74.89 | 112.4629 | 85.1757 | 166 | 15 | 166 | 16 | 0 | 0 | 0 | 0 | 13 | 0 | 3398.4286 | 2997.4286 | 2997.4286 | 2908.7143 | 2995.8571 | 41 | 70 | 41.5714 | 55 | 420 | no data | no data | -621 | 129.5714 | 96.39% | 141.6012 | 85.6% | 99.22% | 87.47% | 52.696 | 136.71 | 7204.0702 | 166.0819 | 1010.4303 | 167814.2071 | 8595.046
| Week 19 | 98.1143 | 37.71% | 0 | 109.4286 | 85.1429 | 164 | 0 | 166 | 28 | 3 | 20 | 0 | 0 | 29 | 0 | 3415.5714 | 3096.1429 | 3052.5714 | 20922 | 21530 | 41 | No outage | 288 | no data | 420 | no data | 608 | -446 | 140.1429 | 91.62% | 142.3155 | 87.52% | 100% | 90.61% | 52.464 | 132.0543 | 6928.096 | 174.104 | 1001.4557 | 174357.4141 | 8664.4947 | [5 empty] | 0.27381
| Week 20 | 96.9114 | 44.78% | 77.3629 | 106.7429 | 86.5743 | 168 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 58 | 58 | 3428.7143 | 3136 | 3108 | 21296 | 21940 | 40.5714 | No outage | 285 | no data | 420 | no data | 644 | -460 | 137.2857 | 95.16% | 142.8631 | 88.75% | 100% | 92.86% | 51.861 | 133.5086 | 6923.888 | 154.7658 | 999.6796 | 154716.2295 | 8721.1526 | [5 empty] | 0.26672
| Week 21 | 90.3429 | 59.07% | 77.3629 | 101.4971 | 78.8571 | 138 | 7 | 168 | 0 | 27 | 53 | 0 | 0 | 21 | 48 | 3494.2857 | 3122.7143 | 2767.5714 | 18969 | 19566 | 40.2857 | No outage | 284 | no data | 420 | no data | 597 | -404 | 133.5714 | 87.48% | 145.5952 | 77.6% | 100% | 87.33% | 50.721 | 136.8514 | 6941.2413 | 159.5432 | 998.9421 | 159374.3885 | 8778.2627
| Week 22 | 90.9571 | 59.89% | 76.42 | 101.9257 | 79.8571 | 138 | 7 | 168 | 0 | 27 | 53 | 0 | 0 | 21 | 48 | 3487.2857 | 3106.8571 | 2751.7143 | 18861 | 19455 | 40.1429 | No outage | 284 | no data | 420 | no data | 594 | -401 | 133.1429 | 87.29% | 145.3036 | 77.33% | 100% | 87.02% | 50.647 | 137.2629 | 6951.9519 | 158.9415 | 998.004 | 158624.2172 | 8787.3509
336
| Date | Plant Status Whether Normal Operation or Tripping (State full detail for trippings/return to normal). | [61 empty] | 420
| 2019-06-01 | Plant load restricted to 118~123 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heat rate. | [61 empty] | 360
| 2019-06-02 | Plant load restricted to 118~123 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heat rate. | [61 empty] | 1116
| 2019-06-03 | Plant load restricted to 119~123 MW from 0000~1100 hrs to remain within contractual heatrate whereas load increased to maximum (ambient corrected) at 1100hrs. | [62 empty] | 22.32
| 2019-06-04 | Plant load restricted to 121~126 MW from 0100~1900 hrs to remain within contractual heatrate whereas load increased to maximum (ambient corrected) at 1900 hrs.
| 2019-06-05 | Plant load restricted to 121~126 MW from 0000~2400 hrs as both DBs kept on minimum firing to remain within contractual heatrate.
| 2019-06-06 | CT-1 de-synch @ 0454 hrs as per NPCC load demand of 62 MW. CT-1 synch @ 0814 hrs as per NPCC maximum load demand. Plant load increased to maximum (ambient corrected) at 2000 hrs by increasing DBs firing.
| 2019-06-07 | Plant load restricted to 122~126 MW from 0520~2200 hrs as both DBs kept on minimum firing to remain within contractual heatrate.
| 2019-06-08 | Plant load restricted to 121~126 MW from 0100~2400 hrs as both DBs kept on minimum firing to remain within contractual heatrate.
| 2019-06-09 | Plant load restricted to 121~126 MW from 0100~2400 hrs as both DBs kept on minimum firing to remain within contractual heatrate.
| 2019-06-10 | Plant load restricted to 121~125 MW from 0000~1200 hrs and 2300~2400 hrs to remain within contractual heat rate.
| 2019-06-11 | Plant load restricted to 122~125 MW from 0000~1100 hrs and 2300~2400 hrs to remain within contractual heat rate.
| 2019-06-12 | Plant load restricted to 122~125 MW from 0000~1100 hrs to remain within contractual heatrate.Plant load remained restricted to 123 MW from 1552~1610 hrs at NPCC demand and again load demand of 123 MW received at 1936 hrs from NPCC.
| 2019-06-13 | Plant load remained restricted to 123 MW from 0000~0855 hrs. Plant load remained restricted to 122 MW from 1015~1035 hrs and 1311~1409 hrs as per NPCC demand.
| 2019-06-14 | Plant load restricted to 122~125 MW from 0000~1100 hrs to remain within contractual heat rate.
| 2019-06-15 | Plant load restricted to 119~122 MW from 0000~1100 hrs to remain within contractual heat rate.
| 2019-06-16 | Plant load restricted to 119~125 MW from 0000~2400 hrs to remain within contractual heat rate.
| 2019-06-17 | Plant load restricted to 119~125 MW from 0000~2400 hrs to remain within contractual heat rate.
| 2019-06-18 | Plant load restricted to 121~125 MW from 0000~2400 hrs to remain within contractual heat rate.
| 2019-06-19 | Plant load restricted to 123~125 MW from 0000~1100 hrs to remain within contractual heat rate.
| 2019-06-20 | Plant load restricted to 120~122 MW from 0000~1100 hrs to remain within contractual heat rate. Plant load reduced to 120 MW from 1813 hrs and CT-1 de-synch @ 1927 hrs as per NPCC load demand of 61 MW.
| 2019-06-21 | CT-1 synch @ 0920 hrs as per NPCC maximum load demand. Plant load restricted to 120~124 MW from 1100~2400 hrs to remain within contractual heat rate.
| 2019-06-22 | Plant load restricted to 119~122 MW from 0000~2400 hrs to remain within contractual heat rate.
| 2019-06-23 | Plant load restricted to 119~123 MW from 0000~2150 hrs to remain within contractual heat rate. CT-1 desynch @ 2206 hrs to meet NPCC load demand of 61 MW.
| 2019-06-24 | CT-1 synch @ 1206 hrs as per NPCC maximum load demand. Plant load restricted to 120~123 MW from 1400~2400 hrs to remain within contractual heat rate.
| 2019-06-25 | Plant load restricted to 116~122 MW from 0000~2400 hrs to remain within contractual heat rate.
| 2019-06-26 | CT-1 de-synch @ 0258 hrs as per NPCC demand of 58 MW. CT-1 synch @ 0828 hrs as per NPCC demand of maximum load complex. CT-1 de-synch @ 2022 hrs as per NPCC demand of 60 MW.
| 2019-06-27 | CT-1 synch @ 0823 hrs as per NPCC demand. Plant load restricted to 115~118 MW from 0908~2400 hrs to remain within contractual heat rate.
| 2019-06-28 | Plant load restricted to 114~120 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2019-06-29 | Plant load restricted to 115~121 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2019-06-30 | Plant load restricted to 116~121 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heatrate.
186
[16 empty] | 3.1 | 20.9
0.9
[5 empty] | min: 93.916 |  |  | 54
43.13
137.046
[12 empty] | 44.6404 |  | 3.07
b
Note on BN34: ops.e: assumed due to problem of GC of OGDCL.

## July
Monthly Operational Returns Kabirwala
2019-07-01
| Date | Site Avg. Ambient Temp.F | Site Avg. Relative Humidty % | Site Avg. Ambient Wetbulb Temp.F | Site Ambient Temp |  | Base load hours |  |  |  | Standby hours |  |  |  | Plant ambient corrected Max Load |  | Corrected Plant Capacity | Ambient Corrected Daclared Avail'y (MWH) | Plant WAPDA Dispatch (MWH) | Net Plant Export (MWH) | Gross Generation | CT1 Average Cap (MW) | CT1 Unavail minutes | CT2 Average Cap (MW) | CT2 Unavail minutes | ST Average Cap (MW) | ST Unavail minutes | Plant Aux Load including Colony Load MWH | Differenece (+/-) MW | Maximum Daily Generation | Daily Load Factor | Avg. Corrected Plant Capacity | Plant Capacity Factor | Plant Availability Factor | Equivalent Plant Availability | LBtu gas flow (mmscf/day) | 1 LBtu gas (Average Btu/scf) | LBTU MMBTU | 1 HBtu gas flow (mmscf/day) | 1 HBtu gas (Average Btu/scf) | HBTU MMBTU | HHV Net Heat Rate (Btu/Kwh) | Avg. declared availability | CT1 Derated MW | CT1 derated mintutes | CT-2 derated MW | CT-2 derated mintutes | ST derated MW | ST derated mintutes | WAPDA Backfeed (MWH) | CT-1 Gross Generation (MWH) | CT-2 Gross Generation (MWH) | STG Gross Generation (MWH) | CT-1 & CT-2 MWH difference | Base load Heat Rate | STG load | DB1 | DB2 | CT1 Gas flow | CT2 Gas flow |  | Freq. Hz | LBTU Gas Specific gravity | CT-1 compressor efficiency(%) | CT-2 compressor efficiency(%) | DB(1+2) | CT-1 Heat Rate (Btu/Kwh) | CT-2 Heat Rate (Btu/Kwh) | RO Operation Hours
[7 empty] | CT1 |  | CT2 |  | CT1 |  | CT2 | [43 empty] | mmscf/d | mmscf/d | HBTU KPPH | HBTU KPPH | LBTU KPPH | Hz |  |  |  | mmscf/d
[5 empty] | Max | Min | hrs | min | hrs | min | hrs | min | hrs | min | hrs | min
Week 26 | 2019-06-25 | 92.2 | 61.8% | 82.6 | 102 | 83 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3474 | 2916 | 2916 | 2855 | 2939 | 40 | 0 | 41 | 0 | 60 | 0 | 84 | -61 | 126 | 97.19% | 144.75 | 82.18% | 100% | 87.23% | 7.255 | 136 | 986.68 | 23.904 | 994.7289 | 23777.9996 | 8674.1435 | 121.5 | 0 | 0 | 0 | 0 | 18 | 1440 | 0 | 965 | 964 | 1010 | -1 | 8674.1435 | 42.0833 | 0.131 | 0.099 | 23.61 | 20.89 | 17.6 | 50.15 | 0.9366 | 88.14 | 87.32 | 0.23 | 11495 | 11708 | 5.35
| 2019-06-26 | 93.7 | 57.5% | 81 | 106 | 82 | 14 | 2 | 24 | 0 | 9 | 8 | 0 | 0 | 0 | 0 | 3358 | 3106 | 2277 | 2231 | 2308 | 40 | 0 | 41 | 0 | 60 | 0 | 77 | -46 | 123 | 78.18% | 139.9167 | 66.44% | 100% | 79.7% | 7.071 | 135.4 | 957.4134 | 18.863 | 1001.007 | 18881.995 | 8892.608 | 129.4167 | 18 | 50 | 0 | 0 | 28 | 1440 | 0 | 576 | 963 | 769 | 387 | 8892.608 | 32.0417 | 0 | 0 | 14.23 | 20.76 | 17.38 | 50.14 | 0.9366 | 87.99 | 87.25 | 0 | 11455 | 11617 | 0
| 2019-06-27 | 91 | 60.1% | 80 | 100 | 80 | 15 | 0 | 24 | 0 | 8 | 23 | 0 | 0 | 0 | 0 | 3485 | 3182 | 2313 | 2281 | 2360 | 40 | 0 | 40 | 0 | 60 | 0 | 79 | -32 | 122 | 80.6% | 145.2083 | 65.45% | 100% | 80.29% | 7.34 | 139.55 | 1024.297 | 19.305 | 999.27 | 19290.9074 | 8906.2711 | 132.5833 | 23 | 37 | 0 | 0 | 27 | 1440 | 0 | 609 | 961 | 790 | 352 | 8906.2711 | 32.9167 | 0 | 0 | 15.08 | 20.8 | 17.51 | 50.09 | 0.9346 | 88.27 | 87.12 | 0 | 11513 | 11674 | 6.57
| 2019-06-28 | 96.47 | 59.49% | 84.66 | 107 | 87 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3432 | 2863 | 2863 | 2794 | 2880 | 40 | 0 | 39 | 0 | 60 | 0 | 86 | -69 | 124 | 96.77% | 143 | 81.41% | 100% | 86.33% | 7.337 | 134.18 | 984.4787 | 23.3833 | 992.3606 | 23204.7115 | 8657.5484 | 119.2917 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 953 | 946 | 981 | -7 | 8657.5484 | 40.875 | 0 | 0 | 23.43 | 20.66 | 17.64 | 50.1 | 0.9366 | 88.35 | 87.19 | 0 | 11548 | 11820 | 3.42
| 2019-06-29 | 96.86 | 56.8% | 82 | 106.5 | 84.7 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3428 | 2880 | 2880 | 2810 | 2891 | 40 | 0 | 40 | 0 | 60 | 0 | 81 | -70 | 124 | 97.14% | 142.8333 | 81.97% | 100% | 86.43% | 7.342 | 133.64 | 981.1849 | 23.3734 | 995.5204 | 23268.7399 | 8629.8665 | 120 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 957 | 949 | 985 | -8 | 8629.8665 | 41.0417 | 0 | 0 | 23.36 | 20.6 | 17.52 | 50.13 | 0.9368 | 88.18 | 87.15 | 0 | 11463 | 11729 | 0
| 2019-06-30 | 95.5 | 53.1% | 80.5 | 104 | 85 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3443 | 2895 | 2895 | 2833 | 2919 | 40 | 0 | 40 | 0 | 60 | 0 | 86 | -62 | 124 | 98.08% | 143.4583 | 82.28% | 100% | 86.43% | 7.441 | 132.86 | 988.6113 | 23.5201 | 997.461 | 23460.3998 | 8630.078 | 120.625 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 968 | 959 | 992 | -9 | 8630.078 | 41.3333 | 0 | 0 | 23.47 | 20.68 | 17.63 | 50.12 | 0.9371 | 88.1 | 87.1 | 0 | 11415 | 11681 | 4.3
| 2019-07-01 | 99 | 54.1% | 83 | 108 | 90 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3401 | 2867 | 2867 | 2795 | 2880 | 40 | 0 | 39 | 0 | 60 | 0 | 85 | -72 | 121 | 99.17% | 141.7083 | 82.18% | 100% | 86.33% | 7.28 | 134.88 | 981.9264 | 23.3108 | 997.3051 | 23247.98 | 8669.0184 | 119.4583 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 951 | 946 | 983 | -5 | 8669.0184 | 40.9583 | 0 | 0 | 23.27 | 20.52 | 17.49 | 50.1 | 0.9365 | 88.19 | 87.15 | 0 | 11477 | 11729 | 0.8
Week 27 | 2019-07-02 | 98 | 55% | 82 | 108 | 86 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3418 | 2874 | 2874 | 2813 | 2900 | 40 | 0 | 40 | 0 | 60 | 0 | 87 | -61 | 123 | 98.24% | 142.4167 | 82.3% | 100% | 86.43% | 7.29 | 136.1 | 992.169 | 23.3825 | 998.9244 | 23357.39 | 8656.0821 | 119.75 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 959 | 954 | 987 | -5 | 8656.0821 | 41.125 | 0 | 0 | 23.3 | 20.62 | 17.44 | 50.13 | 0.9359 | 88.06 | 87.18 | 0 | 11426 | 11682 | 0.5
| 2019-07-03 | 99.2 | 52.1% | 81.9 | 110 | 86 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3407 | 2873 | 2873 | 2806 | 2893 | 40 | 0 | 40 | 0 | 60 | 0 | 87 | -67 | 124 | 97.21% | 141.9583 | 82.36% | 100% | 86.43% | 7.18 | 135.92 | 975.9056 | 23.3575 | 999.4152 | 23343.88 | 8667.0654 | 119.7083 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 957 | 951 | 985 | -6 | 8667.0654 | 41.0417 | 0 | 0 | 23.29 | 20.58 | 17.34 | 50.15 | 0.9361 | 88.1 | 87.15 | 0 | 11437 | 11686 | 3.25
| 2019-07-04 | 99.5 | 51.3% | 81.7 | 110 | 88 | 23 | 3 | 24 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 3404 | 2821 | 2821 | 2759 | 2849 | 40 | 0 | 40 | 0 | 60 | 0 | 90 | -62 | 122 | 97.3% | 141.8333 | 81.05% | 100% | 85.6% | 7.18 | 134.81 | 967.9358 | 22.9969 | 997.8749 | 22948.04 | 8668.3493 | 117.5417 | 16 | 15 | 0 | 0 | 20 | 1440 | 0 | 924 | 954 | 971 | 30 | 8668.3493 | 40.4583 | 0 | 0 | 22.55 | 20.6 | 17.28 | 50.17 | 0.9362 | 88.06 | 87.12 | 0 | 11452 | 11674 | 5.25
| 2019-07-05 | 96.8 | 59.8% | 84.9 | 107 | 87 | 16 | 33 | 24 | 0 | 7 | 6 | 0 | 0 | 0 | 0 | 3429 | 3032 | 2384 | 2326 | 2409 | 39 | 0 | 39 | 0 | 60 | 0 | 83 | -58 | 120 | 83.65% | 142.875 | 67.83% | 100% | 80.96% | 6.9 | 131.35 | 906.315 | 19.6955 | 997.3684 | 19643.62 | 8834.8818 | 126.3333 | 19 | 21 | 0 | 0 | 26 | 1440 | 0 | 657 | 940 | 812 | 283 | 8834.8818 | 33.8333 | 0 | 0 | 16.25 | 20.51 | 17.09 | 50.14 | 0.9375 | 88.37 | 87.29 | 0 | 11522 | 11755 | 0
| 2019-07-06 | 92.3 | 61.2% | 81.9 | 99 | 82 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3474 | 2868 | 2868 | 2816 | 2901 | 40 | 0 | 40 | 0 | 60 | 0 | 85 | -52 | 124 | 97.48% | 144.75 | 81.06% | 100% | 86.43% | 6.8 | 132.63 | 901.884 | 23.5227 | 996.8384 | 23448.38 | 8647.1108 | 119.5 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 962 | 955 | 984 | -7 | 8647.1108 | 41 | 0 | 0 | 23.43 | 20.69 | 17.35 | 50.15 | 0.9365 | 88.18 | 87.21 | 0 | 11444 | 11685 | 4.4
| 2019-07-07 | 94.6 | 59.5% | 83.8 | 104 | 86 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3452 | 2861 | 2861 | 2804 | 2889 | 40 | 0 | 40 | 0 | 60 | 0 | 85 | -57 | 122 | 98.67% | 143.8333 | 81.23% | 100% | 86.43% | 6.8 | 130.55 | 887.74 | 23.439 | 996.6295 | 23359.96 | 8647.5392 | 119.2083 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 955 | 952 | 982 | -3 | 8647.5392 | 40.9167 | 0 | 0 | 23.33 | 20.64 | 17.09 | 50.13 | 0.9373 | 88.23 | 87.22 | 0 | 11459 | 11683 | 0
| 2019-07-08 | 99.5 | 55.5% | 84 | 108 | 90 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3399 | 2834 | 2834 | 2770 | 2856 | 39 | 0 | 39 | 0 | 60 | 0 | 86 | -64 | 121 | 98.35% | 141.625 | 81.49% | 100% | 86.23% | 6.7 | 134.78 | 903.026 | 23.2334 | 996.6445 | 23155.42 | 8685.3596 | 118.0833 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 945 | 937 | 974 | -8 | 8685.3596 | 40.5833 | 0 | 0 | 23.13 | 20.46 | 16.09 | 50.11 | 0.9353 | 88.24 | 87.3 | 0 | 11507 | 11713 | 3.4
Week 28 | 2019-07-09 | 97.9 | 57.4% | 84.2 | 105 | 93 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3419 | 2832 | 2832 | 2768 | 2855 | 39 | 0 | 39 | 0 | 60 | 0 | 87 | -64 | 121 | 98.31% | 142.4583 | 80.96% | 100% | 85.51% | 6.7 | 132.76 | 889.492 | 23.0205 | 1006.956 | 23180.65 | 8695.8605 | 118 | 0 | 0 | 0 | 0 | 20 | 1440 | 0 | 943 | 939 | 973 | -4 | 8695.8605 | 40.5417 | 0 | 0 | 22.96 | 20.42 | 15.82 | 50.15 | 0.9355 | 88.1 | 87.43 | 0 | 11437 | 11616 | 0
| 2019-07-10 | 97.92 | 62.2% | 84.85 | 104.4 | 92.58 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3417 | 2821 | 2821 | 2757 | 2849 | 39 | 0 | 39 | 0 | 60 | 0 | 92 | -64 | 120 | 98.92% | 142.375 | 80.68% | 100% | 85.51% | 6.6 | 130.58 | 861.828 | 22.9548 | 1009.9418 | 23182.99 | 8721.3703 | 117.5417 | 0 | 0 | 0 | 0 | 20 | 1440 | 0 | 939 | 940 | 970 | 1 | 8721.3703 | 40.4167 | 0 | 0 | 22.92 | 20.4 | 15.76 | 50.11 | 0.9362 | 88.15 | 87.43 | 0 | 11447 | 11619 | 4.75
| 2019-07-11 | 96.61 | 60.71% | 83.98 | 104.5 | 91.5 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3430 | 2831 | 2831 | 2770 | 2861 | 39 | 0 | 39 | 0 | 60 | 0 | 91 | -61 | 121 | 98.52% | 142.9167 | 80.76% | 100% | 86.23% | 6.6 | 129.73 | 856.218 | 23.1079 | 1006.1144 | 23249.221 | 8702.3245 | 117.9583 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 944 | 943 | 974 | -1 | 8702.3245 | 40.5833 | 0 | 0 | 23.05 | 20.5 | 15.8 | 50.15 | 0.9363 | 88.1 | 87.35 | 0 | 11479 | 11618 | 0
| 2019-07-12 | 96 | 62% | 83.35 | 102 | 90 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3437 | 2839 | 2839 | 2780 | 2870 | 39 | 0 | 39 | 0 | 60 | 0 | 90 | -59 | 121 | 98.83% | 143.2083 | 80.88% | 100% | 86.23% | 6.6 | 128.92 | 850.872 | 23.2205 | 1005.1136 | 23339.25 | 8701.4827 | 118.2917 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 947 | 946 | 977 | -1 | 8701.4827 | 40.7083 | 0 | 0 | 23.12 | 20.61 | 15.88 | 50.13 | 0.9366 | 88.03 | 87.31 | 0 | 11473 | 11622 | 0
| 2019-07-13 | 96 | 62% | 83 | 103 | 89 | 23 | 35 | 23 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 3436 | 2810 | 2810 | 2753 | 2842 | 39 | 0 | 39 | 0 | 60 | 34 | 89 | -57 | 121 | 97.87% | 143.1667 | 80.12% | 98.97% | 84.6% | 6.65 | 133.87 | 890.2355 | 23.2012 | 1004.2753 | 23300.391 | 8787.0056 | 117.0833 | 9 | 25 | 9 | 25 | 20 | 1406 | 0 | 943 | 946 | 953 | 3 | 8787.0056 | 39.7083 | 0 | 0 | 23.05 | 20.61 | 15.95 | 50.16 | 0.9348 | 87.74 | 87.32 | 0 | 11487 | 11645 | 0
| 2019-07-14 | 95.7 | 60.3% | 82.9 | 102 | 91 | 24 | 0 | 12 | 26 | 7 | 6 | 0 | 0 | 0 | 0 | 3440 | 2754 | 2140 | 2102 | 2187 | 39 | 0 | 39 | 213 | 60 | 0 | 85 | -38 | 121 | 75.31% | 143.3333 | 61.1% | 95.82% | 73.58% | 3.459 | 145.91 | 504.7027 | 18.1552 | 1002.5994 | 18202.391 | 8899.664 | 114.75 | 0 | 0 | 18 | 55 | 30 | 1440 | 0 | 946 | 510 | 731 | -436 | 8899.664 | 30.4583 | 0 | 0 | 23.12 | 11.37 | 8.6 | 50.14 | 0.9308 | 87.66 | 87.55 | 0 | 11480 | 11648 | 5.87
| 2019-07-15 | 93.4 | 66.2% | 85.6 | 101 | 87 | 9 | 47 | 24 | 0 | 13 | 22 | 0 | 0 | 0 | 0 | 3466 | 3169 | 1985 | 1948 | 2030 | 39 | 0 | 39 | 0 | 60 | 0 | 82 | -37 | 120 | 70.49% | 144.4167 | 56.2% | 100% | 76.27% | 6.6 | 127.94 | 844.404 | 16.5273 | 1009.5031 | 16684.35 | 8998.3337 | 132.0417 | 19 | 57 | 0 | 0 | 32 | 1440 | 0 | 399 | 952 | 679 | 553 | 8998.3337 | 28.2917 | 0 | 0 | 22.91 | 20.6 | 15.9 | 50.11 | 0.937 | 87.77 | 87.56 | 0 | 11444 | 11561 | 0
Week 29 | 2019-07-16 | 92.5 | 66.8% | 85 | 100 | 86 | 1 | 5 | 24 | 0 | 22 | 41 | 0 | 0 | 0 | 0 | 3476 | 3362 | 1468 | 1426 | 1503 | 39 | 0 | 39 | 0 | 60 | 0 | 77 | -42 | 120 | 52.19% | 144.8333 | 41.02% | 100% | 85.39% | 6.5 | 134.12 | 871.78 | 11.9988 | 1017.7101 | 12211.28 | 9174.6564 | 140.0833 | 17 | 14 | 0 | 0 | 20 | 1440 | 0 | 48 | 955 | 500 | 907 | 9107.8452 | 20.8333 | 0 | 0 | 23.1 | 20.63 | 15.88 | 50.12 | 0.9347 | 87.63 | 87.51 | 0 | 11323 | 11524 | 4.87
| 2019-07-17 | 90.9 | 65.6% | 83.4 | 100 | 81 | 9 | 41 | 14 | 51 | 13 | 36 | 7 | 45 | 0 | 0 | 3489 | 3154 | 1485 | 1456 | 1516 | 39 | 0 | 39 | 0 | 60 | 0 | 70 | -29 | 120 | 52.64% | 145.375 | 41.73% | 100% | 86.75% | 4.272 | 136.37 | 582.5726 | 12.4401 | 1019.1598 | 12678.45 | 9107.8452 | 131.4167 | 20 | 43 | 14 | 84 | 27 | 900 | 10 | 395 | 625 | 496 | 230 | 8693.8783 | 20.6667 | 0 | 0 | 9.84 | 13.67 | 10.59 | 51.14 | 0.9342 | 87.8 | 87.49 | 0 | 11468 | 11577 | 0
| 2019-07-18 | 87.4 | 72.2% | 84.5 | 101 | 76 | 18 | 53 | 24 | 0 | 4 | 52 | 0 | 0 | 0 | 0 | 3528 | 3007 | 2576 | 2530 | 2612 | 40 | 0 | 40 | 0 | 60 | 0 | 82 | -46 | 125 | 87.07% | 147 | 71.71% | 100% | 83.43% | 6.1 | 126.43 | 771.223 | 20.879 | 1016.5366 | 21224.289 | 8693.8783 | 125.2917 | 19 | 15 | 0 | 0 | 23 | 1440 | 0 | 762 | 963 | 887 | 201 | 8693.8783 | 36.9583 | 0 | 0 | 23.26 | 20.87 | 15.98 | 50.18 | 0.9371 | 87.94 | 87.38 | 0 | 11379 | 11566 | 5.3
| 2019-07-19 | 88.1 | 70.3% | 83.4 | 97 | 80 | 0 | 0 | 16 | 58 | 24 | 0 | 5 | 30 | 0 | 0 | 3519 | 3446 | 1004 | 999 | 1058 | 40 | 0 | 40 | 0 | 60 | 0 | 65 | -5 | 61 | 72.27% | 146.625 | 28.39% | 100% | 78.61% | 4.174 | 133.65 | 557.8551 | 8.5752 | 1020.9681 | 8754.963 | 9322.1402 | 143.5833 | 0 | 0 | 17 | 92 | 40 | 1039 | 6 | 0 | 719 | 339 | 719 | 9322.1402 | 14.125 | 0 | 0 | 0 | 20.2 | 15.6 | 50.18 | 0.9353 | 0 | 87.34 | 0 | 0 | 11716 | 0
| 2019-07-20 | 91.3 | 66.7% | 84.5 | 98.6 | 82.8 | 14 | 57 | 24 | 0 | 8 | 27 | 0 | 0 | 0 | 0 | 3484 | 3111 | 2313 | 2271 | 2358 | 40 | 0 | 40 | 0 | 60 | 0 | 87 | -42 | 122 | 80.53% | 145.1667 | 65.18% | 100% | 76.04% | 5.7 | 127.56 | 727.092 | 19.0004 | 1015.4318 | 19293.631 | 8815.8181 | 129.625 | 22 | 36 | 0 | 0 | 33 | 1440 | 0 | 606 | 959 | 793 | 353 | 8815.8181 | 33.0417 | 0 | 0 | 9.05 | 20.9 | 15.7 | 50.14 | 0.9371 | 87.76 | 87.29 | 0 | 11244 | 11630 | 5.75
| 2019-07-21 | 93.5 | 66.6% | 86.4 | 101 | 86 | 24 | 0 | 1 | 5 | 0 | 0 | 9 | 9 | 0 | 0 | 3461 | 2267 | 1427 | 1401 | 1474 | 40 | 0 | 40 | 810 | 60 | 0 | 73 | -26 | 120 | 51.18% | 144.2083 | 40.48% | 83.93% | 55.16% | 0.225 | 123.72 | 27.837 | 12.5858 | 1006.2126 | 12663.99 | 9059.1199 | 94.4583 | 0 | 0 | 25 | 16 | 40 | 1440 | 0 | 948 | 47 | 479 | -901 | 9059.1199 | 19.9583 | 0 | 0 | 23.08 | 0.83 | 1.14 | 50.15 | 0.9379 | 87.99 | 87.4 | 0 | 11408 | 11715 | 0
| 2019-07-22 | 94.1 | 65.7% | 86.5 | 102 | 86 | 24 | 0 | 18 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 3458 | 2543 | 2511 | 2453 | 2543 | 40 | 0 | 40 | 301 | 60 | 0 | 90 | -58 | 122 | 86.85% | 144.0833 | 70.94% | 94.03% | 76.47% | 4.267 | 134.26 | 572.8874 | 20.8693 | 1005.9835 | 20994.16 | 8792.1106 | 105.9583 | 0 | 0 | 22 | 38 | 24 | 1440 | 0 | 949 | 740 | 854 | -209 | 8792.1106 | 35.5833 | 0 | 0 | 23.26 | 16.31 | 12.38 | 50.15 | 0.9348 | 88.05 | 87.45 | 0 | 11534 | 11688 | 5.77
Week 30 | 2019-07-23 | 96.1 | 60% | 85.1 | 105 | 87 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3441 | 2860 | 2860 | 2791 | 2880 | 40 | 0 | 40 | 0 | 60 | 0 | 89 | -69 | 121 | 99.17% | 143.375 | 81.11% | 100% | 86.43% | 5.72 | 126.41 | 723.0652 | 23.3983 | 1007.0129 | 23562.359 | 8701.3344 | 119.1667 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 947 | 949 | 984 | 2 | 8701.3344 | 41 | 0 | 0 | 23.24 | 20.86 | 15.84 | 50.13 | 0.9376 | 87.99 | 87.41 | 0 | 11532 | 11739 | 0
| 2019-07-24 | 98.8 | 59.9% | 86.4 | 108 | 90 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3407 | 2834 | 2834 | 2765 | 2850 | 39 | 0 | 39 | 0 | 60 | 0 | 85 | -69 | 121 | 98.14% | 141.9583 | 81.16% | 100% | 85.51% | 5.75 | 131.77 | 757.6775 | 23.3778 | 1002.7295 | 23441.57 | 8751.9882 | 118.0833 | 0 | 0 | 0 | 0 | 20 | 1440 | 0 | 936 | 938 | 976 | 2 | 8751.9882 | 40.6667 | 0 | 0 | 23.15 | 20.73 | 15.75 | 50.14 | 0.9358 | 88 | 87.44 | 0 | 11622 | 11803 | 0
| 2019-07-25 | 95.8 | 60.9% | 83.9 | 102 | 86 | 15 | 53 | 21 | 35 | 5 | 11 | 0 | 0 | 0 | 0 | 3439 | 2981 | 2261 | 2222 | 2302 | 40 | 106 | 40 | 79 | 60 | 133 | 81 | -39 | 123 | 77.98% | 143.2917 | 64.61% | 92.37% | 75.28% | 5.323 | 125.66 | 668.8882 | 19.3612 | 1001.891 | 19397.7905 | 9030.9085 | 124.2083 | 15 | 70 | 11 | 66 | 25 | 1307 | 1 | 660 | 880 | 762 | 220 | 9030.9085 | 31.75 | 0 | 0 | 16.54 | 19.56 | 15 | 50.16 | 0.9377 | 88.18 | 87.34 | 0 | 11585 | 11805 | 6.2
| 2019-07-26 | 86.2 | 75.8% | 85.2 | 93 | 78 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3536 | 2895 | 2895 | 2829 | 2917 | 40 | 0 | 40 | 0 | 60 | 0 | 88 | -66 | 124 | 98.02% | 147.3333 | 80.01% | 100% | 86.43% | 5.62 | 125.93 | 707.7266 | 24.0018 | 999.9308 | 24000.18 | 8733.7952 | 120.625 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 968 | 957 | 992 | -11 | 8733.7952 | 41.3333 | 0 | 0 | 23.66 | 20.99 | 16 | 50.14 | 0.9373 | 88.14 | 87.28 | 0 | 11497 | 11701 | 0
| 2019-07-27 | 88.5 | 74.4% | 86.7 | 97 | 83 | 10 | 52 | 18 | 40 | 9 | 52 | 5 | 2 | 0 | 0 | 3510 | 2917 | 1800 | 1743 | 1805 | 39 | 0 | 39 | 0 | 60 | 0 | 67 | -57 | 121 | 62.16% | 146.25 | 49.66% | 100% | 83.46% | 4.392 | 127.28 | 559.0138 | 14.9535 | 999.8502 | 14951.25 | 8898.6023 | 121.5417 | 22 | 35 | 13 | 18 | 32 | 996 | 5 | 455 | 741 | 609 | 286 | 8898.6023 | 25.375 | 0 | 0 | 11.4 | 16.38 | 12.37 | 50.12 | 0.9371 | 88.24 | 87.37 | 0 | 11577 | 11765 | 6
| 2019-07-28 | 87.8 | 75.7% | 86.9 | 94 | 84 | 0 | 0 | 16 | 29 | 24 | 0 | 6 | 31 | 0 | 0 | 3514 | 3440 | 938 | 941 | 994 | 39 | 0 | 39 | 0 | 60 | 0 | 60 | 3 | 60 | 69.03% | 146.4167 | 26.78% | 100% | 79.28% | 3.987 | 138.71 | 553.0368 | 8.2486 | 999.8974 | 8247.718 | 9352.5555 | 143.3333 | 0 | 0 | 18 | 60 | 41 | 978 | 7 | 0 | 677 | 317 | 677 | 9352.5555 | 13.2083 | 0 | 0 | 0 | 15.19 | 11.2 | 50.13 | 0.9333 | 0 | 87.34 | 0 | 0 | 11796 | 0
| 2019-07-29 | 87.03 | 77.02% | 87.05 | 98 | 84 | 14 | 27 | 24 | 0 | 8 | 45 | 0 | 0 | 0 | 0 | 3526 | 3124 | 2279 | 2247 | 2326 | 39 | 0 | 39 | 0 | 60 | 0 | 79 | -32 | 122 | 79.44% | 146.9167 | 63.73% | 100% | 79.99% | 5.6 | 127.27 | 712.712 | 19.1619 | 1000.5725 | 19172.92 | 8849.8585 | 130.1667 | 21 | 42 | 0 | 0 | 27 | 1440 | 0 | 592 | 955 | 779 | 363 | 8849.8585 | 32.4583 | 0 | 0 | 14.69 | 20.91 | 16.05 | 50.12 | 0.9369 | 88.23 | 87.35 | 0 | 11494 | 11691 | 7.05
Week 31 | 2019-07-30 | 92.6 | 61.1% | 86.5 | 101 | 84 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3469 | 2853 | 2853 | 2792 | 2880 | 40 | 0 | 40 | 0 | 60 | 0 | 88 | -61 | 122 | 98.36% | 144.5417 | 80.48% | 100% | 86.43% | 5.6 | 130.56 | 731.136 | 23.3483 | 1010.8016 | 23600.449 | 8714.7511 | 118.875 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 951 | 947 | 982 | -4 | 8714.7511 | 40.9167 | 0 | 0 | 23.26 | 20.76 | 15.53 | 50.14 | 0.9359 | 88.22 | 87.42 | 0 | 11481 | 11720 | 0
| 2019-07-31 | 95.9 | 63.7% | 86.5 | 106 | 87 | 20 | 23 | 24 | 0 | 3 | 37 | 0 | 0 | 0 | 0 | 3442 | 2921 | 2593 | 2538 | 2623 | 39 | 0 | 39 | 0 | 60 | 0 | 85 | -55 | 120 | 91.08% | 143.4167 | 73.74% | 100% | 83.07% | 5.54 | 131.38 | 727.8452 | 21.3749 | 1009.8334 | 21585.119 | 8791.5541 | 121.7083 | 17 | 31 | 0 | 0 | 23 | 1440 | 0 | 793 | 940 | 890 | 147 | 8791.5541 | 37.0833 | 0 | 0 | 19.61 | 20.66 | 15.68 | 50.11 | 0.9358 | 88.23 | 87.47 | 0 | 11550 | 11748 | 5.45
2019-08-01
2019-08-02
2019-08-03
2019-08-04
| 2019-08-05 | [39 empty] | 0 | no data | 0 | [10 empty] | 0 | no data | 0 | [9 empty] | 0
| Monthly | 94.16 | 63.28% | 84.4848 | 102.5645 | 86.1252 | 587 | 440 | 672 | 302 | 153 | 377 | 33 | 117 | 0 | 0 | 107128 | 90801 | 74737 | 73096.46 | 75712 | 39.4839 | 106 | 39.4516 | 1403 | 60 | 167 | 2644.54 | -1566 | 117.6129 | 85.95% | 143.9892 | 68.42% | 98.87% | 82.27% | 178.109 | 131.6713 | 23467.0024 | 616.7006 | 1005.1621 | 619424.0315 | 8795.1049 |  | 6.9677 | 404 | 4.7419 | 454 | 24.2581 | 42626 | 29 | 23381 | 26757 | 25574 | 3376 | 8795.1049 | 34.3737 | 0 | 0 | 596.09 | 567.53 | 449.46 | 50.1656 | 0.9361 | 82.8826 | 87.3321 |  | 11095.3871 | 11674.871 | 66.41
| Totals | Avg.F | % Avg. |  | M Avg | m Avg | hrs | min | hrs | min | hrs | min | hrs | min | Avg Int Avi | Avg Ext Avi | MWhr Total | MWhr Total | MWhr Total | MWhr Total | MWhr Total | MW Avg | Total min | Avg MW | Total min | Avg MW | Total min | MWhr | Total MW | Av Max D/Gen | Av. DailyLF | Avg. | Avg. |  | Avg. | Total | Avg. |  | Total | Avg. |  | Avg. | [7 empty] | Total |  |  |  |  | Avg.
| Weeks data | Site Avg. Amb. Temp F | Site Avg. Relative humidity % | Site Avg. Ambient Wetbulb Temp.F | M Avg: Site Maximum/Minumum Temperature; hrs: CT-1 Base Load Hours; hrs: CT-2 Base Load Hours; hrs: CT-1 stand by hours / min; hrs: CT-2 standby hours / min | Plant ambient Corrected maximum Load hours/min |  | Average Corrected Plant Capacity | Ambient Corrected Declared Avail'y (MWH) | Av Plant WAPDA Dispatch | Net Plant Export (MWH) | Gross Generation | CT1 Av Cap (MW) | CT1 Unavail minutes | CT2 Av Cap (MW) | CT2 Unavail minutes | ST Unavail minutes | ST Average Cap (MW) | Plant Aux Load including Colony Load MWH | Differenece (+/-) MW | Maximum Daily Generation | Daily Load Factor | Avg. Corrected Plant | Plant Capacity Facto | Plant Availability Factor | Equivalent Plant Availability | LBtu gas flow mmscf | 1 LBtu gas (Average Btu/scf) | LBTU MMBTU | PL gas flow (mscf/week) | 1 PL gas (Average Btu/scf) | HBTU MMBTU | Plant Net Heat Rate (Btu/Kwh) | [11 empty] | 482
| Week 26 | 94.9614 | 57.56% | 81.9657 | 104.7857 | 84.5286 | 149 | 2 | 168 | 0 | 17 | 31 | 0 | 0 | 0 | 0 | 3431.5714 | 2958.4286 | 2715.8571 | 2657 | 2739.5714 | 40 | No outage | 40 | No outage | 420 | no data | no data | -412 | 123.4286 | 92.45% | 142.9821 | 77.42% | 100% | 84.68% | 51.066 | 135.2157 | 6904.9257 | 155.6597 | 996.8076 | 155162.775 | 8722.7905
| Week 27 | 97.1286 | 56.34% | 82.8857 | 106.5714 | 86.4286 | 159 | 34 | 168 | 0 | 7 | 48 | 0 | 0 | 0 | 0 | 3426.1429 | 2880.4286 | 2787.8571 | 19094 | 19697 | 39.7143 | No outage | 278 | no data | 420 | no data | 603 | -421 | 122.2857 | 95.84% | 142.756 | 79.62% | 100% | 85.5% | 48.85 | 133.7343 | 6532.9199 | 159.6275 | 997.6708 | 159255.72 | 8686.6269 | [5 empty] | 0.27381
| Week 28 | 96.2186 | 61.54% | 83.9829 | 103.1286 | 90.5829 | 153 | 82 | 156 | 1 | 20 | 28 | 0 | 0 | 0 | 0 | 3435 | 2865.1429 | 2608.2857 | 17878 | 18494 | 39 | No outage | 273 | no data | 420 | no data | 616 | -380 | 120.7143 | 91.18% | 143.125 | 74.39% | 99.26% | 82.56% | 43.209 | 132.8157 | 5738.8342 | 133.6601 | 1005.8334 | 134439.8294 | 8786.5773 | [5 empty] | 0.26672
| Week 29 | 91.1143 | 67.7% | 83.9829 | 99.9429 | 82.5429 | 92 | 36 | 123 | 15 | 73 | 36 | 22 | 24 | 0 | 0 | 3487.8571 | 2984.2857 | 1826.2857 | 12536 | 13064 | 39.7143 | No outage | 278 | no data | 420 | no data | 544 | -248 | 112.8571 | 68.96% | 145.3274 | 51.35% | 96.85% | 77.41% | 31.238 | 130.8729 | 4088.2063 | 106.3486 | 1014.5718 | 107898.2567 | 8995.0813
| Week 30 | 91.6286 | 66.73% | 84.0971 | 100.6571 | 82.6857 | 115 | 31 | 123 | 15 | 50 | 55 | 22 | 24 | 0 | 0 | 3482.8571 | 2912.5714 | 2025.1429 | 13901 | 14441 | 39.8571 | No outage | 279 | no data | 420 | no data | 556 | -275 | 113 | 75.67% | 145.119 | 57.08% | 96.85% | 77.55% | 30.458 | 129.7714 | 3952.5782 | 117.7481 | 1013.0436 | 119283.9174 | 8927.4638
336
| Date | Plant Status Whether Normal Operation or Tripping (State full detail for trippings/return to normal). | [61 empty] | 420
| 2019-07-01 | Plant load restricted to 114~118 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heat rate. | [61 empty] | 360
| 2019-07-02 | Plant load restricted to 115~120 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heat rate. | [61 empty] | 1116
| 2019-07-03 | Plant load restricted to 115~120 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heat rate. | [62 empty] | 22.32
| 2019-07-04 | Plant load restricted to 116~118 MW from 0000~2300 hrs to remain within contractual heat rate. CT-1 desynch @ 2318 hrs to meet NPCC load demand of 58 MW.
| 2019-07-05 | CT-1 Synch @ 0706 hrs on Max. load (141 MW) demand of NPCC. Plant load restricted to 114~116 MW from 0736~2400 hrs to remain within contractual heat rate.
| 2019-07-06 | Plant load restricted to 115~121 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heat rate.
| 2019-07-07 | Plant load restricted to 116~118 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heat rate.
| 2019-07-08 | Plant load restricted to 114~117 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heat rate.
| 2019-07-09 | Plant load restricted to 114~117 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heat rate.
| 2019-07-10 | Plant load restricted to 113~116 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heat rate.
| 2019-07-11 | Plant load restricted to 114~117 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heat rate.
| 2019-07-12 | Plant load restricted to 114~118 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heat rate.
| 2019-07-13 | STG tripped @ 0608 hrs due to "Internal Fault". After rectification of fault, STG synch @ 0642 hrs .
| 2019-07-14 | CT-2 desynch @ 0259 hrs as per 57 MW load demand of NPCC. CT-2 synch @ 1338 hrs as per Max. load (138 MW) demand of NPCC.
| 2019-07-15 | CT-1 desynch @ 0039 hrs as per 57 MW load demand of NPCC. CT-1 synch @ 1401 hrs as per Max. load (137 MW) demand of NPCC.
| 2019-07-16 | CT-1 desynch @ 0119 hrs and remained standby as per 58 MW load demand of NPCC.
| 2019-07-17 | CT-2 & STG desynch @0126 hrs to meet NPCC demand of 00 MW while CT-1 was already in standby mode as per NPCC demand. CT-2 synch at 0911 hrs, ST synch at 1026 hrs & CT-1 synch @ 1336 hrs as per NPCC maximum load demand.
| 2019-07-18 | CT-1 desynch @ 1908 hrs and remained standby as per 58 MW load demand of NPCC.
| 2019-07-19 | STG de-synch @ 0140 hrs & CT-2 de-synch @ 0141 hrs as per NPCC demand of 0 MW. CT-2 synch @ 0711 hrs & STG synch @ 0821 hrs to meet NPCC demand of 57 MW.
| 2019-07-20 | CT-1 synch @ 0827 hrs after receiving maximum load demand from NPCC while CT-2 & STG was already on-bar.
| 2019-07-21 | CT-2 de-synch @ 0121 hrs and remained standby as per 57 MW load demand of NPCC. Maximum load demand from NPCC received at 0945hrs but CT-2 remained shutdown to attend high spread problem.
| 2019-07-22 | CT-2 synch @ 0501 hrs after rectification of internal fault. Plant load restricted to 115~118 MW from 0545~2400 hrs as both DBs kept off to remain within contractual heat rate.
| 2019-07-23 | Plant load restricted to 115~118 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heat rate.
| 2019-07-24 | Plant load restricted to 114~117 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heat rate.
| 2019-07-25 | Plant tripped at 0020hrs due to Wapda supply failure. After restoration of Wapda supply @ 0050 hrs, CT-2 synch @ 0139hrs, CT-1 synch @ 0206hrs and STG synch @ 0233hrs. CT-1 de-synch @ 0822 hrs as per NPCC demand of 56 MW. CT-1 synch @ 1333 hrs as per NPCC max. load demand.
| 2019-07-26 | Plant load restricted to 116~120 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heat rate.
| 2019-07-27 | CT-1 desynch @ 0151 hrs as per 56 MW load demand and CT-1 synch @ 0828 hrs as per Max. load (145 MW) demand of NPCC. CT-1 @ 1829 hrs, CT-2 @ 1858 hrs & STG @ 1859 hrs desynch as per 00 MW load demand of NPCC.
| 2019-07-28 | CT-2 synch @ 0631 hrs and STG synch @ 0742 hrs as per 56 MW load demand of NPCC.
| 2019-07-29 | CT-1 synch @ 0845 hrs as per Max. load demand of NPCC.
| 2019-07-30 | Plant load restricted to 115~118 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heat rate.
| 2019-07-31 | CT-1 desynch @ 0235 hrs as per 56 MW load demand of NPCC. CT-1 synch @ 0612 hrs as per Max. load (146 MW) demand of NPCC.
[5 empty] | hrs: 1.35; min: 9.15 | 0.15 | 9
13.5
Note on BN6: ops.e: assumed due to problem of GC of OGDCL.

## Aug
Monthly Operational Returns Kabirwala
2019-08-01
| Date | Site Avg. Ambient Temp.F | Site Avg. Relative Humidty % | Site Avg. Ambient Wetbulb Temp.F | Site Ambient Temp |  | Base load hours |  |  |  | Standby hours |  |  |  | Plant ambient corrected Max Load |  | Corrected Plant Capacity | Ambient Corrected Daclared Avail'y (MWH) | Plant WAPDA Dispatch (MWH) | Net Plant Export (MWH) | Gross Generation | CT1 Average Cap (MW) | CT1 Unavail minutes | CT2 Average Cap (MW) | CT2 Unavail minutes | ST Average Cap (MW) | ST Unavail minutes | Plant Aux Load including Colony Load MWH | Differenece (+/-) MW | Maximum Daily Generation | Daily Load Factor | Avg. Corrected Plant Capacity | Plant Capacity Factor | Plant Availability Factor | Equivalent Plant Availability | LBtu gas flow (mmscf/day) | 1 LBtu gas (Average Btu/scf) | LBTU MMBTU | 1 HBtu gas flow (mmscf/day) | 1 HBtu gas (Average Btu/scf) | HBTU MMBTU | HHV Net Heat Rate (Btu/Kwh) | Avg. declared availability | CT1 Derated MW | CT1 derated mintutes | CT-2 derated MW | CT-2 derated mintutes | ST derated MW | ST derated mintutes | WAPDA Backfeed (MWH) | CT-1 Gross Generation (MWH) | CT-2 Gross Generation (MWH) | STG Gross Generation (MWH) | CT-1 & CT-2 MWH difference | Base load Heat Rate | STG load | DB1 | DB2 | CT1 Gas flow | CT2 Gas flow |  | Freq. Hz | LBTU Gas Specific gravity | CT-1 compressor efficiency(%) | CT-2 compressor efficiency(%) | DB(1+2) | CT-1 Heat Rate (Btu/Kwh) | CT-2 Heat Rate (Btu/Kwh) | RO Operation Hours
[7 empty] | CT1 |  | CT2 |  | CT1 |  | CT2 | [43 empty] | mmscf/d | mmscf/d | HBTU KPPH | HBTU KPPH | LBTU KPPH | Hz |  |  |  | mmscf/d
[5 empty] | Max | Min | hrs | min | hrs | min | hrs | min | hrs | min | hrs | min
Week 31 | 2019-07-30 | 92.6 | 61.1% | 86.5 | 101 | 84 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3469 | 2853 | 2853 | 2792 | 2880 | 40 | 0 | 40 | 0 | 60 | 0 | 88 | -61 | 122 | 98.36% | 144.5417 | 80.48% | 100% | 86.43% | 5.706 | 130.56 | 744.9754 | 23.3483 | 1010.8016 | 23600.449 | 8719.7079 | 118.875 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 951 | 947 | 982 | -4 | 8719.7079 | 40.9167 | 0 | 0 | 23.26 | 20.76 | 15.53 | 50.14 | 0.9359 | 88.22 | 87.42 | 0 | 11481 | 11720 | 0
| 2019-07-31 | 95.9 | 63.7% | 86.5 | 106 | 87 | 20 | 23 | 24 | 0 | 3 | 37 | 0 | 0 | 0 | 0 | 3442 | 2921 | 2593 | 2538 | 2623 | 39 | 0 | 39 | 0 | 60 | 0 | 85 | -55 | 120 | 91.08% | 143.4167 | 73.74% | 100% | 83.07% | 5.684 | 131.38 | 746.7639 | 21.3749 | 1009.8334 | 21585.119 | 8799.0082 | 121.7083 | 17 | 31 | 0 | 0 | 23 | 1440 | 0 | 793 | 940 | 890 | 147 | 8799.0082 | 37.0833 | 0 | 0 | 19.61 | 20.66 | 15.68 | 50.11 | 0.9358 | 88.23 | 87.47 | 0 | 11550 | 11748 | 5.45
| 2019-08-01 | 90.7 | 71.5% | 86.6 | 100 | 86 | 12 | 49 | 22 | 32 | 10 | 56 | 0 | 0 | 0 | 0 | 3493 | 3134 | 2071 | 2049 | 2128 | 39 | 0 | 39 | 71 | 60 | 102 | 80 | -22 | 121 | 73.28% | 145.5417 | 58.66% | 95.53% | 76.4% | 4.03 | 134.08 | 540.3424 | 17.4019 | 1009.9989 | 17575.91 | 8841.5092 | 130.5833 | 16 | 15 | 18 | 17 | 28 | 1338 | 1 | 515 | 898 | 715 | 383 | 8841.5092 | 29.7917 | 0 | 0 | 12.66 | 19.67 | 15.47 | 50.12 | 0.9347 | 88.28 | 87.43 | 0 | 11516 | 11747 | 0
| 2019-08-02 | 89.6 | 71.3% | 81.3 | 98 | 83 | 17 | 4 | 24 | 0 | 6 | 13 | 0 | 0 | 0 | 0 | 3499 | 3048 | 2439 | 2398 | 2475 | 40 | 0 | 40 | 0 | 60 | 0 | 77 | -41 | 122 | 84.53% | 145.7917 | 68.53% | 100% | 81.67% | 4.687 | 124.44 | 583.2503 | 20.2767 | 1009.6328 | 20472.051 | 8780.3592 | 127 | 22 | 43 | 0 | 0 | 25 | 1440 | 0 | 693 | 947 | 835 | 254 | 8780.3592 | 34.7917 | 0 | 0 | 23.39 | 20.61 | 15.96 | 50.11 | 0.9379 | 88.14 | 87.41 | 0 | 11495 | 11631 | 6
| 2019-08-03 | 90.9 | 71.02% | 86.4 | 97 | 85 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3483 | 2857 | 2857 | 2795 | 2878 | 40 | 0 | 39 | 0 | 60 | 0 | 83 | -62 | 121 | 99.1% | 145.125 | 80.25% | 100% | 86.33% | 4.904 | 124.51 | 610.597 | 23.5055 | 1006.9418 | 23668.67 | 8686.6787 | 119.0417 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 952 | 943 | 983 | -9 | 8686.6787 | 40.9583 | 0 | 0 | 23.39 | 20.77 | 16.08 | 50.11 | 0.938 | 88.18 | 87.46 | 0 | 11538 | 11798 | 0
| 2019-08-04 | 94.46 | 62.68% | 85.05 | 104 | 86 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3454 | 2867 | 2867 | 2801 | 2886 | 40 | 0 | 39 | 0 | 60 | 0 | 85 | -66 | 121 | 99.38% | 143.9167 | 81.09% | 100% | 86.33% | 5.13 | 125.87 | 645.7131 | 23.6106 | 1002.5472 | 23670.75 | 8681.3506 | 119.4583 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 954 | 946 | 986 | -8 | 8681.3506 | 41.0833 | 0 | 0 | 23.51 | 20.86 | 16.03 | 50.15 | 0.9377 | 88.08 | 87.39 | 0 | 11586 | 11820 | 4.8
| 2019-08-05 | 95.9 | 62.69% | 86.1 | 103 | 88 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3442 | 2841 | 2841 | 2772 | 2855 | 39 | 0 | 39 | 0 | 60 | 0 | 83 | -69 | 121 | 98.31% | 143.4167 | 80.53% | 100% | 86.23% | 5 | 125.41 | 627.05 | 23.3867 | 1002.0063 | 23433.6 | 8679.8882 | 118.375 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 942 | 934 | 979 | -8 | 8679.8882 | 40.7917 | 0 | 0 | 23.28 | 20.72 | 15.56 | 50.13 | 0.9379 | 88.12 | 87.46 | 0 | 11607 | 11833 | 0
Week 32 | 2019-08-06 | 97.16 | 64.22% | 87.49 | 106 | 89 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3429 | 2818 | 2818 | 2748 | 2837 | 39 | 0 | 39 | 0 | 60 | 0 | 89 | -70 | 120 | 98.51% | 142.875 | 80.14% | 100% | 86.23% | 5.119 | 134.04 | 686.1508 | 23.1221 | 1008.2241 | 23312.289 | 8733.0567 | 117.4167 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 935 | 930 | 972 | -5 | 8733.0567 | 40.5 | 0 | 0 | 23.01 | 20.43 | 15.73 | 50.13 | 0.9348 | 88.15 | 87.5 | 0 | 11561 | 11774 | 5.2
| 2019-08-07 | 92.5 | 69.7% | 87 | 97 | 87 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3479 | 2845 | 2845 | 2774 | 2859 | 39 | 0 | 39 | 0 | 60 | 0 | 85 | -71 | 121 | 98.45% | 144.9583 | 79.74% | 100% | 86.23% | 4.99 | 128.82 | 642.8118 | 23.3645 | 1008.5515 | 23564.34 | 8726.4426 | 118.5417 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 945 | 936 | 978 | -9 | 8726.4426 | 40.75 | 0 | 0 | 23.18 | 20.59 | 15.73 | 50.15 | 0.9365 | 88.1 | 87.46 | 0 | 11523 | 11779 | 0
| 2019-08-08 | 90.6 | 72.4% | 87.8 | 100 | 87 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3494 | 2852 | 2852 | 2784 | 2869 | 39 | 0 | 39 | 0 | 60 | 0 | 85 | -68 | 121 | 98.79% | 145.5833 | 79.68% | 100% | 86.23% | 4.97 | 132.06 | 656.3382 | 23.5216 | 1006.0068 | 23662.859 | 8735.3438 | 118.8333 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 948 | 939 | 982 | -9 | 8735.3438 | 40.9167 | 0 | 0 | 23.29 | 20.75 | 15.47 | 50.14 | 0.9354 | 88.06 | 87.4 | 0 | 11543 | 11783 | 0
| 2019-08-09 | 89 | 76.4% | 87.4 | 106 | 83 | 16 | 3 | 24 | 0 | 7 | 40 | 0 | 0 | 0 | 0 | 3510 | 3061 | 2366 | 2318 | 2396 | 39 | 0 | 39 | 0 | 60 | 0 | 78 | -48 | 121 | 82.51% | 146.25 | 66.04% | 100% | 81.02% | 5.092 | 128.54 | 654.5257 | 19.7122 | 1003.6798 | 19784.7472 | 8817.6328 | 127.5417 | 16 | 17 | 0 | 0 | 26 | 1440 | 0 | 638 | 941 | 817 | 303 | 8817.6328 | 34.0417 | 0 | 0 | 15.78 | 20.75 | 16.04 | 50.16 | 0.9367 | 88.07 | 87.41 | 0 | 11558 | 11780 | 5.47
| 2019-08-10 | 88.6 | 75.3% | 87.2 | 95 | 83 | 6 | 43 | 22 | 22 | 15 | 46 | 0 | 0 | 0 | 0 | 3512 | 3343 | 1750 | 1670 | 1745 | 39 | 42 | 39 | 79 | 60 | 117 | 75 | -80 | 119 | 61.1% | 146.3333 | 47.55% | 94.09% | 69.49% | 4.752 | 126.19 | 599.6549 | 14.569 | 1001.1939 | 14586.3645 | 9093.4248 | 139.2917 | 19 | 50 | 16 | 19 | 36 | 1323 | 0 | 282 | 891 | 572 | 609 | 9093.4248 | 23.8333 | 0 | 0 | 7.12 | 19.67 | 15.44 | 50.02 | 0.9375 | 87.88 | 87.49 | 0 | 11576 | 11780 | 0
| 2019-08-11 | 90.3 | 72% | 87.7 | 96 | 84 | 11 | 31 | 24 | 0 | 10 | 16 | 0 | 0 | 0 | 0 | 3497 | 3168 | 2090 | 2063 | 2144 | 39 | 68 | 39 | 0 | 60 | 0 | 81 | -27 | 120 | 74.44% | 145.7083 | 58.99% | 98.67% | 76.48% | 4.962 | 128.34 | 636.8231 | 17.8289 | 999.2286 | 17815.1109 | 8944.2239 | 132 | 16 | 56 | 0 | 0 | 30 | 1440 | 0 | 480 | 947 | 717 | 467 | 8944.2239 | 29.875 | 0 | 0 | 12.11 | 20.98 | 15.89 | 50.18 | 0.9368 | 88.37 | 87.36 | 0 | 11616 | 11830 | 5.75
| 2019-08-12 | 94.9 | 68.17% | 86.94 | 104 | 87 | 17 | 15 | 24 | 0 | 6 | 28 | 0 | 0 | 0 | 0 | 3448 | 3037 | 2426 | 2378 | 2462 | 40 | 0 | 40 | 0 | 60 | 0 | 84 | -48 | 121 | 84.78% | 143.6667 | 68.97% | 100% | 82.73% | 4.941 | 130.54 | 644.9981 | 20.2605 | 1000.3805 | 20268.2202 | 8794.4568 | 126.5417 | 15 | 17 | 0 | 0 | 24 | 1440 | 0 | 688 | 942 | 832 | 254 | 8794.4568 | 34.6667 | 0 | 0 | 17.07 | 20.73 | 16.05 | 50.15 | 0.936 | 88.28 | 87.39 | 0 | 11585 | 11799 | 0
Week 33 | 2019-08-13 | 92.66 | 66.13% | 84.35 | 99.7 | 86.7 | 11 | 51 | 24 | 0 | 11 | 12 | 0 | 0 | 0 | 0 | 3474 | 3166 | 2113 | 2085 | 2166 | 40 | 0 | 40 | 0 | 60 | 0 | 81 | -28 | 122 | 73.98% | 144.75 | 60.02% | 100% | 78.01% | 4.902 | 135.94 | 666.3779 | 17.9002 | 1000.7052 | 17912.7943 | 8910.8739 | 131.9167 | 20 | 57 | 0 | 0 | 30 | 1440 | 0 | 490 | 951 | 725 | 461 | 8910.8739 | 30.2083 | 0 | 0 | 12.3 | 20.94 | 16.01 | 50.14 | 0.9345 | 88.12 | 87.24 | 0 | 11555 | 11779 | 5.75
| 2019-08-14 | 93.2 | 63.8% | 79.1 | 101 | 86 | 19 | 16 | 24 | 0 | 4 | 10 | 0 | 0 | 0 | 0 | 3461 | 3016 | 2580 | 2533 | 2611 | 40 | 0 | 40 | 0 | 60 | 0 | 78 | -47 | 122 | 89.17% | 144.2083 | 73.19% | 100% | 83.27% | 4.964 | 132.62 | 658.3257 | 21.5046 | 1000.6005 | 21517.5001 | 8754.7674 | 125.6667 | 18 | 34 | 0 | 0 | 23 | 1440 | 0 | 779 | 947 | 885 | 168 | 8754.7674 | 36.875 | 0 | 0 | 19.19 | 20.93 | 16.1 | 50.15 | 0.9355 | 88.17 | 87.3 | 0 | 11467 | 11817 | 6.27
| 2019-08-15 | 95.2 | 62.4% | 85.2 | 104 | 86 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3449 | 2854 | 2854 | 2781 | 2870 | 40 | 0 | 39 | 0 | 60 | 0 | 89 | -73 | 122 | 98.02% | 143.7083 | 80.63% | 100% | 86.33% | 4.978 | 129.51 | 644.7008 | 23.4419 | 1001.6958 | 23481.6292 | 8675.4153 | 118.9167 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 951 | 938 | 981 | -13 | 8675.4153 | 40.875 | 0 | 0 | 23.38 | 20.73 | 15.28 | 50.11 | 0.9366 | 88.26 | 87.44 | 0 | 11549 | 11798 | 0
| 2019-08-16 | 92.6 | 64.7% | 84.6 | 101 | 83 | 22 | 30 | 24 | 0 | 1 | 17 | 0 | 0 | 0 | 0 | 3470 | 2903 | 2770 | 2712 | 2797 | 40 | 0 | 39 | 0 | 60 | 0 | 85 | -58 | 123 | 94.75% | 144.5833 | 78.16% | 100% | 85.52% | 5.088 | 131.61 | 669.6317 | 22.8417 | 1002.3395 | 22895.119 | 8689.0674 | 120.9583 | 14 | 13 | 0 | 0 | 20 | 1440 | 0 | 900 | 942 | 955 | 42 | 8689.0674 | 39.7917 | 0 | 0 | 22.09 | 20.79 | 14.78 | 50.14 | 0.9358 | 88.22 | 87.39 | 0 | 11518 | 11720 | 6.58
| 2019-08-17 | 88.8 | 70.7% | 85.16 | 98 | 83 | 10 | 5 | 24 | 0 | 13 | 4 | 0 | 0 | 0 | 0 | 3510 | 3195 | 2006 | 1976 | 2052 | 40 | 0 | 39 | 0 | 60 | 0 | 76 | -30 | 123 | 69.51% | 146.25 | 56.3% | 100% | 77.19% | 5.065 | 130.59 | 661.4384 | 16.7579 | 1010.1916 | 16928.689 | 8901.8863 | 133.125 | 20 | 51 | 0 | 0 | 31 | 1440 | 0 | 416 | 946 | 690 | 530 | 8901.8863 | 28.75 | 0 | 0 | 10.37 | 20.8 | 15.03 | 50.1 | 0.9359 | 88.34 | 87.36 | 0 | 11474 | 11708 | 6.1
| 2019-08-18 | 89.3 | 70.3% | 84.62 | 98 | 81 | 8 | 17 | 24 | 0 | 15 | 10 | 0 | 0 | 0 | 0 | 3509 | 3240 | 1891 | 1859 | 1939 | 40 | 0 | 39 | 0 | 60 | 0 | 80 | -32 | 121 | 66.77% | 146.2083 | 52.98% | 100% | 76.67% | 5 | 129.99 | 649.95 | 15.8599 | 1009.1136 | 16004.43 | 8958.7843 | 135 | 19 | 33 | 0 | 0 | 32 | 1440 | 0 | 341 | 949 | 649 | 608 | 8958.7843 | 27.0417 | 0 | 0 | 8.54 | 20.9 | 15.01 | 50.12 | 0.936 | 88.04 | 87.35 | 0 | 11520 | 11695 | 0
| 2019-08-19 | 87.8 | 63.15% | 79.16 | 97 | 78 | 13 | 6 | 24 | 0 | 10 | 10 | 0 | 0 | 0 | 0 | 3517 | 3154 | 2240 | 2200 | 2278 | 40 | 0 | 40 | 0 | 60 | 0 | 78 | -40 | 123 | 77.17% | 146.5417 | 62.55% | 100% | 79.63% | 5.063 | 131.36 | 665.0757 | 18.3482 | 1015.238 | 18627.75 | 8769.4662 | 131.4167 | 17 | 44 | 0 | 0 | 28 | 1440 | 0 | 546 | 966 | 766 | 420 | 8769.4662 | 31.9167 | 0 | 0 | 13.35 | 20.93 | 15.11 | 50.1 | 0.9355 | 87.97 | 87.11 | 0 | 11332 | 11528 | 5.7
Week 34 | 2019-08-20 | 91.6 | 66.8% | 84.6 | 98 | 84 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3484 | 2854 | 2854 | 2805 | 2891 | 40 | 0 | 39 | 0 | 60 | 0 | 86 | -49 | 123 | 97.93% | 145.1667 | 80.51% | 100% | 86.33% | 5.001 | 129.3 | 646.6293 | 23.0104 | 1020.8146 | 23489.311 | 8604.6133 | 118.9167 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 958 | 945 | 988 | -13 | 8631.781 | 41.1667 | 0 | 0 | 23.03 | 20.39 | 15.32 | 50.12 | 0.9371 | 88.11 | 87.25 | 0 | 11290 | 11537 | 5.72
| 2019-08-21 | 93.5 | 64.8% | 84.3 | 102 | 84 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3463 | 2868 | 2868 | 2796 | 2883 | 40 | 0 | 39 | 0 | 60 | 0 | 87 | -72 | 122 | 98.46% | 144.2917 | 80.74% | 100% | 86.33% | 5.017 | 131.15 | 657.9796 | 23.3168 | 1006.847 | 23476.48 | 8631.781 | 119.5 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 953 | 945 | 985 | -8 | 8618.3874 | 41.0417 | 0 | 0 | 23.22 | 20.69 | 15.25 | 50.13 | 0.9357 | 87.99 | 87.17 | 0 | 11435 | 11679 | 0
| 2019-08-22 | 93 | 64.3% | 83.8 | 103 | 85 | 22 | 51 | 24 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 3465 | 2886 | 2799 | 2741 | 2827 | 39 | 0 | 39 | 0 | 60 | 0 | 86 | -58 | 122 | 96.55% | 144.375 | 79.11% | 100% | 85.4% | 5.022 | 132.31 | 664.4608 | 22.9411 | 1000.7619 | 22958.539 | 8618.3874 | 120.25 | 14 | 15 | 0 | 0 | 20 | 1440 | 0 | 914 | 944 | 969 | 30 | 8618.3874 | 40.375 | 0 | 0 | 22.35 | 20.83 | 14.84 | 50.14 | 0.9353 | 87.98 | 87.13 | 0 | 11448 | 11702 | 6.5
| 2019-08-23 | 92 | 60.2% | 80.81 | 101 | 82 | 15 | 10 | 24 | 0 | 8 | 13 | 0 | 0 | 0 | 0 | 3471 | 3067 | 2330 | 2290 | 2372 | 39 | 0 | 39 | 0 | 60 | 0 | 82 | -40 | 121 | 81.68% | 144.625 | 65.98% | 100% | 80.1% | 5.016 | 131.67 | 660.4567 | 19.1948 | 1006.8274 | 19325.84 | 8727.6405 | 127.7917 | 18 | 37 | 0 | 0 | 27 | 1440 | 0 | 619 | 954 | 799 | 335 | 8727.6405 | 33.2917 | 0 | 0 | 15.19 | 20.89 | 15.05 | 50.14 | 0.9356 | 88.07 | 87.08 | 0 | 11426 | 11671 | 5.3
| 2019-08-24 | 93.8 | 63.7% | 84.5 | 103 | 84 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3462 | 2867 | 2867 | 2797 | 2880 | 40 | 0 | 39 | 0 | 60 | 0 | 83 | -70 | 122 | 98.36% | 144.25 | 80.79% | 100% | 86.33% | 5.064 | 134.55 | 681.3612 | 23.2659 | 1007.0845 | 23430.692 | 8620.684 | 119.4583 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 954 | 939 | 987 | -15 | 8620.684 | 41.125 | 0 | 0 | 23.26 | 20.68 | 14.95 | 50.13 | 0.935 | 88.09 | 87.18 | 0 | 11442 | 11718 | 0
| 2019-08-25 | 94.5 | 61.1% | 83.8 | 104 | 85 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3449 | 2867 | 2867 | 2805 | 2888 | 40 | 0 | 40 | 0 | 60 | 0 | 83 | -62 | 123 | 97.83% | 143.7083 | 81.33% | 100% | 86.43% | 5.071 | 132.77 | 673.2767 | 23.2928 | 1007.9725 | 23478.544 | 8610.2747 | 119.4583 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 957 | 942 | 989 | -15 | 8610.2747 | 41.2083 | 0 | 0 | 23.29 | 20.73 | 14.72 | 50.16 | 0.936 | 88.06 | 87.15 | 0 | 11432 | 11694 | 5.83
| 2019-08-26 | 91.96 | 67.4% | 85.2 | 99 | 84 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3476 | 2859 | 2859 | 2795 | 2881 | 40 | 0 | 39 | 0 | 60 | 0 | 86 | -64 | 122 | 98.39% | 144.8333 | 80.41% | 100% | 86.33% | 4.954 | 129.1 | 639.5614 | 23.3049 | 1006.8966 | 23465.584 | 8624.3812 | 119.125 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 954 | 941 | 986 | -13 | 8624.3812 | 41.0833 | 0 | 0 | 23.29 | 20.73 | 14.91 | 50.13 | 0.9364 | 88.1 | 87.3 | 0 | 11472 | 11737 | 5.01
Week 35 | 2019-08-27 | 92.2 | 67.6% | 86.4 | 98.6 | 86.8 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3474 | 2855 | 2855 | 2789 | 2873 | 40 | 0 | 39 | 0 | 60 | 0 | 84 | -66 | 121 | 98.93% | 144.75 | 80.28% | 100% | 86.33% | 4.975 | 134.36 | 668.441 | 23.311 | 1005.0752 | 23429.282 | 8640.2736 | 118.9583 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 951 | 938 | 984 | -13 | 8640.2736 | 41 | 0 | 0 | 23.36 | 20.73 | 15.11 | 50.1 | 0.9345 | 88.16 | 87.32 | 0 | 11530 | 11746 | 0
| 2019-08-28 | 93.2 | 65.1% | 85.3 | 100.6 | 86.7 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3463 | 2857 | 2857 | 2795 | 2881 | 40 | 0 | 39 | 0 | 60 | 0 | 86 | -62 | 121 | 99.21% | 144.2917 | 80.71% | 100% | 86.33% | 4.9 | 127.42 | 624.358 | 23.3207 | 1006.2184 | 23465.696 | 8618.9818 | 119.0417 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 954 | 942 | 985 | -12 | 8618.9818 | 41.0417 | 0 | 0 | 23.37 | 20.73 | 14.91 | 50.14 | 0.9371 | 88.1 | 87.2 | 0 | 11516 | 11730 | 6
| 2019-08-29 | 95.17 | 64% | 86.72 | 103 | 87 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3447 | 2840 | 2840 | 2771 | 2856 | 39 | 0 | 39 | 0 | 60 | 0 | 85 | -69 | 121 | 98.35% | 143.625 | 80.39% | 100% | 86.23% | 4.896 | 129.57 | 634.3747 | 23.1575 | 1007.9336 | 23341.238 | 8652.3323 | 118.3333 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 943 | 933 | 980 | -10 | 8652.3323 | 40.8333 | 0 | 0 | 23.22 | 20.58 | 14.6 | 50.13 | 0.9364 | 88.15 | 87.24 | 0 | 11542 | 11734 | 5.6
| 2019-08-30 | 94.9 | 63.9% | 86.45 | 104 | 87 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3453 | 2839 | 2839 | 2771 | 2858 | 39 | 0 | 39 | 0 | 60 | 0 | 87 | -68 | 121 | 98.42% | 143.875 | 80.25% | 100% | 86.23% | 4.899 | 131.8 | 645.6882 | 23.282 | 1007.7026 | 23461.382 | 8699.7727 | 118.2917 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 945 | 933 | 980 | -12 | 8699.7727 | 40.8333 | 0 | 0 | 23.34 | 20.74 | 14.43 | 50.13 | 0.9356 | 88.03 | 87.22 | 0 | 11595 | 11810 | 0
| 2019-08-31 | 90.1 | 69.6% | 85.3 | 101 | 84 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3496 | 2863 | 2863 | 2806 | 2888 | 40 | 0 | 40 | 0 | 60 | 0 | 82 | -57 | 122 | 98.63% | 145.6667 | 80.26% | 100% | 86.43% | 4.88 | 130.11 | 634.9368 | 23.698 | 1007.7027 | 23880.5382 | 8736.805 | 119.2917 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 956 | 946 | 986 | -10 | 8736.805 | 41.0833 | 0 | 0 | 23.73 | 21.07 | 14.06 | 50.12 | 0.9361 | 87.95 | 87.11 | 0 | 11671 | 11762 | 6.1
| 2019-09-01 | [26 empty] | 0 | 0 |  | no data | no data | no data | #DIV/0! | no data |  |  | 0 |  |  | 0 | no data | 0 | [10 empty] | 0 | no data | 0
| 2019-09-02 | [26 empty] | 0 | 0 |  | no data | no data | no data | #DIV/0! | no data |  |  | 0 |  |  | 0 | no data | 0 | [10 empty] | 0 | no data | 0
| Monthly | 92.2616 | 67% | 85.0435 | 100.7065 | 84.8774 | 612 | 343 | 740 | 55 | 121 | 329 | 0 | 0 | 0 | 0 | 107733 | 91921 | 80374 | 78557.3 | 81225 | 39.6129 | 110 | 39.2258 | 150 | 60 | 219 | 2668.7 | -1717 | 121.4839 | 89.85% | 144.8024 | 73.06% | 99.62% | 83.25% | 153.332 | 130.2765 | 19975.2798 | 662.3103 | 1006.1327 | 666385.9496 | 8737.0776 |  | 7.871 | 482 | 1.0968 | 36 | 22.6774 | 44421 | 1 | 24453 | 29135 | 27637 | 4682 | 8737.0776 | 37.1465 | 0 | 0 | 607.66 | 641.34 | 474.92 | 50.1284 | 0.93615 | 88.1168 | 87.3129 |  | 11513.4839 | 11739.3226 | 103.68
| Totals | Avg.F | % Avg. |  | M Avg | m Avg | hrs | min | hrs | min | hrs | min | hrs | min | Avg Int Avi | Avg Ext Avi | MWhr Total | MWhr Total | MWhr Total | MWhr Total | MWhr Total | MW Avg | Total min | Avg MW | Total min | Avg MW | Total min | MWhr | Total MW | Av Max D/Gen | Av. DailyLF | Avg. | Avg. |  | Avg. | Total | Avg. |  | Total | Avg. |  | Avg. | [7 empty] | Total |  |  |  |  | Avg.
| Weeks data | Site Avg. Amb. Temp F | Site Avg. Relative humidity % | Site Avg. Ambient Wetbulb Temp.F | M Avg: Site Maximum/Minumum Temperature; hrs: CT-1 Base Load Hours; hrs: CT-2 Base Load Hours; hrs: CT-1 stand by hours / min; hrs: CT-2 standby hours / min | Plant ambient Corrected maximum Load hours/min |  | Average Corrected Plant Capacity | Ambient Corrected Declared Avail'y (MWH) | Av Plant WAPDA Dispatch | Net Plant Export (MWH) | Gross Generation | CT1 Av Cap (MW) | CT1 Unavail minutes | CT2 Av Cap (MW) | CT2 Unavail minutes | ST Unavail minutes | ST Average Cap (MW) | Plant Aux Load including Colony Load MWH | Differenece (+/-) MW | Maximum Daily Generation | Daily Load Factor | Avg. Corrected Plant | Plant Capacity Facto | Plant Availability Factor | Equivalent Plant Availability | LBtu gas flow mmscf | 1 LBtu gas (Average Btu/scf) | LBTU MMBTU | PL gas flow (mscf/week) | 1 PL gas (Average Btu/scf) | HBTU MMBTU | Plant Net Heat Rate (Btu/Kwh) | [11 empty] | 65.8
| Week 26 | 92.8657 | 66.28% | 85.4929 | 101.2857 | 85.5714 | 146 | 16 | 166 | 32 | 20 | 46 | 0 | 0 | 0 | 0 | 3468.8571 | 2931.5714 | 2645.8571 | 2592.1429 | 2675 | 39.5714 | No outage | 39.2857 | 71 | 420 | no data | no data | -376 | 121.1429 | 92.01% | 144.5357 | 74.76% | 99.36% | 83.78% | 35.141 | 128.0357 | 4499.303 | 152.9046 | 1007.3946 | 154035.2726 | 8741.2146
| Week 27 | 91.8657 | 71.17% | 87.3614 | 100.5714 | 85.7143 | 123 | 90 | 166 | 22 | 40 | 130 | 0 | 0 | 0 | 0 | 3481.2857 | 3017.7143 | 2449.5714 | 16735 | 17312 | 39.1429 | 110 | 274 | no data | 420 | no data | 577 | -412 | 120.4286 | 85.51% | 145.0536 | 68.73% | 98.97% | 81.2% | 34.826 | 129.79 | 4520.0665 | 142.3788 | 1003.895 | 142933.3639 | 8834.9402 | [5 empty] | 0.27381
| Week 28 | 91.3657 | 65.88% | 83.17 | 99.8143 | 83.3857 | 109 | 125 | 168 | 0 | 55 | 3 | 0 | 0 | 0 | 0 | 3484.2857 | 3075.4286 | 2350.5714 | 16146 | 16713 | 40 | No outage | 276 | no data | 420 | no data | 567 | -308 | 122.2857 | 81.34% | 145.1786 | 66.26% | 100% | 80.94% | 35.06 | 131.66 | 4615.9996 | 118.3061 | 1004.1077 | 118792.069 | 8808.6087 | [5 empty] | 0.26672
| Week 29 | 92.9086 | 64.04% | 83.17 | 101.4286 | 84 | 158 | 1 | 168 | 0 | 9 | 7 | 0 | 0 | 0 | 0 | 3467.1429 | 2895.4286 | 2777.7143 | 19029 | 19622 | 39.7143 | No outage | 274 | no data | 420 | no data | 593 | -415 | 122.1429 | 95.6% | 144.4643 | 78.41% | 100% | 85.32% | 35.145 | 131.55 | 4623.3247 | 158.3266 | 1008.1721 | 159620.4619 | 8633.966
| Week 30 | 92.9943 | 64.16% | 83.2057 | 101.5143 | 84.4 | 158 | 1 | 168 | 0 | 9 | 7 | 0 | 0 | 0 | 0 | 3465.7143 | 2895.5714 | 2777.8571 | 19013 | 19604 | 39.7143 | No outage | 274 | no data | 420 | no data | 591 | -432 | 121.8571 | 95.74% | 144.4048 | 78.38% | 100% | 85.32% | 35.119 | 132.2729 | 4645.2905 | 158.6272 | 1005.9236 | 159566.8621 | 8639.0603
336
| Date | Plant Status Whether Normal Operation or Tripping (State full detail for trippings/return to normal). | [61 empty] | 420
| 2019-08-01 | CT-1 desynch @1304 hrs and remained standby as per 56 MW load demand of NPCC.Plant tripped at 1532 hrs due to Wapda supply failure. After restoration of Wapda supply @ 1542 hrs, CT-2 synch @ 1643 hrs & STG synch @ 1714hrs. | [61 empty] | 360
| 2019-08-02 | CT-1 synch @ 0613 hrs at NPCC demand of maximum load. Plant load restricted to 115~118 MW from 0700~2400 hrs as both DBs kept off to remain within contractual heatrate. | [61 empty] | 1116
| 2019-08-03 | Plant load restricted to 115~118 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heat rate. | [62 empty] | 22.32
| 2019-08-04 | Plant load restricted to 116~118 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heat rate.
| 2019-08-05 | Plant load restricted to 114~117 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heat rate.
| 2019-08-06 | Plant load restricted to 113~116 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heat rate.
| 2019-08-07 | Plant load restricted to 114~117 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heat rate.
| 2019-08-08 | Plant load restricted to 115~117 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heat rate.
| 2019-08-09 | CT-1 desynch @ 1620 hrs and remained standby as per 57 MW demand of NPCC.
| 2019-08-10 | CT-1 synch @ 1020 hrs as per NPCC max. load demand.Plant tripped at 1752 hrs due to Wapda supply failure. After restoration of Wapda supply @ 1831 hrs, 56 MW load demand received from NPCC @ 1834 hrs then CT-2 synch @ 1911 hrs and STG synch @ 1949 hrs.
| 2019-08-11 | CT-1 synch @ 1121 hrs as per Max. load (144 MW) demand of NPCC. CT-1 de-synch @ 2357 hrs as per 56 MW load demand of NPCCC.
| 2019-08-12 | CT-1 synch @ 0628 hrs at NPCC demand of maximum load. Plant load restricted to 115~117 MW from 0700~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2019-08-13 | CT-1 de-synch @ 0125 hrs as per 56 MW load demand of NPCC. CT-1 synch @ 1237 hrs as per NPCC maximum load demand.
| 2019-08-14 | CT-1 de-synch @ 0208 hrs as per 57 MW load demand of NPCC. CT-1 synch @ 0618 hrs as per NPCC maximum load demand. Plant load restricted to 116~118 MW from 0642~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2019-08-15 | Plant load restricted to 114~118 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heat rate.
| 2019-08-16 | Plant load restricted to 114~119 MW from 0000~2230 hrs as both DBs kept off to remain within contractual heat rate. CT-1 de-synch @ 2243 hrs at NPCC demand of 57 MW.
| 2019-08-17 | CT-1 synch @ 0923hrs as per NPCC max load demand. CT-1 de-synch @ 2019hrs as per NPCC load demand of 57MW.
| 2019-08-18 | CT-1 synch @ 1510 hrs at NPCC maximum load demand. Plant load restricted to 115~118 MW from 1547~2400 hrs as both DBs kept off to remain within contractual heatrate.
| 2019-08-19 | CT-1 de-synch @ 0219 hrs as per NPCC load demand of 57 MW. CT-1 synch @ 1229 hrs at NPCC maximum load demand.
| 2019-08-20 | Plant load restricted to 114~119 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heat rate.
| 2019-08-21 | Plant load restricted to 115~119 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heat rate.
| 2019-08-22 | Plant load restricted to 114~119 MW from 0000~2250 hrs as both DBs kept off to remain within contractual heat rate. CT-1 desynchronized at 23:06 hrs at NPCC demand of 57 MW.
| 2019-08-23 | CT-1 synchronized at 08:13 hrs at NPCC maximum load demand. Plant load restricted to 116~117 MW from 0853~2400 hrs as both DBs kept off to remain within contractual heat rate.
| 2019-08-24 | Plant load restricted to 115~118 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heat rate.
| 2019-08-25 | Plant load restricted to 115~119 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heat rate.
| 2019-08-26 | Plant load restricted to 115~118 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heat rate.
| 2019-08-27 | Plant load restricted to 115~117 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heat rate.
| 2019-08-28 | Plant load restricted to 115~118 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heat rate.
| 2019-08-29 | Plant load restricted to 114~117 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heat rate.
| 2019-08-30 | Plant load restricted to 114~117 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heat rate.
| 2019-08-31 | Plant load restricted to 114~119 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heat rate.
[5 empty] | hrs: 0.066667 |  |  |  | 0.81667 |  | 0.3
[5 empty] | hrs: 0.81667 |  |  |  | 0.53333
0.28333
0.25
0.18333
0.93333
Note on BN6: ops.e: assumed due to problem of GC of OGDCL.

## Sep
Monthly Operational Returns Kabirwala
2019-09-01
| Date | Site Avg. Ambient Temp.F | Site Avg. Relative Humidty % | Site Avg. Ambient Wetbulb Temp.F | Site Ambient Temp |  | Base load hours |  |  |  | Standby hours |  |  |  | Plant ambient corrected Max Load |  | Corrected Plant Capacity | Ambient Corrected Daclared Avail'y (MWH) | Plant WAPDA Dispatch (MWH) | Net Plant Export (MWH) | Gross Generation | CT1 Average Cap (MW) | CT1 Unavail minutes | CT2 Average Cap (MW) | CT2 Unavail minutes | ST Average Cap (MW) | ST Unavail minutes | Plant Aux Load including Colony Load MWH | Differenece (+/-) MW | Maximum Daily Generation | Daily Load Factor | Avg. Corrected Plant Capacity | Plant Capacity Factor | Plant Availability Factor | Equivalent Plant Availability | LBtu gas flow (mmscf/day) | 1 LBtu gas (Average Btu/scf) | LBTU MMBTU | 1 HBtu gas flow (mmscf/day) | 1 HBtu gas (Average Btu/scf) | HBTU MMBTU | HHV Net Heat Rate (Btu/Kwh) | Avg. declared availability | CT1 Derated MW | CT1 derated mintutes | CT-2 derated MW | CT-2 derated mintutes | ST derated MW | ST derated mintutes | WAPDA Backfeed (MWH) | CT-1 Gross Generation (MWH) | CT-2 Gross Generation (MWH) | STG Gross Generation (MWH) | CT-1 & CT-2 MWH difference | Base load Heat Rate | STG load | DB1 | DB2 | CT1 Gas flow | CT2 Gas flow |  | Freq. Hz | LBTU Gas Specific gravity | CT-1 compressor efficiency(%) | CT-2 compressor efficiency(%) | DB(1+2) | CT-1 Heat Rate (Btu/Kwh) | CT-2 Heat Rate (Btu/Kwh) | RO Operation Hours
[7 empty] | CT1 |  | CT2 |  | CT1 |  | CT2 | [43 empty] | mmscf/d | mmscf/d | HBTU KPPH | HBTU KPPH | LBTU KPPH | Hz |  |  |  | mmscf/d
[5 empty] | Max | Min | hrs | min | hrs | min | hrs | min | hrs | min | hrs | min
Week 35 | 2019-08-27 | 92.6 | 61.1% | 86.5 | 101 | 84 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3469 | 2853 | 2853 | 2792 | 2880 | 40 | 0 | 40 | 0 | 60 | 0 | 88 | -61 | 122 | 98.36% | 144.5417 | 80.48% | 100% | 86.43% | 5.706 | 130.56 | 744.9754 | 23.3483 | 1010.8016 | 23600.449 | 8719.7079 | 118.875 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 951 | 947 | 982 | -4 | 8719.7079 | 40.9167 | 0 | 0 | 23.26 | 20.76 | 15.53 | 50.14 | 0.9359 | 88.22 | 87.42 | 0 | 11481 | 11720 | 0
| 2019-08-28 | 95.9 | 63.7% | 86.5 | 106 | 87 | 20 | 23 | 24 | 0 | 3 | 37 | 0 | 0 | 0 | 0 | 3442 | 2921 | 2593 | 2538 | 2623 | 39 | 0 | 39 | 0 | 60 | 0 | 85 | -55 | 120 | 91.08% | 143.4167 | 73.74% | 100% | 83.07% | 5.684 | 131.38 | 746.7639 | 21.3749 | 1009.8334 | 21585.119 | 8799.0082 | 121.7083 | 17 | 31 | 0 | 0 | 23 | 1440 | 0 | 793 | 940 | 890 | 147 | 8799.0082 | 37.0833 | 0 | 0 | 19.61 | 20.66 | 15.68 | 50.11 | 0.9358 | 88.23 | 87.47 | 0 | 11550 | 11748 | 5.45
| 2019-08-29 | 90.7 | 71.5% | 86.6 | 100 | 86 | 12 | 49 | 22 | 32 | 10 | 56 | 0 | 0 | 0 | 0 | 3493 | 3134 | 2071 | 2049 | 2128 | 39 | 0 | 39 | 71 | 60 | 102 | 80 | -22 | 121 | 73.28% | 145.5417 | 58.66% | 95.53% | 76.4% | 4.03 | 134.08 | 540.3424 | 17.4019 | 1009.9989 | 17575.91 | 8841.5092 | 130.5833 | 16 | 15 | 18 | 17 | 28 | 1338 | 1 | 515 | 898 | 715 | 383 | 8841.5092 | 29.7917 | 0 | 0 | 12.66 | 19.67 | 15.47 | 50.12 | 0.9347 | 88.28 | 87.43 | 0 | 11516 | 11747 | 0
| 2019-08-30 | 89.6 | 71.3% | 81.3 | 98 | 83 | 17 | 4 | 24 | 0 | 6 | 13 | 0 | 0 | 0 | 0 | 3499 | 3048 | 2439 | 2398 | 2475 | 40 | 0 | 40 | 0 | 60 | 0 | 77 | -41 | 122 | 84.53% | 145.7917 | 68.53% | 100% | 81.67% | 4.687 | 124.44 | 583.2503 | 20.2767 | 1009.6328 | 20472.051 | 8780.3592 | 127 | 22 | 43 | 0 | 0 | 25 | 1440 | 0 | 693 | 947 | 835 | 254 | 8780.3592 | 34.7917 | 0 | 0 | 23.39 | 20.61 | 15.96 | 50.11 | 0.9379 | 88.14 | 87.41 | 0 | 11495 | 11631 | 6
| 2019-08-31 | 90.9 | 71.02% | 86.4 | 97 | 85 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3483 | 2857 | 2857 | 2795 | 2878 | 40 | 0 | 39 | 0 | 60 | 0 | 83 | -62 | 121 | 99.1% | 145.125 | 80.25% | 100% | 86.33% | 4.891 | 124.51 | 608.9784 | 23.5055 | 1006.9418 | 23668.67 | 8686.0996 | 119.0417 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 952 | 943 | 983 | -9 | 8686.0996 | 40.9583 | 0 | 0 | 23.39 | 20.77 | 16.08 | 50.11 | 0.938 | 88.18 | 87.46 | 0 | 11538 | 11798 | 0
| 2019-09-01 | 90 | 70.3% | 85.8 | 99 | 84 | 20 | 3 | 22 | 32 | 2 | 3 | 0 | 0 | 0 | 0 | 3496 | 2908 | 2510 | 2460 | 2542 | 40 | 116 | 40 | 70 | 60 | 103 | 84 | -50 | 120 | 88.26% | 145.6667 | 70.37% | 93.24% | 78.47% | 4.39 | 136.66 | 599.9374 | 20.6432 | 1007.7026 | 20802.192 | 8700.0526 | 121.1667 | 0 | 0 | 21 | 18 | 22 | 1337 | 2 | 789 | 891 | 862 | 102 | 8700.0526 | 35.9167 | 0 | 0 | 19.31 | 19.64 | 13.3 | 50.14 | 0.9337 | 87.79 | 87.16 | 0 | 11462 | 11564 | 5
| 2019-09-02 | 90.1 | 71% | 86.5 | 97 | 82 | 0 | 0 | 24 | 0 | 7 | 13 | 0 | 0 | 0 | 0 | 3497 | 2202 | 1581 | 1558 | 1636 | 40 | 690 | 40 | 0 | 60 | 0 | 78 | -23 | 110 | 61.97% | 145.7083 | 44.55% | 86.31% | 58.31% | 4.805 | 139.66 | 671.0663 | 13.6121 | 1007.7026 | 13716.9659 | 9234.9372 | 91.75 | 10 | 317 | 0 | 0 | 37 | 1440 | 0 | 159 | 940 | 537 | 781 | 9234.9372 | 22.375 | 0 | 0 | 4.39 | 20.56 | 13.54 | 50.11 | 0.9328 | 88.35 | 87.22 | 0 | 12076 | 11541 | 2.13
Week 36 | 2019-09-03 | 93.96 | 67.07% | 87.18 | 103 | 85 | 11 | 4 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3457 | 2401 | 2401 | 2341 | 2426 | 39 | 305 | 39 | 0 | 60 | 0 | 85 | -60 | 121 | 83.54% | 144.0417 | 67.72% | 94.01% | 73.28% | 4.85 | 133.12 | 645.632 | 20.0226 | 1007.7026 | 20176.8751 | 8894.7062 | 100.0417 | 8 | 471 | 0 | 0 | 26 | 1440 | 0 | 674 | 930 | 822 | 256 | 8894.7062 | 34.25 | 0 | 0 | 17.12 | 20.5 | 13.56 | 50.09 | 0.9351 | 88.03 | 87.21 | 0 | 11577 | 11663 | 6
| 2019-09-04 | 95.7 | 65% | 87.1 | 105 | 87 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3441 | 2821 | 2821 | 2748 | 2833 | 39 | 0 | 39 | 0 | 60 | 0 | 85 | -73 | 120 | 98.37% | 143.375 | 79.86% | 100% | 86.23% | 4.399 | 133.58 | 587.6184 | 23.1154 | 1007.7026 | 23293.4698 | 8690.3523 | 117.5417 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 936 | 924 | 973 | -12 | 8690.3523 | 40.5417 | 0 | 0 | 23.09 | 20.5 | 13.27 | 50.14 | 0.9351 | 88.04 | 87.09 | 0 | 11586 | 11671 | 5.9
| 2019-09-05 | 96 | 63.9% | 87.3 | 105 | 88 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3439 | 2817 | 2817 | 2743 | 2832 | 40 | 0 | 39 | 0 | 60 | 0 | 89 | -74 | 120 | 98.33% | 143.2917 | 79.76% | 100% | 86.33% | 3.816 | 133.52 | 509.5123 | 23.0424 | 1007.6717 | 23219.1775 | 8650.6343 | 117.375 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 934 | 927 | 971 | -7 | 8650.6343 | 40.4583 | 0 | 0 | 23.03 | 20.49 | 13.23 | 50.14 | 0.9352 | 87.98 | 86.64 | 0 | 11574 | 11680 | 4.9
| 2019-09-06 | 94 | 68.9% | 88.3 | 102 | 87 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3462 | 2809 | 2809 | 2740 | 2827 | 39 | 0 | 39 | 0 | 60 | 0 | 87 | -69 | 120 | 98.16% | 144.25 | 79.15% | 100% | 85.51% | 4.151 | 131.9 | 547.5169 | 22.9379 | 1011.0299 | 23190.9117 | 8663.6601 | 117.0417 | 0 | 0 | 0 | 0 | 20 | 1440 | 0 | 934 | 924 | 969 | -10 | 8663.6601 | 40.375 | 0 | 0 | 22.98 | 20.39 | 13.26 | 50.16 | 0.9355 | 88.1 | 86.53 | 0 | 11552 | 11651 | 0.75
| 2019-09-07 | 92.07 | 71.3% | 88.7 | 98 | 86 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3476 | 2814 | 2814 | 2750 | 2834 | 39 | 0 | 39 | 0 | 60 | 0 | 84 | -64 | 120 | 98.4% | 144.8333 | 79.11% | 100% | 86.23% | 4.117 | 137.52 | 566.1698 | 23.187 | 1004.6305 | 23294.3312 | 8676.5458 | 117.25 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 936 | 927 | 971 | -9 | 8676.5458 | 40.4583 | 0 | 0 | 23.11 | 20.45 | 13.37 | 50.16 | 0.9337 | 87.98 | 86.46 | 0 | 11587 | 11636 | 5.99
| 2019-09-08 | 93.11 | 68.09% | 87.13 | 101 | 86 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3463 | 2828 | 2828 | 2758 | 2844 | 39 | 0 | 39 | 0 | 60 | 0 | 86 | -70 | 119 | 99.58% | 144.2917 | 79.64% | 100% | 86.23% | 4.099 | 136.64 | 560.0874 | 23.2774 | 1003.0081 | 23347.4493 | 8668.4324 | 117.8333 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 939 | 929 | 976 | -10 | 8668.4324 | 40.6667 | 0 | 0 | 23.19 | 20.63 | 13.42 | 50.15 | 0.9341 | 87.94 | 86.36 | 0 | 11597 | 11703 | 2.01
| 2019-09-09 | 94.9 | 64.8% | 86.6 | 105 | 86 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3451 | 2822 | 2822 | 2750 | 2838 | 39 | 0 | 39 | 0 | 60 | 0 | 88 | -72 | 120 | 98.54% | 143.7917 | 79.69% | 100% | 86.23% | 4.045 | 135.49 | 548.0571 | 23.3633 | 994.6925 | 23239.3326 | 8649.9599 | 117.5833 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 935 | 928 | 975 | -7 | 8649.9599 | 40.625 | 0 | 0 | 23.35 | 20.72 | 13.23 | 50.13 | 0.9344 | 87.7 | 86.26 | 0 | 11719 | 11774 | 3.45
Week 37 | 2019-09-10 | 94.6 | 63.6% | 85.7 | 104 | 87 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3453 | 2826 | 2826 | 2756 | 2840 | 39 | 0 | 39 | 0 | 60 | 0 | 84 | -70 | 121 | 97.8% | 143.875 | 79.81% | 100% | 86.23% | 4.05 | 133.36 | 540.108 | 23.3727 | 994.994 | 23255.7124 | 8634.1874 | 117.75 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 939 | 925 | 976 | -14 | 8634.1874 | 40.6667 | 0 | 0 | 23.35 | 20.6 | 12.63 | 50.12 | 0.9352 | 87.74 | 86.67 | 0 | 11687 | 11711 | 5.65
| 2019-09-11 | 93.43 | 65.15% | 85.64 | 102 | 85 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3458 | 2838 | 2838 | 2759 | 2842 | 39 | 0 | 38 | 0 | 60 | 0 | 83 | -79 | 121 | 97.87% | 144.0833 | 79.79% | 100% | 86.13% | 4.129 | 138.06 | 570.0497 | 23.3146 | 998.799 | 23286.6219 | 8646.8545 | 118.25 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 939 | 927 | 976 | -12 | 8646.8545 | 40.6667 | 0 | 0 | 23.24 | 20.3 | 12.4 | 50.1 | 0.9333 | 87.53 | 86.74 | 0 | 11617 | 11553 | 0
| 2019-09-12 | 93.3 | 66.2% | 86 | 102 | 85 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3465 | 2841 | 2841 | 2765 | 2852 | 39 | 0 | 39 | 0 | 60 | 0 | 87 | -76 | 124 | 95.83% | 144.375 | 79.8% | 100% | 86.23% | 4.1 | 137.51 | 563.791 | 23.2967 | 1006.2672 | 23442.6738 | 8682.2657 | 118.375 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 939 | 926 | 987 | -13 | 8682.2657 | 41.125 | 0.095 | 0 | 23.21 | 20.3 | 11.95 | 50.12 | 0.9336 | 87.61 | 86.89 | 0.095 | 11586 | 11508 | 5.5
| 2019-09-13 | 92.8 | 65.7% | 84.9 | 104 | 84 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3467 | 2845 | 2845 | 2775 | 2862 | 39 | 0 | 39 | 0 | 60 | 0 | 87 | -70 | 121 | 98.55% | 144.4583 | 80.04% | 100% | 86.23% | 4.091 | 138.58 | 566.9308 | 23.373 | 1001.6687 | 23411.9886 | 8641.052 | 118.5417 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 944 | 935 | 983 | -9 | 8641.052 | 40.9583 | 0 | 0 | 23.36 | 20.47 | 12.13 | 50.13 | 0.9332 | 87.57 | 86.99 | 0 | 11617 | 11501 | 0.25
| 2019-09-14 | 91.8 | 63.5% | 82.8 | 102 | 82 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3477 | 2865 | 2865 | 2805 | 2892 | 40 | 0 | 40 | 0 | 60 | 0 | 87 | -60 | 123 | 97.97% | 144.875 | 80.67% | 100% | 86.43% | 4.108 | 137.08 | 563.1246 | 23.5711 | 1001.3576 | 23603.1132 | 8615.4145 | 119.375 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 956 | 944 | 992 | -12 | 8615.4145 | 41.3333 | 0 | 0 | 23.58 | 20.57 | 12.07 | 50.11 | 0.9338 | 87.74 | 86.92 | 0 | 11583 | 11457 | 5.37
| 2019-09-15 | 92.4 | 66.5% | 84.8 | 104 | 84 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3473 | 2842 | 2842 | 2775 | 2858 | 39 | 0 | 39 | 0 | 60 | 0 | 83 | -67 | 121 | 98.42% | 144.7083 | 79.9% | 100% | 86.23% | 4.029 | 142.13 | 572.6418 | 23.3701 | 1002.439 | 23427.0847 | 8648.5501 | 118.4167 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 944 | 930 | 984 | -14 | 8648.5501 | 41 | 0 | 0 | 23.37 | 20.42 | 12.02 | 50.08 | 0.9322 | 87.83 | 87 | 0 | 11599 | 11508 | 5.5
| 2019-09-16 | 93.2 | 63.5% | 84 | 102 | 83 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3469 | 2849 | 2849 | 2785 | 2870 | 40 | 0 | 39 | 0 | 60 | 0 | 85 | -64 | 122 | 98.02% | 144.5417 | 80.28% | 100% | 86.33% | 4.002 | 144.42 | 577.9688 | 23.6415 | 994.8889 | 23520.6762 | 8653.0144 | 118.7083 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 948 | 935 | 987 | -13 | 8653.0144 | 41.125 | 0 | 0 | 23.59 | 20.65 | 12.02 | 50.1 | 0.9311 | 87.75 | 87.06 | 0 | 11681 | 11593 | 0.45
Week 38 | 2019-09-17 | 91.4 | 65.9% | 84 | 103 | 83 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3483 | 2861 | 2861 | 2793 | 2882 | 40 | 0 | 39 | 0 | 60 | 0 | 89 | -68 | 122 | 98.43% | 145.125 | 80.19% | 100% | 86.33% | 3.925 | 135.54 | 531.9945 | 23.7698 | 992.4874 | 23591.225 | 8637.0281 | 119.2083 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 952 | 942 | 988 | -10 | 8643.6421 | 41.1667 | 0 | 0 | 23.61 | 20.78 | 11.91 | 50.13 | 0.9341 | 87.59 | 87.07 | 0 | 11658 | 11561 | 5.9
| 2019-09-18 | 92 | 63.9% | 83.3 | 105 | 82 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3478 | 2866 | 2866 | 2798 | 2882 | 40 | 0 | 39 | 0 | 60 | 0 | 84 | -68 | 123 | 97.63% | 144.9167 | 80.45% | 100% | 86.33% | 3.9 | 142.42 | 555.438 | 23.7626 | 994.3971 | 23629.4727 | 8643.6421 | 119.4167 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 952 | 939 | 991 | -13 | 8649.1871 | 41.2917 | 0 | 0 | 23.61 | 20.77 | 11.72 | 50.1 | 0.9319 | 87.64 | 87.03 | 0 | 11650 | 11579 | 0
| 2019-09-19 | 89.63 | 70.1% | 84.8 | 99.8 | 82.8 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3503 | 2860 | 2860 | 2801 | 2885 | 40 | 0 | 39 | 0 | 60 | 0 | 84 | -59 | 122 | 98.53% | 145.9583 | 79.96% | 100% | 86.33% | 3.904 | 145.2 | 566.8608 | 23.6846 | 998.9401 | 23659.5123 | 8649.1871 | 119.1667 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 950 | 944 | 991 | -6 | 8649.1871 | 41.2917 | 0 | 0 | 23.54 | 20.66 | 12.15 | 50.12 | 0.9308 | 87.56 | 87.25 | 0 | 11625 | 11488 | 5.58
| 2019-09-20 | 87.15 | 71.1% | 82.75 | 95.86 | 80.4 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3529 | 2884 | 2884 | 2827 | 2912 | 40 | 0 | 40 | 0 | 60 | 0 | 85 | -57 | 123 | 98.64% | 147.0417 | 80.11% | 100% | 87.14% | 3.88 | 141.31 | 548.2828 | 23.823 | 1000.6381 | 23838.2342 | 8626.2883 | 120.1667 | 0 | 0 | 0 | 0 | 18 | 1440 | 0 | 961 | 951 | 1000 | -10 | 8626.2883 | 41.6667 | 0 | 0 | 23.74 | 20.84 | 12 | 50.1 | 0.932 | 87.62 | 87.4 | 0 | 11598 | 11482 | 0
| 2019-09-21 | 87.88 | 67.62% | 81.8 | 96.65 | 80.4 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3520 | 2898 | 2898 | 2834 | 2915 | 40 | 0 | 40 | 0 | 60 | 0 | 81 | -64 | 123 | 98.75% | 146.6667 | 80.51% | 100% | 87.14% | 3.883 | 141.99 | 551.3472 | 23.8281 | 1002.4618 | 23886.7535 | 8623.183 | 120.75 | 0 | 0 | 0 | 0 | 18 | 1440 | 0 | 962 | 953 | 1000 | -9 | 8623.183 | 41.6667 | 0 | 0 | 23.75 | 20.84 | 11.9 | 50.1 | 0.9321 | 87.56 | 87.33 | 0 | 11586 | 11455 | 5.75
| 2019-09-22 | 88.64 | 65% | 81 | 99 | 81 | 16 | 5 | 24 | 0 | 7 | 21 | 0 | 0 | 0 | 0 | 3511 | 3054 | 2400 | 2363 | 2445 | 40 | 0 | 40 | 0 | 60 | 0 | 82 | -37 | 122 | 83.5% | 146.2917 | 67.3% | 100% | 81.91% | 3.648 | 143.74 | 524.3635 | 20.128 | 1002.25 | 20173.2547 | 8759.0428 | 127.25 | 14 | 34 | 0 | 0 | 25 | 1440 | 0 | 658 | 956 | 831 | 298 | 8759.0428 | 34.625 | 0 | 0 | 16.38 | 20.8 | 11.58 | 50.1 | 0.9313 | 87.51 | 87.29 | 0 | 11563 | 11384 | 5.3
| 2019-09-23 | 87.93 | 66.11% | 80.8 | 99 | 79 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3522 | 2904 | 2904 | 2839 | 2922 | 40 | 0 | 40 | 0 | 60 | 0 | 83 | -65 | 123 | 98.98% | 146.75 | 80.61% | 100% | 86.43% | 3.739 | 142.32 | 532.1345 | 24.0138 | 1001.3344 | 24045.844 | 8657.2661 | 121 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 965 | 956 | 1001 | -9 | 8657.2661 | 41.7083 | 0 | 0 | 23.81 | 20.94 | 11.49 | 50.09 | 0.9318 | 87.48 | 87.29 | 0 | 11589 | 11429 | 0
Week 39 | 2019-09-24 | 87.5 | 67.5% | 81.1 | 99 | 80 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 3523 | 3108 | 3108 | 3039 | 3132 | 39 | 0 | 40 | 0 | 59 | 0 | 93 | -69 | 139 | 93.88% | 146.7917 | 86.26% | 100% | 93.48% | 3.814 | 144.56 | 551.3518 | 26.2462 | 999.9368 | 26244.57 | 8817.3484 | 129.5 | 0 | 0 | 0 | 0 | 18 | 720 | 0 | 961 | 956 | 1215 | -5 | 8817.3484 | 50.625 | 1.181 | 1.149 | 23.72 | 20.89 | 11.42 | 50.07 | 0.931 | 87.36 | 87.26 | 2.33 | 11590 | 11432 | 6
| 2019-09-25 | 88.4 | 66.5% | 81.5 | 97 | 81 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 3518 | 3106 | 3106 | 3040 | 3128 | 40 | 0 | 40 | 0 | 60 | 0 | 88 | -66 | 140 | 93.1% | 146.5833 | 86.41% | 100% | 93.57% | 3.79 | 147.91 | 560.5789 | 26.1509 | 1002.9567 | 26228.26 | 8812.1181 | 129.4167 | 0 | 0 | 0 | 0 | 18 | 720 | 0 | 959 | 952 | 1217 | -7 | 8812.1181 | 50.7083 | 1.171 | 1.112 | 23.63 | 20.82 | 11.23 | 50.03 | 0.9299 | 87.48 | 87.24 | 2.283 | 11571 | 11401 | 5.58
| 2019-09-26 | 88.6 | 66.9% | 81.7 | 99 | 81 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3515 | 2906 | 2906 | 2828 | 2910 | 40 | 0 | 40 | 0 | 60 | 0 | 82 | -78 | 123 | 98.58% | 146.4583 | 80.46% | 100% | 86.43% | 3.798 | 141.54 | 537.5689 | 23.8291 | 1005.1747 | 23952.359 | 8659.8048 | 121.0833 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 961 | 951 | 998 | -10 | 8659.8048 | 41.5833 | 0 | 0 | 23.68 | 20.87 | 11.34 | 50.1 | 0.9322 | 87.49 | 87.03 | 0 | 11566 | 11442 | 1
| 2019-09-27 | 89.58 | 65.44% | 81.7 | 100 | 81 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3502 | 2881 | 2881 | 2820 | 2905 | 40 | 0 | 39 | 0 | 60 | 0 | 85 | -61 | 123 | 98.41% | 145.9167 | 80.53% | 100% | 86.33% | 3.738 | 143.37 | 535.9171 | 23.5956 | 1009.9125 | 23829.461 | 8640.205 | 120.0417 | 0 | 0 | 0 | 0 | 19 | 1440 | 0 | 959 | 950 | 996 | -9 | 8640.205 | 41.5 | 0 | 0 | 23.4 | 20.61 | 11.25 | 50.12 | 0.9314 | 87.44 | 86.97 | 0 | 11475 | 11333 | 5.1
| 2019-09-28 | 88.7 | 67.1% | 82.1 | 103 | 82 | 24 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 3510 | 3083 | 3083 | 3015 | 3103 | 40 | 0 | 40 | 0 | 60 | 0 | 88 | -68 | 143 | 90.41% | 146.25 | 85.9% | 100% | 92.5% | 3.69 | 147.63 | 544.7547 | 25.7967 | 1008.3108 | 26011.07 | 8807.9021 | 128.4583 | 0 | 0 | 0 | 0 | 18 | 840 | 0 | 954 | 949 | 1200 | -5 | 8807.9021 | 50 | 1.053 | 1.053 | 23.39 | 20.53 | 11.15 | 50.1 | 0.9299 | 87.4 | 86.91 | 2.106 | 11507 | 11303 | 5.45
| 2019-09-29 | 80.1 | 76.7% | 73.1 | 89 | 69 | 24 | 0 | 4 | 36 | 0 | 0 | 19 | 3 | 0 | 0 | 3597 | 3177 | 1692 | 1687 | 1753 | 40 | 0 | 40 | 0 | 60 | 0 | 66 | -5 | 124 | 58.9% | 149.875 | 46.9% | 100% | 74.15% | 0.501 | 145.39 | 72.8404 | 14.7901 | 1010.4239 | 14944.29 | 8901.6778 | 132.375 | 0 | 0 | 13 | 21 | 36 | 1440 | 0 | 982 | 192 | 579 | -790 | 8901.6778 | 24.125 | 0 | 0 | 23.83 | 20.89 | 11.77 | 50.12 | 0.9302 | 87.22 | 86.87 | 0 | 11394 | 11183 | 0
| 2019-09-30 | 83 | 74.6% | 81.32 | 93 | 77 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 3568 | 3488 | 1386 | 1377 | 1449 | 40 | 0 | 40 | 0 | 60 | 0 | 72 | -9 | 62 | 97.38% | 148.6667 | 38.59% | 100% | 71.43% | 0 | 0 | 0 | 12.328 | 1014.8808 | 12511.43 | 9086.0058 | 145.3333 | 0 | 0 | 0 | 0 | 40 | 1440 | 0 | 978 | 0 | 471 | -978 | 9086.0058 | 19.625 | 0 | 0 | 23.66 | 0 | 0 | 50.1 | 0 | 87.31 | 0 | 0 | 11412 | 0 | 5.5
| Monthly | 90.7293 | 0.67299 | 83.9807 | 100.4437 | 82.6867 | 671 | 23 | 675 | 68 | 16 | 37 | 43 | 3 | 34 | 1745 | 104723 | 86404 | 81144 | 79242.43 | 81851 | 39.6 | 1111 | 39.4 | 70 | 59.9667 | 103 | 2610.57 | -1926 | 121.1667 | 93.82% | 145.4486 | 75.67% | 99.12% | 84.34% | 113.391 | 139.7293 | 15803.6454 | 672.8876 | 1003.2121 | 674774.3122 | 8714.7499 |  | 1.0667 | 822 | 1.1333 | 39 | 21.2667 | 41057 | 2 | 26999 | 26433 | 28419 | -566 | 8714.7499 | 39.4708 | 3.5 | 3.314 | 667.02 | 597.43 | 356.31 | 50.112 | 0.90169 | 87.678 | 84.0713 |  | 11596.1333 | 11139.5333 | 110.01
| Totals | Avg.F | % Avg. |  | M Avg | m Avg | hrs | min | hrs | min | hrs | min | hrs | min | Avg Int Avi | Avg Ext Avi | MWhr Total | MWhr Total | MWhr Total | MWhr Total | MWhr Total | MW Avg | Total min | Avg MW | Total min | Avg MW | Total min | MWhr | Total MW | Av Max D/Gen | Av. DailyLF | Avg. | Avg. |  | Avg. | Total | Avg. |  | Total | Avg. |  | Avg. | [7 empty] | Total |  |  |  |  | Avg.
| Weeks data | Site Avg. Amb. Temp F | Site Avg. Relative humidity % | Site Avg. Ambient Wetbulb Temp.F | M Avg: Site Maximum/Minumum Temperature; hrs: CT-1 Base Load Hours; hrs: CT-2 Base Load Hours; hrs: CT-1 stand by hours / min; hrs: CT-2 standby hours / min | Plant ambient Corrected maximum Load hours/min |  | Average Corrected Plant Capacity | Ambient Corrected Declared Avail'y (MWH) | Av Plant WAPDA Dispatch | Net Plant Export (MWH) | Gross Generation | CT1 Av Cap (MW) | CT1 Unavail minutes | CT2 Av Cap (MW) | CT2 Unavail minutes | ST Unavail minutes | ST Average Cap (MW) | Plant Aux Load including Colony Load MWH | Differenece (+/-) MW | Maximum Daily Generation | Daily Load Factor | Avg. Corrected Plant | Plant Capacity Facto | Plant Availability Factor | Equivalent Plant Availability | LBtu gas flow mmscf | 1 LBtu gas (Average Btu/scf) | LBTU MMBTU | PL gas flow (mscf/week) | 1 PL gas (Average Btu/scf) | HBTU MMBTU | Plant Net Heat Rate (Btu/Kwh) | [11 empty] | -9.6
| Week 35 | 91.4 | 68.56% | 85.6571 | 99.7143 | 84.4286 | 118 | 19 | 165 | 4 | 30 | 2 | 0 | 0 | 0 | 0 | 3482.7143 | 2846.1429 | 2414.8571 | 2370 | 2451.7143 | 39.7143 | 806 | 39.5714 | 141 | 420 | no data | no data | -314 | 119.4286 | 85.23% | 145.1131 | 68.08% | 96.44% | 78.67% | 34.193 | 131.6129 | 4500.2384 | 140.1626 | 1008.9448 | 141416.3517 | 8823.0963
| Week36 | 94.2486 | 67.01% | 87.4729 | 102.7143 | 86.4286 | 155 | 2 | 168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3455.5714 | 2758.8571 | 2758.8571 | 18830 | 19434 | 39.1429 | 305 | 273 | no data | 420 | no data | 604 | -482 | 120 | 96.42% | 143.9821 | 77.85% | 99.14% | 84.29% | 29.477 | 134.5386 | 3965.7935 | 158.9461 | 1005.2054 | 159773.488 | 8699.1844 | [5 empty] | 0.27381
| Week37 | 93.0757 | 64.88% | 84.8343 | 102.8571 | 84.2857 | 168 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3466 | 2843.7143 | 2843.7143 | 19420 | 20016 | 39.2857 | No outage | 273 | no data | 420 | no data | 596 | -486 | 121.8571 | 97.78% | 144.4167 | 80.04% | 100% | 86.26% | 28.509 | 138.7343 | 3955.1758 | 140.2982 | 1000.9209 | 140427.395 | 8645.9055 |  |  |  |  | 840 | 0.26672
| Week38 | 89.2329 | 67.1% | 84.8343 | 99.7586 | 81.2286 | 160 | 5 | 168 | 0 | 7 | 21 | 0 | 0 | 0 | 0 | 3506.5714 | 2903.8571 | 2810.4286 | 19255 | 19843 | 40 | No outage | 277 | no data | 420 | no data | 588 | -418 | 122.5714 | 96.35% | 146.1071 | 78.45% | 100% | 85.94% | 26.879 | 141.7886 | 3811.135 | 163.0099 | 998.9299 | 162835.4726 | 8656.5197
| Week 39 | 88.6757 | 67.33% | 84.5914 | 99.1871 | 80.8 | 160 | 5 | 168 | 0 | 7 | 21 | 0 | 0 | 12 | 0 | 3512.2857 | 2939.1429 | 2845.7143 | 19501 | 20093 | 39.8571 | No outage | 278 | no data | 419 | no data | 592 | -419 | 125 | 95.7% | 146.3452 | 79.31% | 100% | 86.97% | 26.768 | 143.0771 | 3829.889 | 165.4863 | 999.9941 | 165485.3639 | 8682.2797
336
| Date | Plant Status Whether Normal Operation or Tripping (State full detail for trippings/return to normal). | [61 empty] | 420
| 2019-09-01 | Complex tripped at 2002 hrs due to Wapda supply failure. CT-2 synch @ 2112 hrs & STG @ 2145 hrs whereas NPCC demand of 56 MW received @ 2158 hrs. CT-1 is in standby mode as per NPCC demand. | [61 empty] | 360
| 2019-09-02 | CT-1 synch @ 0713 hrs as per NPCC demand of Max load (144 MW). CT-1 Desynch @ 0736 hrs due to internal fault. CT-1 Synch @ 1906 hrs after rectification of internal fault. | [61 empty] | 1116
| 2019-09-03 | CT-1 De-synch @ 0728 hrs and Synch @ 1233 hrs after rectification of high bladepath spread issue. | [62 empty] | 22.32
| 2019-09-04 | Plant load restricted to 113~116 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heat rate.
| 2019-09-05 | Plant load restricted to 113~116 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heat rate.
| 2019-09-06 | Plant load restricted to 112~116 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heat rate.
| 2019-09-07 | Plant load restricted to 113~116 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heat rate.
| 2019-09-08 | Plant load restricted to 114~116 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heat rate.
| 2019-09-09 | Plant load restricted to 113~116 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heat rate.
| 2019-09-10 | Plant load restricted to 113~117 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heat rate.
| 2019-09-11 | Plant load restricted to 113~117 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heat rate.
| 2019-09-12 | Plant load restricted to 113~120 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heat rate.
| 2019-09-13 | Plant load restricted to 114~118 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heat rate.
| 2019-09-14 | Plant load restricted to 115~118 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heat rate.
| 2019-09-15 | Plant load restricted to 114~118 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heat rate.
| 2019-09-16 | Plant load restricted to 115~118 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heat rate.
| 2019-09-17 | Plant load restricted to 115~118 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heat rate.
| 2019-09-18 | Plant load restricted to 115~119 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heat rate.
| 2019-09-19 | Plant load restricted to 115~118 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heat rate.
| 2019-09-20 | Plant load restricted to 116~119 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heat rate.
| 2019-09-21 | Plant load restricted to 117~119 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heat rate.
| 2019-09-22 | CT-1 de-synch @ 0307 hrs as per NPCC demand of 57 MW. CT-1 synch @ 1028 hrs as per NPCC max. load demand.
| 2019-09-23 | Plant load restricted to 117~120 MW from 0000~2400 hrs as both DBs kept off to remain within contractual heat rate.
| 2019-09-24 | Plant load remained Maximum (135 MW) from 1100~2300 hrs by keeping DB’s into service. Plant load restricted to 118~120 MW from 0000~1100 hrs and 2300~2400 hrs as both DB's kept off to remain within contractual heat rate.
| 2019-09-25 | Plant load remained Maximum (135 MW) from 1100~2300 hrs by keeping DB’s into service. Plant load restricted to 117~119 MW from 0000~1100 hrs and 2300~2400 hrs as both DB's kept off to remain within contractual heat rate.
| 2019-09-26 | Plant load restricted to 117~119 MW from 0000~2400 hrs as both DB's kept off to remain within contractual heat rate.
| 2019-09-27 | Plant load restricted to 116~120 MW from 0000~2400 hrs as both DB's kept off to remain within contractual heat rate.
| 2019-09-28 | Plant load remained (134~139 MW) from 1300~2300 hrs by keeping DB’s into service. Plant load restricted to 116~120 MW from 0000~1300 hrs and 2300~2400 hrs as both DB's kept off to remain within contractual heat rate.
| 2019-09-29 | CT-2 desynchronized at 04:57 hrs and remained standby as per 58 MW demand of NPCC.
| 2019-09-30 | CT-2 remained shutdown and at standby mode at 58 MW demand of NPCC. CT-2 compressor offline washing carried out.
[5 empty] | hrs: 0.066667 |  |  |  | 0.81667 |  | 0.3
[5 empty] | hrs: 0.81667 |  |  |  | 0.53333
0.28333
0.25
0.18333
0.93333
Note on BN6: ops.e: assumed due to problem of GC of OGDCL.

## Oct
Monthly Operational Returns Kabirwala
2019-10-01
| Date | Site Avg. Ambient Temp.F | Site Avg. Relative Humidty % | Site Avg. Ambient Wetbulb Temp.F | Site Ambient Temp |  | Base load hours |  |  |  | Standby hours |  |  |  | Plant ambient corrected Max Load |  | Corrected Plant Capacity | Ambient Corrected Daclared Avail'y (MWH) | Plant WAPDA Dispatch (MWH) | Net Plant Export (MWH) | Gross Generation | CT1 Average Cap (MW) | CT1 Unavail minutes | CT2 Average Cap (MW) | CT2 Unavail minutes | ST Average Cap (MW) | ST Unavail minutes | Plant Aux Load including Colony Load MWH | Differenece (+/-) MW | Maximum Daily Generation | Daily Load Factor | Avg. Corrected Plant Capacity | Plant Capacity Factor | Plant Availability Factor | Equivalent Plant Availability | LBtu gas flow (mmscf/day) | 1 LBtu gas (Average Btu/scf) | LBTU MMBTU | 1 HBtu gas flow (mmscf/day) | 1 HBtu gas (Average Btu/scf) | HBTU MMBTU | HHV Net Heat Rate (Btu/Kwh) | Avg. declared availability | CT1 Derated MW | CT1 derated mintutes | CT-2 derated MW | CT-2 derated mintutes | ST derated MW | ST derated mintutes | WAPDA Backfeed (MWH) | CT-1 Gross Generation (MWH) | CT-2 Gross Generation (MWH) | STG Gross Generation (MWH) | CT-1 & CT-2 MWH difference | Base load Heat Rate | STG load | DB1 | DB2 | CT1 Gas flow | CT2 Gas flow |  | Freq. Hz | LBTU Gas Specific gravity | CT-1 compressor efficiency(%) | CT-2 compressor efficiency(%) | DB(1+2) | CT-1 Heat Rate (Btu/Kwh) | CT-2 Heat Rate (Btu/Kwh) | RO Operation Hours
[7 empty] | CT1 |  | CT2 |  | CT1 |  | CT2 | [43 empty] | mmscf/d | mmscf/d | HBTU KPPH | HBTU KPPH | LBTU KPPH | Hz |  |  |  | mmscf/d
[5 empty] | Max | Min | hrs | min | hrs | min | hrs | min | hrs | min | hrs | min
Week 40 | 2019-10-01 | 84.1 | 72% | 81.3 | 92 | 78 | 17 | 55 | 0 | 0 | 5 | 52 | 24 | 0 | 0 | 0 | 3557 | 3492 | 1045 | 1024.42 | 1076 | 40 | 0 | 40 | 0 | 60 | 0 | 57.58 | -20.58 | 61 | 73.5% | 148.2083 | 28.8% | 100% | 78.36% | 0 | 0 | 0 | 9.359 | 1008.12 | 9434.9951 | 9210.0848 | 145.5 | 14 | 13 | 0 | 0 | 40 | 1086 | 6 | 724 | 0 | 352 | -724 | 9210.0848 | 14.6667 | 0 | 0 | 23.71 | 0 | 0 | 50.09 | 0 | 87.28 | 0 | 0 | 11449 | 0 | 0
| 2019-10-02 | 83.5 | 69% | 78.9 | 93.9 | 75.9 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3562 | 3512 | 0 | 0 | 0 | 40 | 0 | 40 | 0 | 60 | 0 | 16 | 0 | 0 | no data | 148.4167 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 146.3333 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 50.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-10-03 | 82.34 | 66.29% | 76.1 | 94.97 | 72.76 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3547 | 3511 | 0 | 0 | 0 | 40 | 0 | 40 | 0 | 60 | 0 | 14 | 0 | 0 | no data | 147.7917 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 146.2917 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-10-04 | 79.02 | 68.8% | 74.64 | 89 | 72 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3597 | 3521 | 0 | 0 | 0 | 40 | 0 | 40 | 0 | 60 | 0 | 11 | 0 | 0 | no data | 149.875 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 146.7083 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 50.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-10-05 | 81 | 67.1% | 75.3 | 92 | 73 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3588 | 3521 | 0 | 0 | 0 | 40 | 0 | 40 | 0 | 60 | 0 | 9 | 0 | 0 | no data | 149.5 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 146.7083 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 50.09 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1
| 2019-10-06 | 73.4 | 76.6% | 73.3 | 79 | 70 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3652 | 3525 | 0 | 0 | 0 | 40 | 0 | 40 | 0 | 60 | 0 | 8 | 0 | 0 | no data | 152.1667 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 146.875 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 50.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-10-07 | 76.4 | 70% | 71.1 | 94 | 67.4 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3632 | 3528 | 0 | 0 | 0 | 40 | 0 | 40 | 0 | 60 | 0 | 10 | 0 | 0 | no data | 151.3333 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 147 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 50.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Week 41 | 2019-10-08 | 79.6 | 63.2% | 66.9 | 96.7 | 68.8 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3610 | 3528 | 0 | 0 | 0 | 40 | 0 | 40 | 0 | 60 | 0 | 8 | 0 | 0 | no data | 150.4167 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 147 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 50.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-10-09 | 81.3 | 62.9% | 68.3 | 93 | 71 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3578 | 3532 | 0 | 0 | 0 | 40 | 0 | 40 | 0 | 60 | 0 | 9 | 0 | 0 | no data | 149.0833 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 147.1667 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 50.11 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2
| 2019-10-10 | 81.4 | 61.8% | 72.95 | 97 | 71 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3580 | 3533 | 0 | 0 | 0 | 40 | 0 | 40 | 0 | 60 | 0 | 7 | 0 | 0 | no data | 149.1667 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 147.2083 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-10-11 | 82.4 | 63% | 77.6 | 98 | 73 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3566 | 3533 | 0 | 0 | 0 | 40 | 0 | 40 | 0 | 60 | 0 | 6 | 0 | 0 | no data | 148.5833 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 147.2083 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-10-12 | 83.1 | 62.7% | 75.1 | 96 | 73 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3566 | 3534 | 0 | 0 | 0 | 40 | 0 | 40 | 0 | 60 | 0 | 6 | 0 | 0 | no data | 148.5833 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 147.25 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5
| 2019-10-13 | 82.89 | 64.84% | 75.64 | 94 | 73.5 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3567 | 3535 | 0 | 0 | 0 | 40 | 0 | 40 | 0 | 60 | 0 | 7 | 0 | 0 | no data | 148.625 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 147.2917 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-10-14 | 82 | 63.4% | 73.7 | 96 | 73 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3576 | 3531 | 0 | 0 | 0 | 40 | 0 | 40 | 0 | 60 | 0 | 8 | 0 | 0 | no data | 149 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 147.125 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Week 42 | 2019-10-15 | 82.17 | 59.02% | 72.27 | 96.4 | 71.65 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3572 | 3531 | 0 | 0 | 0 | 40 | 0 | 40 | 0 | 60 | 0 | 6 | 0 | 0 | no data | 148.8333 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 147.125 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-10-16 | 82 | 59% | 71.8 | 94 | 72 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3575 | 3531 | 0 | 0 | 0 | 40 | 0 | 40 | 0 | 60 | 0 | 8 | 0 | 0 | no data | 148.9583 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 147.125 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-10-17 | 82 | 63.6% | 73.8 | 94 | 73 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3579 | 3534 | 0 | 0 | 0 | 40 | 0 | 40 | 0 | 60 | 0 | 6 | 0 | 0 | no data | 149.125 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 147.25 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-10-18 | 76.6 | 61.9% | 68.7 | 85 | 70 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3628 | 3534 | 0 | 0 | 0 | 40 | 0 | 40 | 0 | 60 | 0 | 6 | 0 | 0 | no data | 151.1667 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 147.25 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-10-19 | 75.3 | 63.4% | 68.4 | 89 | 66 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3638 | 3539 | 0 | 0 | 0 | 40 | 0 | 40 | 0 | 60 | 0 | 5 | 0 | 0 | no data | 151.5833 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 147.4583 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1
| 2019-10-20 | 77 | 61.4% | 68.9 | 90 | 67 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3625 | 3542 | 0 | 0 | 0 | 40 | 0 | 40 | 0 | 60 | 0 | 5 | 0 | 0 | no data | 151.0417 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 147.5833 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-10-21 | 77.5 | 61.8% | 69.8 | 91 | 67 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3623 | 3546 | 0 | 0 | 0 | 40 | 0 | 40 | 0 | 60 | 0 | 7 | 0 | 0 | no data | 150.9583 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 147.75 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Week 43 | 2019-10-22 | 77.93 | 61.42% | 69.69 | 93.26 | 67.89 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3615 | 3550 | 0 | 0 | 0 | 40 | 0 | 40 | 0 | 60 | 0 | 5 | 0 | 0 | no data | 150.625 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 147.9167 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-10-23 | 78.5 | 57.98% | 67.98 | 91 | 69 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3612 | 3554 | 0 | 0 | 0 | 40 | 0 | 40 | 0 | 60 | 0 | 6 | 0 | 0 | no data | 150.5 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 148.0833 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 2
| 2019-10-24 | 78.7 | 62.4% | 70.4 | 90 | 70 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3605 | 3557 | 0 | 0 | 0 | 40 | 0 | 40 | 0 | 60 | 0 | 5 | 0 | 0 | no data | 150.2083 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 148.2083 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-10-25 | 78.5 | 62.5% | 70.8 | 90 | 70 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3608 | 3557 | 0 | 0 | 0 | 40 | 0 | 40 | 0 | 60 | 0 | 5 | 0 | 0 | no data | 150.3333 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 148.2083 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-10-26 | 77.9 | 63.5% | 70.5 | 90 | 68 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3616 | 3559 | 0 | 0 | 0 | 40 | 0 | 40 | 0 | 60 | 0 | 6 | 0 | 0 | no data | 150.6667 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 148.2917 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-10-27 | 76.7 | 65.9% | 70.7 | 88 | 69 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3625 | 3560 | 0 | 0 | 0 | 40 | 0 | 40 | 0 | 60 | 0 | 5 | 0 | 0 | no data | 151.0417 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 148.3333 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-10-28 | 76.9 | 63.7% | 69.7 | 92 | 66 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3626 | 3561 | 0 | 0 | 0 | 40 | 0 | 40 | 0 | 60 | 0 | 6 | 0 | 0 | no data | 151.0833 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 148.375 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Week 44 | 2019-10-29 | 77.4 | 60.1% | 68.1 | 93 | 67 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3623 | 3562 | 0 | 0 | 0 | 40 | 0 | 40 | 0 | 60 | 0 | 5 | 0 | 0 | no data | 150.9583 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 148.4167 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-10-30 | 76.9 | 58.4% | 67.5 | 91 | 67 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3625 | 3564 | 0 | 0 | 0 | 40 | 0 | 40 | 0 | 60 | 0 | 5 | 0 | 0 | no data | 151.0417 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 148.5 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-10-31 | 78 | 57.8% | 67.8 | 94 | 67 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3614 | 3569 | 0 | 0 | 0 | 40 | 0 | 40 | 0 | 60 | 0 | 5 | 0 | 0 | no data | 150.5833 | no data | 100% | no data | 0 | 0 | 0 | 0 | 0 | 0 | no data | 148.7083 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-11-01 | [26 empty] | 0 | 0 |  | no data | no data | no data | #DIV/0! | no data |  |  | 0 |  |  | 0 | no data | 0 | [10 empty] | 0 | no data | 0 | [9 empty] | 0
| 2019-11-02 | [26 empty] | 0 | 0 |  | no data | no data | no data | #DIV/0! | no data |  |  | 0 |  |  | 0 | no data | 0 | [10 empty] | 0 | no data | 0 | [9 empty] | 0
| 2019-11-03 | [26 empty] | 0 | 0 |  | no data | no data | no data | #DIV/0! | no data |  |  | 0 |  |  | 0 | no data | 0 | [10 empty] | 0 | no data | 0 | [9 empty] | 0
| 2019-11-04 | [26 empty] | 0 | 0 |  | no data | no data | no data | #DIV/0! | no data |  |  | 0 |  |  | 0 | no data | 0 | [10 empty] | 0 | no data | 0 | [9 empty] | 0
| Monthly | 79.4339 | 0.63724 | 71.8603 | 92.1687 | 70.3194 | 17 | 55 | 0 | 12 | 725 | 64 | 744 | 0 | 0 | 1859 | 111587 | 109686 | 1045 | 1024.42 | 1076 | 40 | 0 | 40 | 0 | 60 | 0 | 272.58 | -20.58 | 1.9677 | 0.73497 | 149.9825 | 0.288 | 100% | 0.78362 | 0 | 0 | 0 | 9.359 | 32.52 | 9434.9951 | 9210.0848 |  | 0.45161 | 13 | 0 | 0 | 1.2903 | 1086 | 221 | 724 | 0 | 352 | -724 | 9210.0848 | 0.47312 | 0 | 0 | 23.71 | 0 | 0 | 50.0247 | 0 | 2.8155 | 0 |  | 369.3226 | 0 | 6.9
| Totals | Avg.F | % Avg. |  | M Avg | m Avg | hrs | min | hrs | min | hrs | min | hrs | min | Avg Int Avi | Avg Ext Avi | MWhr Total | MWhr Total | MWhr Total | MWhr Total | MWhr Total | MW Avg | Total min | Avg MW | Total min | Avg MW | Total min | MWhr | Total MW | Av Max D/Gen | Av. DailyLF | Avg. | Avg. |  | Avg. | Total | Avg. |  | Total | Avg. |  | Avg. | [7 empty] | Total |  |  |  |  | Avg.
| Weeks data | Site Avg. Amb. Temp F | Site Avg. Relative humidity % | Site Avg. Ambient Wetbulb Temp.F | M Avg: Site Maximum/Minumum Temperature; hrs: CT-1 Base Load Hours; hrs: CT-2 Base Load Hours; hrs: CT-1 stand by hours / min; hrs: CT-2 standby hours / min | Plant ambient Corrected maximum Load hours/min |  | Average Corrected Plant Capacity | Ambient Corrected Declared Avail'y (MWH) | Av Plant WAPDA Dispatch | Net Plant Export (MWH) | Gross Generation | CT1 Av Cap (MW) | CT1 Unavail minutes | CT2 Av Cap (MW) | CT2 Unavail minutes | ST Unavail minutes | ST Average Cap (MW) | Plant Aux Load including Colony Load MWH | Differenece (+/-) MW | Maximum Daily Generation | Daily Load Factor | Avg. Corrected Plant | Plant Capacity Facto | Plant Availability Factor | Equivalent Plant Availability | LBtu gas flow mmscf | 1 LBtu gas (Average Btu/scf) | LBTU MMBTU | PL gas flow (mscf/week) | 1 PL gas (Average Btu/scf) | HBTU MMBTU | Plant Net Heat Rate (Btu/Kwh) | [11 empty] | 0
| Week 40 | 79.9657 | 69.97% | 75.8057 | 90.6957 | 72.7229 | 17 | 55 | 0 | 0 | 149 | 52 | 168 | 0 | 0 | 0 | 3590.7143 | 3515.7143 | 149.2857 | 146.3457 | 153.7143 | 40 | No outage | 40 | No outage | 420 | no data | no data | -20.58 | 8.7143 | 73.5% | 149.6131 | 28.8% | 100% | 78.36% | no data | no data | #VALUE! | 9.359 | 144.0171 | 1347.8564 | 9210.0848
| Week 41 | 81.8129 | 63.12% | 72.8843 | 95.8143 | 71.9 | 0 | 0 | 0 | -120 | 168 | -120 | 168 | 0 | 0 | 0 | 3577.5714 | 3532.2857 | no data | no data | no data | 40 | No outage | 280 | no data | 420 | no data | 51 | no data | no data | #DIV/0! | 149.0655 | #DIV/0! | 100% | #DIV/0! | no data | no data | #VALUE! | no data | no data | #VALUE! | #DIV/0! | [5 empty] | 0.27381
| Week 42 | 78.9386 | 61.45% | 70.5243 | 91.3429 | 69.5214 | 0 | 0 | 0 | 0 | 168 | 0 | 168 | 0 | 0 | 0 | 3605.7143 | 3536.7143 | no data | no data | no data | 40 | No outage | 280 | no data | 420 | no data | 43 | no data | no data | #DIV/0! | 150.2381 | #DIV/0! | 100% | #DIV/0! | no data | no data | #VALUE! | no data | no data | #VALUE! | #DIV/0! |  |  |  |  | 840 | 0.26672
| Week 43 | 77.8757 | 62.49% | 70.5243 | 90.6086 | 68.5557 | 0 | 0 | 0 | 0 | 168 | 0 | 168 | 0 | 0 | 0 | 3615.2857 | 3556.8571 | no data | no data | no data | 40 | No outage | 280 | no data | 420 | no data | 38 | no data | no data | #DIV/0! | 150.6369 | #DIV/0! | 100% | #DIV/0! | no data | no data | #VALUE! | no data | no data | #VALUE! | #DIV/0!
| Week 44 | 77.8 | 62.3% | 70.1557 | 90.5714 | 68.4286 | 0 | 0 | 0 | 0 | 168 | 0 | 168 | 0 | 0 | 0 | 3616.4286 | 3558.5714 | no data | no data | no data | 40 | No outage | 280 | no data | 420 | no data | 38 | no data | no data | #DIV/0! | 150.6845 | #DIV/0! | 100% | #DIV/0! | no data | no data | #VALUE! | no data | no data | #VALUE! | #DIV/0!
336
| Date | Plant Status Whether Normal Operation or Tripping (State full detail for trippings/return to normal). | [61 empty] | 420
| 2019-10-01 | CT-2 remained shutdown and at standby mode at 58 MW demand of NPCC. ST @ 1806 hrs & CT-1 @ 1808 hrs desynch as per NPCC 00 MW demand. | [61 empty] | 360
| 2019-10-02 | Plant remained shutdown and in standby mode from 0000~2400 hrs as per NPCC demand. | [61 empty] | 1116
| 2019-10-03 | Plant remained shutdown and in standby mode from 0000~2400 hrs as per NPCC demand. | [62 empty] | 22.32
| 2019-10-04 | Plant remained shutdown and in standby mode from 0000~2400 hrs as per NPCC demand.
| 2019-10-05 | Plant remained shutdown and in standby mode from 0000~2400 hrs as per NPCC demand.
| 2019-10-06 | Plant remained shutdown and in standby mode from 0000~2400 hrs as per NPCC demand.
| 2019-10-07 | Plant remained shutdown and in standby mode from 0000~2400 hrs as per NPCC demand.
| 2019-10-08 | Plant remained shutdown and in standby mode from 0000~2400 hrs as per NPCC demand.
| 2019-10-09 | Plant remained shutdown and in standby mode from 0000~2400 hrs as per NPCC demand.
| 2019-10-10 | Plant remained shutdown and in standby mode from 0000~2400 hrs as per NPCC demand.
| 2019-10-11 | Plant remained shutdown and in standby mode from 0000~2400 hrs as per NPCC demand.
| 2019-10-12 | Plant remained shutdown and in standby mode from 0000~2400 hrs as per NPCC demand.
| 2019-10-13 | Plant remained shutdown and in standby mode from 0000~2400 hrs as per NPCC demand.
| 2019-10-14 | Plant remained shutdown and in standby mode from 0000~2400 hrs as per NPCC demand.
| 2019-10-15 | Plant remained shutdown and in standby mode from 0000~2400 hrs as per NPCC demand.
| 2019-10-16 | Plant remained shutdown and in standby mode from 0000~2400 hrs as per NPCC demand.
| 2019-10-17 | Plant remained shutdown and in standby mode from 0000~2400 hrs as per NPCC demand.
| 2019-10-18 | Plant remained shutdown and in standby mode from 0000~2400 hrs as per NPCC demand.
| 2019-10-19 | Plant remained shutdown and in standby mode from 0000~2400 hrs as per NPCC demand.
| 2019-10-20 | Plant remained shutdown and in standby mode from 0000~2400 hrs as per NPCC demand.
| 2019-10-21 | Plant remained shutdown and in standby mode from 0000~2400 hrs as per NPCC demand.
| 2019-10-22 | Plant remained shutdown and in standby mode from 0000~2400 hrs as per NPCC demand.
| 2019-10-23 | Plant remained shutdown and in standby mode from 0000~2400 hrs as per NPCC demand.
| 2019-10-24 | Plant remained shutdown and in standby mode from 0000~2400 hrs as per NPCC demand.
| 2019-10-25 | Plant remained shutdown and in standby mode from 0000~2400 hrs as per NPCC demand.
| 2019-10-26 | Plant remained shutdown and in standby mode from 0000~2400 hrs as per NPCC demand.
| 2019-10-27 | Plant remained shutdown and in standby mode from 0000~2400 hrs as per NPCC demand.
| 2019-10-28 | Plant remained shutdown and in standby mode from 0000~2400 hrs as per NPCC demand.
| 2019-10-29 | Plant remained shutdown and in standby mode from 0000~2400 hrs as per NPCC demand.
| 2019-10-30 | Plant remained shutdown and in standby mode from 0000~2400 hrs as per NPCC demand.
| 2019-10-31 | Plant remained shutdown and in standby mode from 0000~2400 hrs as per NPCC demand.
[5 empty] | hrs: 0.066667 |  |  |  | 0.81667 |  | 0.3
[5 empty] | hrs: 0.81667 |  |  |  | 0.53333
0.28333
0.25
0.18333
0.93333

## Nov
Monthly Operational Returns Kabirwala
2019-11-01
| Date | Site Avg. Ambient Temp.F | Site Avg. Relative Humidty % | Site Avg. Ambient Wetbulb Temp.F | Site Ambient Temp |  | Base load hours |  |  |  | Standby hours |  |  |  | Plant ambient corrected Max Load |  | Corrected Plant Capacity | Ambient Corrected Daclared Avail'y (MWH) | Plant WAPDA Dispatch (MWH) | Net Plant Export (MWH) | Gross Generation | CT1 Average Cap (MW) | CT1 Unavail minutes | CT2 Average Cap (MW) | CT2 Unavail minutes | ST Average Cap (MW) | ST Unavail minutes | Plant Aux Load including Colony Load MWH | Differenece (+/-) MW | Maximum Daily Generation | Daily Load Factor | Avg. Corrected Plant Capacity | Plant Capacity Factor | Plant Availability Factor | Equivalent Plant Availability | 1 HBtu gas flow (mmscf/day) | 1 HBtu gas (Average Btu/scf) | HBTU MMBTU | HHV Net Heat Rate (Btu/Kwh) | Avg. declared availability | CT1 Derated MW | CT1 derated mintutes | CT-2 derated MW | CT-2 derated mintutes | ST derated MW | ST derated mintutes | WAPDA Backfeed (MWH) | CT-1 Gross Generation (MWH) | CT-2 Gross Generation (MWH) | STG Gross Generation (MWH) | CT-1 & CT-2 MWH difference | Base load Heat Rate | STG load | DB1 | DB2 | CT1 Gas flow | CT2 Gas flow | Freq. Hz | CT-1 compressor efficiency(%) | CT-2 compressor efficiency(%) | DB(1+2) | CT-1 Heat Rate (Btu/Kwh) | CT-2 Heat Rate (Btu/Kwh) | RO Operation Hours
[7 empty] | CT1 |  | CT2 |  | CT1 |  | CT2 | [40 empty] | mmscf/d | mmscf/d | HBTU KPPH | HBTU KPPH | Hz |  |  | mmscf/d
[5 empty] | Max | Min | hrs | min | hrs | min | hrs | min | hrs | min | hrs | min
Week 44 | 2019-10-29 | 75.7 | 64.8% | 69.1 | 88 | 70 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3638 | 3588 | 0 | 0 | 0 | 40 | 0 | 40 | 0 | 60 | 0 | 4 | 0 | 0 | no data | 151.5833 | no data | 100% | no data | 0 | 0 | 0 | no data | 149.5 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-10-30 | 75.6 | 67.6% | 70.2 | 84 | 68 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3642 | 3592 | 0 | 0 | 0 | 40 | 0 | 40 | 0 | 60 | 0 | 5 | 0 | 0 | no data | 151.75 | no data | 100% | no data | 0 | 0 | 0 | no data | 149.6667 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-10-31 | 78 | 57.8% | 66.42 | 94 | 67 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3614 | 3569 | 0 | 0 | 0 | 40 | 0 | 40 | 0 | 60 | 0 | 5 | 0 | 0 | no data | 150.5833 | no data | 100% | no data | 0 | 0 | 0 | no data | 148.7083 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-11-01 | 75.7 | 64.8% | 69.04 | 88 | 70 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3638 | 3588 | 0 | 0 | 0 | 40 | 0 | 40 | 0 | 60 | 0 | 4 | 0 | 0 | no data | 151.5833 | no data | 100% | no data | 0 | 0 | 0 | no data | 149.5 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-11-02 | 75.6 | 67.4% | 69.96 | 84 | 68 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3642 | 3592 | 0 | 0 | 0 | 40 | 0 | 40 | 0 | 60 | 0 | 5 | 0 | 0 | no data | 151.75 | no data | 100% | no data | 0 | 0 | 0 | no data | 149.6667 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-11-03 | 76.14 | 61.9% | 68.32 | 90 | 67 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3631 | 3593 | 0 | 0 | 0 | 40 | 0 | 40 | 0 | 60 | 0 | 5 | 0 | 0 | no data | 151.2917 | no data | 100% | no data | 0 | 0 | 0 | no data | 149.7083 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-11-04 | 75.9 | 64.5% | 69.4 | 89 | 66 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3635 | 3592 | 0 | 0 | 0 | 40 | 0 | 40 | 0 | 60 | 0 | 4 | 0 | 0 | no data | 151.4583 | no data | 100% | no data | 0 | 0 | 0 | no data | 149.6667 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
Week 45 | 2019-11-05 | 75.4 | 61% | 67.5 | 92 | 65 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3639 | 3594 | 0 | 0 | 0 | 40 | 0 | 40 | 0 | 60 | 0 | 5 | 0 | 0 | no data | 151.625 | no data | 100% | no data | 0 | 0 | 0 | no data | 149.75 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-11-06 | 73.1 | 58.1% | 64.3 | 87 | 64.6 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3662 | 3599 | 0 | 0 | 0 | 40 | 0 | 40 | 0 | 60 | 0 | 5 | 0 | 0 | no data | 152.5833 | no data | 100% | no data | 0 | 0 | 0 | no data | 149.9583 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-11-07 | 65.33 | 66.96% | 61.5 | 72 | 59 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3712 | 3618 | 0 | 0 | 0 | 40 | 0 | 40 | 0 | 60 | 0 | 4 | 0 | 0 | no data | 154.6667 | no data | 100% | no data | 0 | 0 | 0 | no data | 150.75 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-11-08 | 64.3 | 69.4% | 60.9 | 77.85 | 55.86 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3705 | 3642 | 0 | 0 | 0 | 40 | 0 | 40 | 0 | 60 | 0 | 5 | 0 | 0 | no data | 154.375 | no data | 100% | no data | 0 | 0 | 0 | no data | 151.75 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-11-09 | 67.2 | 61.7% | 60.4 | 86 | 57 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3691 | 3644 | 0 | 0 | 0 | 42 | 0 | 42 | 0 | 60 | 0 | 4 | 0 | 0 | no data | 153.7917 | no data | 100% | no data | 0 | 0 | 0 | no data | 151.8333 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-11-10 | 68.4 | 56.5% | 59.7 | 86 | 56 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3680 | 3642 | 0 | 0 | 0 | 42 | 0 | 42 | 0 | 60 | 0 | 4 | 0 | 0 | no data | 153.3333 | no data | 100% | no data | 0 | 0 | 0 | no data | 151.75 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-11-11 | 68.6 | 58.6% | 60.3 | 78 | 59 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3689 | 3642 | 0 | 0 | 0 | 42 | 0 | 42 | 0 | 60 | 0 | 8 | 0 | 0 | no data | 153.7083 | no data | 100% | no data | 0.697 | 992 | 691.424 | no data | 151.75 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
Week 46 | 2019-11-12 | 68.8 | 60.5% | 61.3 | 87 | 59 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3687 | 3643 | 0 | 0 | 0 | 42 | 0 | 42 | 0 | 60 | 0 | 7 | 0 | 0 | no data | 153.625 | no data | 100% | no data | 0 | 0 | 0 | no data | 151.7917 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-11-13 | 66.4 | 71.9% | 64.1 | 71 | 63 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3713 | 3662 | 0 | 0 | 0 | 42 | 0 | 42 | 0 | 60 | 0 | 5 | 0 | 0 | no data | 154.7083 | no data | 100% | no data | 0 | 0 | 0 | no data | 152.5833 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-11-14 | 65.5 | 76.8% | 65.2 | 76 | 60 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3709 | 3689 | 0 | 0 | 0 | 42 | 0 | 42 | 0 | 60 | 0 | 4 | 0 | 0 | no data | 154.5417 | no data | 100% | no data | 0 | 0 | 0 | no data | 153.7083 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-11-15 | 67 | 77% | 66.4 | 74 | 61 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3699 | 3688 | 0 | 0 | 0 | 42 | 0 | 42 | 0 | 60 | 0 | 5 | 0 | 0 | no data | 154.125 | no data | 100% | no data | 0 | 0 | 0 | no data | 153.6667 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-11-16 | 69 | 74% | 66.8 | 82 | 63 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3691 | 3687 | 0 | 0 | 0 | 42 | 0 | 42 | 0 | 60 | 0 | 4 | 0 | 0 | no data | 153.7917 | no data | 100% | no data | 0 | 0 | 0 | no data | 153.625 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-11-17 | 68.5 | 68.4% | 64 | 83.5 | 60 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3690 | 3682 | 0 | 0 | 0 | 42 | 0 | 42 | 0 | 60 | 0 | 4 | 0 | 0 | no data | 153.75 | no data | 100% | no data | 0 | 0 | 0 | no data | 153.4167 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-11-18 | 69.5 | 66.5% | 63.7 | 82 | 59 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3678 | 3678 | 0 | 0 | 0 | 42 | 0 | 42 | 0 | 60 | 0 | 5 | 0 | 0 | no data | 153.25 | no data | 100% | no data | 0 | 0 | 0 | no data | 153.25 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
Week 47 | 2019-11-19 | 68.5 | 64.7% | 62.7 | 84 | 58 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3682 | 3671 | 0 | 0 | 0 | 42 | 0 | 42 | 0 | 60 | 0 | 4 | 0 | 0 | no data | 153.4167 | no data | 100% | no data | 0 | 0 | 0 | no data | 152.9583 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-11-20 | 68.83 | 61.25% | 62 | 82 | 60 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3682 | 3668 | 0 | 0 | 0 | 42 | 0 | 42 | 0 | 60 | 0 | 5 | 0 | 0 | no data | 153.4167 | no data | 100% | no data | 0 | 0 | 0 | no data | 152.8333 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 50 | 0 | 0 | 0
| 2019-11-21 | 67.5 | 65.4% | 62.3 | 76 | 61 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3696 | 3669 | 0 | 0 | 0 | 42 | 0 | 42 | 0 | 60 | 0 | 4 | 0 | 0 | no data | 154 | no data | 100% | no data | 0 | 0 | 0 | no data | 152.875 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 50 | 0 | 0 | 0
| 2019-11-22 | 63.1 | 77% | 63 | 67 | 61 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3720 | 3669 | 0 | 0 | 0 | 42 | 0 | 42 | 0 | 60 | 0 | 5 | 0 | 0 | no data | 155 | no data | 100% | no data | 0 | 0 | 0 | no data | 152.875 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-11-23 | 64.67 | 71.92% | 62 | 80.37 | 57 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3705 | 3672 | 0 | 0 | 0 | 42 | 0 | 42 | 0 | 60 | 0 | 4 | 0 | 0 | no data | 154.375 | no data | 100% | no data | 0 | 0 | 0 | no data | 153 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-11-24 | 65.9 | 64.3% | 60.4 | 83 | 57 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3696 | 3676 | 0 | 0 | 0 | 42 | 0 | 42 | 0 | 60 | 0 | 5 | 0 | 0 | no data | 154 | no data | 100% | no data | 0 | 0 | 0 | no data | 153.1667 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-11-25 | 65.8 | 62.6% | 59.8 | 82 | 55 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3698 | 3677 | 0 | 0 | 0 | 42 | 0 | 42 | 0 | 60 | 0 | 5 | 0 | 0 | no data | 154.0833 | no data | 100% | no data | 0 | 0 | 0 | no data | 153.2083 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
Week 48 | 2019-11-26 | 66.4 | 59.5% | 59.5 | 76 | 59 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3699 | 3682 | 0 | 0 | 0 | 42 | 0 | 42 | 0 | 60 | 0 | 4 | 0 | 0 | no data | 154.125 | no data | 100% | no data | 0 | 0 | 0 | no data | 153.4167 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-11-27 | 64 | 68% | 60.4 | 80 | 55 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3702 | 3686 | 0 | 0 | 0 | 42 | 0 | 42 | 0 | 60 | 0 | 5 | 0 | 0 | no data | 154.25 | no data | 100% | no data | 0 | 0 | 0 | no data | 153.5833 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-11-28 | 64 | 70% | 61.1 | 76 | 46 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3708 | 3686 | 0 | 0 | 0 | 42 | 0 | 42 | 0 | 60 | 0 | 5 | 0 | 0 | no data | 154.5 | no data | 100% | no data | 0 | 0 | 0 | no data | 153.5833 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-11-29 | 62.3 | 64.5% | 57.7 | 79 | 53 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3707 | 3689 | 0 | 0 | 0 | 42 | 0 | 42 | 0 | 60 | 0 | 5 | 0 | 0 | no data | 154.4583 | no data | 100% | no data | 0 | 0 | 0 | no data | 153.7083 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-11-30 | 62.2 | 55% | 54 | 84 | 52 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3702 | 3696 | 0 | 0 | 0 | 42 | 0 | 42 | 0 | 60 | 0 | 5 | 0 | 0 | no data | 154.25 | no data | 100% | no data | 0 | 0 | 0 | no data | 154 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-12-01 | [26 empty] | 0 | 0 |  | no data | no data | no data | #DIV/0! | no data |  |  | 0 | no data | 0 | [10 empty] | 0 | no data | 0 | [7 empty] | 0
| 2019-12-02 | [26 empty] | 0 | 0 |  | no data | no data | no data | #DIV/0! | no data |  |  | 0 | no data | 0 | [10 empty] | 0 | no data | 0 | [7 empty] | 0
| Monthly | 68.119 | 0.65671 | 62.924 | 81.1573 | 59.5487 | 0 | 0 | 0 | 12 | 720 | 12 | 720 | 0 | 0 | 1843 | 110588 | 109616 | 0 | 0 | 0 | 41.4667 | 0 | 41.4667 | 0 | 60 | 0 | 142.08 | 0 | 0 | #DIV/0! | 153.5944 | #DIV/0! | 100% | #DIV/0! | 0.697 | 33.0667 | 691.424 | #DIV/0! |  | 0 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 100 | 0 | 0 | 0
| Totals | Avg.F | % Avg. | % Avg. | M Avg | m Avg | hrs | min | hrs | min | hrs | min | hrs | min | Avg Int Avi | Avg Ext Avi | MWhr Total | MWhr Total | MWhr Total | MWhr Total | MWhr Total | MW Avg | Total min | Avg MW | Total min | Avg MW | Total min | MWhr | Total MW | Av Max D/Gen | Av. DailyLF | Avg. | Avg. |  | Avg. | Total | Avg. |  | Avg. | [7 empty] | Total |  |  |  |  | Avg.
| Weeks data | Site Avg. Amb. Temp F | Site Avg. Relative humidity % | Site Avg. Ambient Wetbulb Temp.F | Max: Site Maximum/Minumum Temperature; CT1 hrs: CT-1 Base Load Hours; CT2 hrs: CT-2 Base Load Hours; CT1 hrs: CT-1 stand by hours / min; CT2 hrs: CT-2 standby hours / min; CT2 hrs: Plant ambient Corrected maximum Load hours/min | Average Corrected Plant Capacity | Ambient Corrected Declared Avail'y (MWH) | Av Plant WAPDA Dispatch | Net Plant Export (MWH) | Gross Generation | CT1 Av Cap (MW) | CT1 Unavail minutes | CT2 Av Cap (MW) | CT2 Unavail minutes | ST Unavail minutes | ST Average Cap (MW) | Plant Aux Load including Colony Load MWH | Differenece (+/-) MW | Maximum Daily Generation | Daily Load Factor | Avg. Corrected Plant | Plant Capacity Facto | Plant Availability Factor | Equivalent Plant Availability | PL gas flow (mscf/week) | 1 PL gas (Average Btu/scf) | HBTU MMBTU | Plant Net Heat Rate (Btu/Kwh) | [11 empty] | 0
| Week 44 | 76.0914 | 64.11% | 68.92 | 88.1429 | 68 | 0 | 0 | 0 | 0 | 168 | 0 | 168 | 0 | 0 | 0 | 3634.2857 | 3587.7143 | no data | no data | no data | 40 | #REF! | 40 | #REF! | #REF! | no data | no data | no data | no data | #DIV/0! | 151.4286 | #DIV/0! | 100% | #DIV/0! | no data | no data | #VALUE! | #DIV/0!
| Week 45 | 68.9043 | 61.75% | 62.0857 | 82.6929 | 59.4943 | 0 | 0 | 0 | -120 | 168 | -120 | 168 | 0 | 0 | 0 | 3682.5714 | 3625.8571 | no data | no data | no data | 40.8571 | No outage | 286 | no data | 420 | no data | 35 | no data | no data | #DIV/0! | 153.4405 | #DIV/0! | 100% | #DIV/0! | no data | no data | #VALUE! | #DIV/0! | [5 empty] | 0.27381
| Week 46 | 67.8143 | 70.73% | 64.5 | 79.3571 | 60.7143 | 0 | 0 | 0 | 0 | 168 | 0 | 168 | 0 | 0 | 0 | 3695.2857 | 3675.5714 | no data | no data | no data | 42 | No outage | 294 | no data | 420 | no data | 34 | no data | no data | #DIV/0! | 153.9702 | #DIV/0! | 100% | #DIV/0! | no data | no data | #VALUE! | #DIV/0! |  |  |  |  | 840 | 0.26672
| Week 47 | 66.3286 | 66.74% | 64.5 | 79.1957 | 58.4286 | 0 | 0 | 0 | 0 | 168 | 0 | 168 | 0 | 0 | 0 | 3697 | 3671.7143 | no data | no data | no data | 42 | No outage | 294 | no data | 420 | no data | 32 | no data | no data | #DIV/0! | 154.0417 | #DIV/0! | 100% | #DIV/0! | no data | no data | #VALUE! | #DIV/0!
| Week 48 | 66.0286 | 66% | 64.7 | 78.0529 | 58.5714 | 0 | 0 | 0 | 0 | 168 | 0 | 168 | 0 | 0 | 0 | 3699.4286 | 3673.2857 | no data | no data | no data | 42 | No outage | 294 | no data | 420 | no data | 32 | no data | no data | #DIV/0! | 154.1429 | #DIV/0! | 100% | #DIV/0! | no data | no data | #VALUE! | #DIV/0!
336
| Date | Plant Status Whether Normal Operation or Tripping (State full detail for trippings/return to normal). | [56 empty] | 420
| 2019-11-01 | Plant remained shutdown and in standby mode from 0000~2400 hrs as per NPCC demand. | [56 empty] | 360
| 2019-11-02 | Plant remained shutdown and in standby mode from 0000~2400 hrs as per NPCC demand. | [56 empty] | 1116
| 2019-11-03 | Plant remained shutdown and in standby mode from 0000~2400 hrs as per NPCC demand. | [57 empty] | 22.32
| 2019-11-04 | Plant remained shutdown and in standby mode from 0000~2400 hrs as per NPCC demand.
| 2019-11-05 | Plant remained shutdown and in standby mode from 0000~2400 hrs as per NPCC demand.
| 2019-11-06 | Plant remained shutdown and in standby mode from 0000~2400 hrs as per NPCC demand.
| 2019-11-07 | Plant remained shutdown and in standby mode from 0000~2400 hrs as per NPCC demand.
| 2019-11-08 | Plant remained shutdown and in standby mode from 0000~2400 hrs as per NPCC demand.
| 2019-11-09 | Plant remained shutdown and in standby mode from 0000~2400 hrs as per NPCC demand.
| 2019-11-10 | Plant remained shutdown and in standby mode from 0000~2400 hrs as per NPCC demand.
| 2019-11-11 | CT-2 hot commissioning on single fuel carried out. CT-1 & CT-2 kept on FSNL for 30 min. for biolers warmup for hot drainage to carryout dry preservation of HRSGs.
| 2019-11-12 | Plant remained shutdown and in standby mode from 0000~2400 hrs as per NPCC demand.
| 2019-11-13 | Plant remained shutdown and in standby mode from 0000~2400 hrs as per NPCC demand.
| 2019-11-14 | Plant remained shutdown and in standby mode from 0000~2400 hrs as per NPCC demand.
| 2019-11-15 | Plant remained shutdown and in standby mode from 0000~2400 hrs as per NPCC demand.
| 2019-11-16 | Plant remained shutdown and in standby mode from 0000~2400 hrs as per NPCC demand.
| 2019-11-17 | Plant remained shutdown and in standby mode from 0000~2400 hrs as per NPCC demand.
| 2019-11-18 | Plant remained shutdown and in standby mode from 0000~2400 hrs as per NPCC demand.
| 2019-11-19 | Plant remained shutdown and in standby mode from 0000~2400 hrs as per NPCC demand.
| 2019-11-20 | Plant remained shutdown and in standby mode from 0000~2400 hrs as per NPCC demand.
| 2019-11-21 | Plant remained shutdown and in standby mode from 0000~2400 hrs as per NPCC demand.
| 2019-11-22 | Plant remained shutdown and in standby mode from 0000~2400 hrs as per NPCC demand.
| 2019-11-23 | Plant remained shutdown and in standby mode from 0000~2400 hrs as per NPCC demand.
| 2019-11-24 | Plant remained shutdown and in standby mode from 0000~2400 hrs as per NPCC demand.
| 2019-11-25 | Plant remained shutdown and in standby mode from 0000~2400 hrs as per NPCC demand.
| 2019-11-26 | Plant remained shutdown and in standby mode from 0000~2400 hrs as per NPCC demand.
| 2019-11-27 | Plant remained shutdown and in standby mode from 0000~2400 hrs as per NPCC demand.
| 2019-11-28 | Plant remained shutdown and in standby mode from 0000~2400 hrs as per NPCC demand.
| 2019-11-29 | Plant remained shutdown and in standby mode from 0000~2400 hrs as per NPCC demand.
| 2019-11-30 | Plant remained shutdown and in standby mode from 0000~2400 hrs as per NPCC demand.
[5 empty] | CT2 hrs: 0.066667 |  | 0.81667 |  | 0.3
[5 empty] | CT2 hrs: 0.81667 |  | 0.53333
0.28333
0.25
0.18333
0.93333

## Dec
Monthly Operational Returns Kabirwala
2019-12-01
| Date | Site Avg. Ambient Temp.F | Site Avg. Relative Humidty % | Site Avg. Ambient Wetbulb Temp.F | Site Ambient Temp |  | Base load hours |  |  |  | Standby hours |  |  |  | Plant ambient corrected Max Load |  | Corrected Plant Capacity | Ambient Corrected Daclared Avail'y (MWH) | Plant WAPDA Dispatch (MWH) | Net Plant Export (MWH) | Gross Generation | CT1 Average Cap (MW) | CT1 Unavail minutes | CT2 Average Cap (MW) | CT2 Unavail minutes | ST Average Cap (MW) | ST Unavail minutes | Plant Aux Load including Colony Load MWH | Differenece (+/-) MW | Maximum Daily Generation | Daily Load Factor | Avg. Corrected Plant Capacity | Plant Capacity Factor | Plant Availability Factor | Equivalent Plant Availability | 1 HBtu gas flow (mmscf/day) | 1 HBtu gas (Average Btu/scf) | HBTU MMBTU | HHV Net Heat Rate (Btu/Kwh) | Avg. declared availability | CT1 Derated MW | CT1 derated mintutes | CT-2 derated MW | CT-2 derated mintutes | ST derated MW | ST derated mintutes | WAPDA Backfeed (MWH) | CT-1 Gross Generation (MWH) | CT-2 Gross Generation (MWH) | STG Gross Generation (MWH) | CT-1 & CT-2 MWH difference | Base load Heat Rate | STG load | DB1 | DB2 | CT1 Gas flow | CT2 Gas flow | Freq. Hz | CT-1 compressor efficiency(%) | CT-2 compressor efficiency(%) | DB(1+2) | CT-1 Heat Rate (Btu/Kwh) | CT-2 Heat Rate (Btu/Kwh) | RO Operation Hours
[7 empty] | CT1 |  | CT2 |  | CT1 |  | CT2 | [40 empty] | mmscf/d | mmscf/d | HBTU KPPH | HBTU KPPH | Hz |  |  | mmscf/d
[5 empty] | Max | Min | hrs | min | hrs | min | hrs | min | hrs | min | hrs | min
Week 48 | 2019-11-26 | 66.4 | 59.5% | 59.5 | 76 | 59 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3699 | 3682 | 0 | 0 | 0 | 42 | 0 | 42 | 0 | 60 | 0 | 4 | 0 | 0 | no data | 154.125 | no data | 100% | no data | 0 | 0 | 0 | no data | 153.4167 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-11-27 | 64 | 68% | 60.4 | 80 | 55 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3702 | 3686 | 0 | 0 | 0 | 42 | 0 | 42 | 0 | 60 | 0 | 5 | 0 | 0 | no data | 154.25 | no data | 100% | no data | 0 | 0 | 0 | no data | 153.5833 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-11-28 | 64 | 70% | 61.1 | 76 | 46 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3708 | 3686 | 0 | 0 | 0 | 42 | 0 | 42 | 0 | 60 | 0 | 5 | 0 | 0 | no data | 154.5 | no data | 100% | no data | 0 | 0 | 0 | no data | 153.5833 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-11-29 | 62.3 | 64.5% | 57.7 | 79 | 53 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3707 | 3689 | 0 | 0 | 0 | 42 | 0 | 42 | 0 | 60 | 0 | 5 | 0 | 0 | no data | 154.4583 | no data | 100% | no data | 0 | 0 | 0 | no data | 153.7083 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-11-30 | 62.2 | 55% | 54 | 84 | 52 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3702 | 3696 | 0 | 0 | 0 | 42 | 0 | 42 | 0 | 60 | 0 | 5 | 0 | 0 | no data | 154.25 | no data | 100% | no data | 0 | 0 | 0 | no data | 154 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-12-01 | 63 | 53.57% | 54.34 | 86 | 51.4 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3701 | 3696 | 0 | 0 | 0 | 42 | 0 | 42 | 0 | 60 | 0 | 4 | 0 | 0 | no data | 154.2083 | no data | 100% | no data | 0 | 0 | 0 | no data | 154 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-12-02 | 62.72 | 57.69% | 55.21 | 80 | 51 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3700 | 3696 | 0 | 0 | 0 | 42 | 0 | 42 | 0 | 60 | 0 | 5 | 0 | 0 | no data | 154.1667 | no data | 100% | no data | 0 | 0 | 0 | no data | 154 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
Week 49 | 2019-12-03 | 62.3 | 63.7% | 56.9 | 80 | 51 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3700 | 3695 | 0 | 0 | 0 | 42 | 0 | 42 | 0 | 60 | 0 | 4 | 0 | 0 | no data | 154.1667 | no data | 100% | no data | 0 | 0 | 0 | no data | 153.9583 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-12-04 | 62.3 | 61.7% | 56.3 | 79 | 51 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3700 | 3695 | 0 | 0 | 0 | 43 | 0 | 43 | 0 | 60 | 0 | 5 | 0 | 0 | 0% | 154.1667 | no data | 100% | no data | 0 | 0 | 0 | no data | 153.9583 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-12-05 | 61.6 | 60.3% | 55.3 | 85 | 51 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3703 | 3695 | 0 | 0 | 0 | 43 | 0 | 43 | 0 | 60 | 0 | 5 | 0 | 0 | no data | 154.2917 | no data | 100% | no data | 0 | 0 | 0 | no data | 153.9583 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-12-06 | 61.3 | 58% | 54.3 | 85 | 50 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3709 | 3696 | 0 | 0 | 0 | 43 | 0 | 43 | 0 | 60 | 0 | 5 | 0 | 0 | no data | 154.5417 | no data | 100% | no data | 0 | 0 | 0 | no data | 154 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-12-07 | 60.61 | 59.25% | 53.8 | 83 | 49.75 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3708 | 3696 | 0 | 0 | 0 | 44 | 0 | 44 | 0 | 60 | 0 | 4 | 0 | 0 | no data | 154.5 | no data | 100% | no data | 0 | 0 | 0 | no data | 154 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-12-08 | 60.2 | 61.3% | 54.3 | 81 | 49 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3707 | 3697 | 0 | 0 | 0 | 44 | 0 | 44 | 0 | 60 | 0 | 5 | 0 | 0 | no data | 154.4583 | no data | 100% | no data | 0 | 0 | 0 | no data | 154.0417 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-12-09 | 61.7 | 62.4% | 56 | 74 | 51 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3708 | 3699 | 0 | 0 | 0 | 44 | 0 | 44 | 0 | 60 | 0 | 4 | 0 | 0 | no data | 154.5 | no data | 100% | no data | 0 | 0 | 0 | no data | 154.125 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
Week 50 | 2019-12-10 | 61.25 | 64.38% | 56.5 | 80 | 53 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3710 | 3699 | 0 | 0 | 0 | 44 | 0 | 44 | 0 | 60 | 0 | 5 | 0 | 0 | no data | 154.5833 | no data | 100% | no data | 0 | 0 | 0 | no data | 154.125 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-12-11 | 60.2 | 67% | 55.8 | 67 | 53 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3720 | 3704 | 0 | 0 | 0 | 44 | 0 | 44 | 0 | 60 | 0 | 5 | 0 | 0 | no data | 155 | no data | 100% | no data | 0 | 0 | 0 | no data | 154.3333 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-12-12 | 56.1 | 83.7% | 58.3 | 59 | 54 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3720 | 3717 | 0 | 0 | 0 | 44 | 0 | 44 | 0 | 60 | 0 | 5 | 0 | 0 | no data | 155 | no data | 100% | no data | 0 | 0 | 0 | no data | 154.875 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-12-13 | 54.5 | 83.7% | 56.5 | 60.9 | 48.8 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3720 | 3719 | 0 | 0 | 0 | 46 | 0 | 46 | 0 | 60 | 0 | 5 | 0 | 0 | no data | 155 | no data | 100% | no data | 0 | 0 | 0 | no data | 154.9583 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-12-14 | 53.17 | 88.67% | 55.88 | 57 | 48.8 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3720 | 3720 | 0 | 0 | 0 | 46 | 0 | 46 | 0 | 60 | 0 | 6 | 0 | 0 | no data | 155 | no data | 100% | no data | 0 | 0 | 0 | no data | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-12-15 | 53.7 | 84.7% | 56.2 | 57 | 52 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3720 | 3720 | 0 | 0 | 0 | 45 | 0 | 45 | 0 | 60 | 0 | 5 | 0 | 0 | no data | 155 | no data | 100% | no data | 0 | 0 | 0 | no data | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-12-16 | 54.4 | 80.7% | 56 | 67 | 51 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3720 | 3720 | 0 | 0 | 0 | 45 | 0 | 45 | 0 | 60 | 0 | 6 | 0 | 0 | no data | 155 | no data | 100% | no data | 0 | 0 | 0 | no data | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
Week 51 | 2019-12-17 | 53.7 | 79.9% | 54 | 67 | 43 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3720 | 3720 | 0 | 0 | 0 | 45 | 0 | 45 | 0 | 60 | 0 | 6 | 0 | 0 | no data | 155 | no data | 100% | no data | 0 | 0 | 0 | no data | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-12-18 | 55.3 | 73.8% | 53.6 | 75 | 42 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3719 | 3720 | 0 | 0 | 0 | 45 | 0 | 45 | 0 | 60 | 0 | 5 | 0 | 0 | no data | 154.9583 | no data | 100% | no data | 0 | 0 | 0 | no data | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-12-19 | 56.7 | 74.9% | 56.1 | 66.6 | 48.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 3718 | 3718 | 0 | 0 | 45 | 0 | 45 | 0 | 60 | 0 | 5 | -3718 | 0 | no data | 155 | no data | 100% | no data | 0 | 0 | 0 | no data | 154.9167 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-12-20 | 54.9 | 76.7% | 54.6 | 68 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 3716 | 3716 | 0 | 0 | 45 | 0 | 45 | 0 | 60 | 0 | 6 | -3716 | 0 | no data | 155 | no data | 100% | no data | 0 | 0 | 0 | no data | 154.8333 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-12-21 | 51.7 | 84% | 53.8 | 60 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 3720 | 3720 | 0 | 0 | 45 | 0 | 45 | 0 | 60 | 0 | 5 | -3720 | 0 | no data | 155 | no data | 100% | no data | 0 | 0 | 0 | no data | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-12-22 | 47.9 | 90.6% | 50.9 | 52 | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 3720 | 3720 | 0 | 0 | 45 | 0 | 45 | 0 | 60 | 0 | 5 | -3720 | 0 | no data | 155 | no data | 100% | no data | 0 | 0 | 0 | no data | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-12-23 | 48.17 | 85.5% | 51.42 | 52.45 | 44.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 3720 | 3720 | 0 | 0 | 48 | 0 | 48 | 0 | 60 | 0 | 6 | -3720 | 0 | no data | 155 | no data | 100% | no data | 0 | 0 | 0 | no data | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
Week 52 | 2019-12-24 | 47.88 | 88.46% | 51 | 50 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 3720 | 3720 | 0 | 0 | 48 | 0 | 48 | 0 | 60 | 0 | 6 | -3720 | 0 | no data | 155 | no data | 100% | no data | 0 | 0 | 0 | no data | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-12-25 | 47.3 | 79.2% | 47.5 | 54 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 3720 | 3720 | 0 | 0 | 48 | 0 | 48 | 0 | 60 | 0 | 5 | -3720 | 0 | no data | 155 | no data | 100% | no data | 0 | 0 | 0 | no data | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-12-26 | 43.71 | 89.33% | 46.63 | 47 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 3720 | 3720 | 0 | 0 | 48 | 0 | 48 | 0 | 60 | 0 | 6 | -3720 | 0 | no data | 155 | no data | 100% | no data | 0 | 0 | 0 | no data | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-12-27 | 43.9 | 86.3% | 46.7 | 46 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 3720 | 3720 | 0 | 0 | 48 | 0 | 48 | 0 | 60 | 0 | 5 | -3720 | 0 | no data | 155 | no data | 100% | no data | 0 | 0 | 0 | no data | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 49.97 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-12-28 | 45.8 | 75.7% | 47.2 | 47 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 3720 | 3720 | 0 | 0 | 48 | 0 | 48 | 0 | 60 | 0 | 5 | -3720 | 0 | no data | 155 | no data | 100% | no data | 0 | 0 | 0 | no data | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 49.9 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-12-29 | 46.6 | 73.6% | 47.1 | 51 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 3720 | 3720 | 0 | 0 | 48 | 0 | 48 | 0 | 60 | 0 | 5 | -3720 | 0 | no data | 155 | no data | 100% | no data | 0 | 0 | 0 | no data | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 49.98 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-12-30 | 42.3 | 80.8% | 44.4 | 44 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 3720 | 3720 | 0 | 0 | 48 | 0 | 48 | 0 | 60 | 0 | 6 | -3720 | 0 | no data | 155 | no data | 100% | no data | 0 | 0 | 0 | no data | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| 2019-12-31 | 45.2 | 73.7% | 45.9 | 49 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720 | 3720 | 3720 | 0 | 0 | 48 | 0 | 48 | 0 | 60 | 0 | 7 | -3720 | 0 | no data | 155 | no data | 100% | no data | 0 | 0 | 0 | no data | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | no data | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| Monthly | 54.1971 | 0.74298 | 52.9832 | 64.8371 | 47.3777 | 0 | 0 | 0 | 7 | 432 | 7 | 432 | 0 | 0 | 1919 | 115165 | 115058 | 48354 | 0 | 0 | 45.2581 | 0 | 45.2581 | 0 | 60 | 0 | 159.72 | -48354 | 0 | 0 | 154.7917 | #DIV/0! | 1 | #DIV/0! | 0 | 0 | 0 | #DIV/0! |  | 0 | 0 | 0 | 0 | 0 | 0 | 159.72 | 0 | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 49.9952 | 0 | 0 | 0 | 0 | 0 | 0
| Totals | Avg.F | % Avg. | % Avg. | M Avg | m Avg | hrs | min | hrs | min | hrs | min | hrs | min | Avg Int Avi | Avg Ext Avi | MWhr Total | MWhr Total | MWhr Total | MWhr Total | MWhr Total | MW Avg | Total min | Avg MW | Total min | Avg MW | Total min | MWhr | Total MW | Av Max D/Gen | Av. DailyLF | Avg. | Avg. |  | Avg. | Total | Avg. |  | Avg. | [7 empty] | Total |  |  |  |  | Avg.
| Weeks data | Site Avg. Amb. Temp F | Site Avg. Relative humidity % | Site Avg. Ambient Wetbulb Temp.F | Max: Site Maximum/Minumum Temperature; CT1 hrs: CT-1 Base Load Hours; CT2 hrs: CT-2 Base Load Hours; CT1 hrs: CT-1 stand by hours / min; CT2 hrs: CT-2 standby hours / min; CT2 hrs: Plant ambient Corrected maximum Load hours/min | Average Corrected Plant Capacity | Ambient Corrected Declared Avail'y (MWH) | Av Plant WAPDA Dispatch | Net Plant Export (MWH) | Gross Generation | CT1 Av Cap (MW) | CT1 Unavail minutes | CT2 Av Cap (MW) | CT2 Unavail minutes | ST Unavail minutes | ST Average Cap (MW) | Plant Aux Load including Colony Load MWH | Differenece (+/-) MW | Maximum Daily Generation | Daily Load Factor | Avg. Corrected Plant | Plant Capacity Facto | Plant Availability Factor | Equivalent Plant Availability | PL gas flow (mscf/week) | 1 PL gas (Average Btu/scf) | HBTU MMBTU | Plant Net Heat Rate (Btu/Kwh) | [11 empty] | 0
| Week 48 | 63.5171 | 61.18% | 57.4643 | 80.1429 | 52.4857 | 0 | 0 | 0 | 0 | 168 | 0 | 168 | 0 | 0 | 0 | 3702.7143 | 3690.1429 | no data | no data | no data | 42 | #REF! | 42 | #REF! | #REF! | no data | no data | no data | no data | #DIV/0! | 154.2798 | #DIV/0! | 100% | #DIV/0! | no data | no data | #VALUE! | #DIV/0!
| Week 49 | 61.43 | 60.95% | 55.2714 | 81 | 50.3929 | 0 | 0 | 0 | -120 | 168 | -120 | 168 | 0 | 0 | 0 | 3705 | 3696.1429 | no data | no data | no data | 43.2857 | No outage | 303 | no data | 420 | no data | 32 | no data | no data | 0% | 154.375 | #DIV/0! | 100% | #DIV/0! | no data | no data | #VALUE! | #DIV/0! | [5 empty] | 0.27381
| Week 50 | 56.1886 | 78.98% | 56.4543 | 63.9857 | 51.5143 | 0 | 0 | 0 | 0 | 168 | 0 | 168 | 0 | 0 | 0 | 3718.5714 | 3714.1429 | no data | no data | no data | 44.8571 | No outage | 314 | no data | 420 | no data | 37 | no data | no data | #DIV/0! | 154.9405 | #DIV/0! | 100% | #DIV/0! | no data | no data | #VALUE! | #DIV/0! |  |  |  |  | 840 | 0.26672
| Week 51 | 52.6243 | 80.77% | 56.4543 | 63.0071 | 45.4229 | 0 | 0 | 0 | 0 | 48 | 0 | 48 | 0 | 0 | 0 | 3719.8571 | 3719.1429 | no data | no data | no data | 45.4286 | No outage | 318 | no data | 420 | no data | 38 | no data | no data | #DIV/0! | 154.994 | #DIV/0! | 100% | #DIV/0! | no data | no data | #VALUE! | #DIV/0!
| Week 52 | 51.7929 | 81.99% | 56.0971 | 60.5786 | 45.7086 | 0 | 0 | 0 | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 3719.8571 | 3719.1429 | no data | no data | no data | 45.8571 | No outage | 321 | no data | 420 | no data | 38 | no data | no data | #DIV/0! | 154.994 | #DIV/0! | 100% | #DIV/0! | no data | no data | #VALUE! | #DIV/0!
336
| Date | Plant Status Whether Normal Operation or Tripping (State full detail for trippings/return to normal). | [56 empty] | 420
| 2019-12-01 | Plant remained shutdown and in standby mode from 0000~2400 hrs as per NPCC demand. | [56 empty] | 360
| 2019-12-02 | Plant remained shutdown and in standby mode from 0000~2400 hrs as per NPCC demand. | [56 empty] | 1116
| 2019-12-03 | Plant remained shutdown and in standby mode from 0000~2400 hrs as per NPCC demand. | [57 empty] | 22.32
| 2019-12-04 | Plant remained shutdown and in standby mode from 0000~2400 hrs as per NPCC demand.
| 2019-12-05 | Plant remained shutdown and in standby mode from 0000~2400 hrs as per NPCC demand.
| 2019-12-06 | Plant remained shutdown and in standby mode from 0000~2400 hrs as per NPCC demand.
| 2019-12-07 | Plant remained shutdown and in standby mode from 0000~2400 hrs as per NPCC demand.
| 2019-12-08 | Plant remained shutdown and in standby mode from 0000~2400 hrs as per NPCC demand.
| 2019-12-09 | Plant remained shutdown and in standby mode from 0000~2400 hrs as per NPCC demand.
| 2019-12-10 | Plant remained shutdown and in standby mode from 0000~2400 hrs as per NPCC demand.
| 2019-12-11 | Plant remained shutdown and in standby mode from 0000~2400 hrs as per NPCC demand.
| 2019-12-12 | Plant remained shutdown and in standby mode from 0000~2400 hrs as per NPCC demand.
| 2019-12-13 | Plant remained shutdown and in standby mode from 0000~2400 hrs as per NPCC demand.
| 2019-12-14 | Plant remained shutdown and in standby mode from 0000~2400 hrs as per NPCC demand.
| 2019-12-15 | Plant remained shutdown and in standby mode from 0000~2400 hrs as per NPCC demand.
| 2019-12-16 | Plant remained shutdown and in standby mode from 0000~2400 hrs as per NPCC demand.
| 2019-12-17 | Plant remained shutdown and in standby mode from 0000~2400 hrs as per NPCC demand.
| 2019-12-18 | Plant remained shutdown and in standby mode from 0000~2400 hrs as per NPCC demand.
| 2019-12-19 | Plant remained in Standby mode from 0000~0045 hrs as per NPCC demand. Plant remained shut down 0045~2400 hrs due to non-allocation of FKPCL’s RLNG quota by SNGPL.
| 2019-12-20 | Plant remained shut down 0000~2400 hrs due to non-allocation of FKPCL’s RLNG quota by SNGPL.
| 2019-12-21 | Plant remained shut down 0000~2400 hrs due to non-allocation of FKPCL’s RLNG quota by SNGPL.
| 2019-12-22 | Plant remained shut down 0000~2400 hrs due to non-allocation of FKPCL’s RLNG quota by SNGPL.
| 2019-12-23 | Plant remained shut down 0000~2400 hrs due to non-allocation of FKPCL’s RLNG quota by SNGPL.
| 2019-12-24 | Plant remained shut down 0000~2400 hrs due to non-allocation of FKPCL’s RLNG quota by SNGPL.
| 2019-12-25 | Plant remained shut down 0000~2400 hrs due to non-allocation of FKPCL’s RLNG quota by SNGPL.
| 2019-12-26 | Plant remained shut down 0000~2400 hrs due to non-allocation of FKPCL’s RLNG quota by SNGPL.
| 2019-12-27 | Plant remained shut down 0000~2400 hrs due to non-allocation of FKPCL’s RLNG quota by SNGPL.
| 2019-12-28 | Plant remained shut down 0000~2400 hrs due to non-allocation of FKPCL’s RLNG quota by SNGPL.
| 2019-12-29 | Plant remained shut down 0000~2400 hrs due to non-allocation of FKPCL’s RLNG quota by SNGPL.
| 2019-12-30 | Plant remained shut down 0000~2400 hrs due to non-allocation of FKPCL’s RLNG quota by SNGPL.
| 2019-12-31 | Plant remained shut down 0000~2400 hrs due to non-allocation of FKPCL’s RLNG quota by SNGPL.
[5 empty] | CT2 hrs: 0.066667 |  | 0.81667 |  | 0.3
[5 empty] | CT2 hrs: 0.81667 |  | 0.53333
0.28333
0.25
0.18333
0.93333