## July
Plant Daily Statistics
2020-07-01
Date | Site Avg. Ambient Temp.F | RH | Corrected Plant Capacity | Ambient Corrected Declared Avail'y (MWH) | Plant WAPDA Dispatch (MWH) | Net Plant Export (MWH) | Complex Aux Load including Colony Load MWH | CT1 Gross Generation (MWH) | CT-2 Gross Generation (MWH) | STG Gross Generation (MWH) | Gross Generation (MWH) | WAPDA Backfeed (MWH) | Differenece (+/-) MWh | Plant Capacity Factor | Plant Availability | HBtu gas mmscf/day | HBtu gas (Average Btu/scf) | HBtu mmBtu | HHV Net Heat Rate (Btu/Kwh) | Daily LD's (MWhr) | Accum* LD's (MWhr)
%age
2020-07-01 | 96.08 | 53.13 | 3435 | 3367 | 2808 | 2795 | 90 | 948 | 916 | 1021 | 2885 | 0 | -13 | 81.37% | 100% | 24.5797 | 1000.96 | 24603.329 | 8802.6222 | 0 | 20198
2020-07-02 | 99.46 | 55.79 | 3399 | 3263 | 3102 | 2969 | 94 | 924 | 897 | 1242 | 3063 | 0 | -133 | 87.35% | 100% | 26.6153 | 1007.9599 | 26827.169 | 9035.7592 | 138 | 20336
2020-07-03 | 101.3 | 52.04 | 3385 | 3181 | 3333 | 3110 | 95 | 924 | 898 | 1383 | 3205 | 0 | -223 | 91.88% | 100% | 27.8601 | 1019.3357 | 28398.83 | 9131.4566 | 168 | 20504
2020-07-04 | 96.46 | 53.17 | 3427 | 3241 | 2915 | 2764 | 87 | 743 | 911 | 1197 | 2851 | 0 | -151 | 80.65% | 100% | 24.9028 | 1013.3866 | 25236.126 | 9130.2916 | 95 | 20599
2020-07-05 | 90.4 | 60.6 | 3492 | 3001 | 2410 | 1942 | 80 | 420 | 895 | 707 | 2022 | 0 | -468 | 55.61% | 96.4% | 18.1919 | 1011.7428 | 18405.479 | 9477.5896 | 210 | 20809
2020-07-06 | 94.33 | 58.8 | 3455 | 3373 | 2891 | 2872 | 83 | 947 | 907 | 1101 | 2955 | 0 | -19 | 83.13% | 100% | 25.1847 | 1011.5485 | 25475.58 | 8870.3273 | 19 | 20828
2020-07-07 | 95.33 | 57.38 | 3443 | 3314 | 3140 | 3029 | 93 | 944 | 907 | 1271 | 3122 | 0 | -111 | 87.98% | 100% | 27.2456 | 1003.9174 | 27352.346 | 9030.1571 | 89 | 20917
2020-07-08 | 94 | 61.25 | 3456 | 3321 | 3087 | 2995 | 92 | 947 | 908 | 1232 | 3087 | 0 | -92 | 86.66% | 100% | 26.9876 | 998.7051 | 26952.624 | 8999.2067 | 74 | 20991
2020-07-09 | 94.7 | 61.1 | 3450 | 3200 | 3364 | 3125 | 95 | 936 | 891 | 1393 | 3220 | 0 | -239 | 90.58% | 100% | 28.6852 | 995.547 | 28557.451 | 9138.3843 | 193 | 21184
2020-07-10 | 98.8 | 59.6 | 3412 | 3223 | 3187 | 3020 | 90 | 929 | 885 | 1296 | 3110 | 0 | -167 | 88.51% | 100% | 27.5914 | 994.9441 | 27451.948 | 9090.049 | 138 | 21322
2020-07-11 | 97.3 | 56.6 | 3426 | 3316 | 2855 | 2794 | 82 | 933 | 822 | 1121 | 2876 | 0 | -61 | 81.55% | 100% | 25.2718 | 996.7384 | 25189.3652 | 9015.5208 | 73 | 21395
2020-07-12 | 89.5 | 64.58 | 3497 | 2205 | 2653 | 1447 | 73 | 953 | 0 | 567 | 1520 | 0 | -1206 | 41.38% | 73.19% | 13.4986 | 998.39 | 13476.8461 | 9313.6462 | 548 | 21943
2020-07-13 | 92.88 | 60.71 | 3467 | 1553 | 3395 | 1541 | 74 | 947 | 0 | 668 | 1615 | 0 | -1854 | 44.45% | 73.19% | 14.433 | 995.8946 | 14373.7225 | 9327.5292 | 2258 | 24201
2020-07-14 | 98.63 | 55.83 | 3409 | 1590 | 3367 | 1560 | 70 | 929 | 0 | 701 | 1630 | 0 | -1807 | 45.76% | 73.19% | 14.708 | 995.6813 | 14644.4813 | 9387.488 | 2201 | 26402
2020-07-15 | 98.8 | 54.1 | 3404 | 1591 | 3355 | 1563 | 75 | 935 | 0 | 703 | 1638 | 0 | -1792 | 45.92% | 73.19% | 14.7024 | 998.1597 | 14675.3088 | 9389.1931 | 2183 | 28585
2020-07-16 | 92.5 | 60.8 | 3471 | 3148 | 3009 | 2703 | 88 | 895 | 724 | 1171 | 2790 | 1 | -306 | 77.87% | 90.61% | 25.1613 | 994.4328 | 25021.2111 | 9256.8299 | 238 | 28823
2020-07-17 | 93.88 | 61.42 | 3460 | 3212 | 3141 | 3022 | 96 | 941 | 903 | 1274 | 3118 | 0 | -119 | 87.34% | 100% | 27.3713 | 997.75 | 27309.7443 | 9036.9769 | 130 | 28953
2020-07-18 | 96.08 | 61.42 | 3438 | 3214 | 3361 | 3136 | 95 | 928 | 887 | 1416 | 3231 | 0 | -225 | 91.22% | 100% | 28.6613 | 1002.7727 | 28740.794 | 9164.794 | 170 | 29123
2020-07-19 | 98.25 | 59.75 | 3413 | 3250 | 3140 | 2997 | 100 | 928 | 886 | 1283 | 3097 | 0 | -143 | 87.81% | 100% | 26.9326 | 1011.2645 | 27235.978 | 9087.7471 | 52 | 29175
2020-07-20 | 95.29 | 63.88 | 3447 | 3326 | 2999 | 2930 | 91 | 928 | 890 | 1203 | 3021 | 0 | -69 | 85% | 100% | 26.1813 | 1010.6775 | 26460.872 | 9031.0143 | 76 | 29251
2020-07-21 | 82.1 | 76.8 | 3579 | 3497 | 2489 | 2533 | 81 | 968 | 731 | 915 | 2614 | 0 | 44 | 70.77% | 100% | 22.5278 | 1001.2566 | 22556.0709 | 8904.8839 | 0 | 29251
2020-07-22 | 87.8 | 67.5 | 3520 | 3430 | 2161 | 2126 | 80 | 955 | 409 | 842 | 2206 | 0 | -35 | 60.4% | 100% | 19.2939 | 1005.6797 | 19403.4532 | 9126.7419 | 24 | 29275
2020-07-23 | 92.3 | 60.6 | 3473 | 3372 | 2491 | 2405 | 82 | 933 | 560 | 994 | 2487 | 0 | -86 | 69.25% | 100% | 21.9531 | 1002.4126 | 22006.0514 | 9150.1253 | 53 | 29328
2020-07-24 | 93.25 | 67.42 | 3464 | 3373 | 2849 | 2799 | 83 | 928 | 894 | 1060 | 2882 | 0 | -50 | 80.8% | 100% | 24.8248 | 1005.2012 | 24953.966 | 8915.3148 | 14 | 29342
2020-07-25 | 92.88 | 64.83 | 3470 | 3323 | 3062 | 2968 | 86 | 935 | 900 | 1219 | 3054 | 0 | -94 | 85.53% | 100% | 26.6589 | 1001.4665 | 26697.95 | 8995.2662 | 84 | 29426
2020-07-26 | 94.88 | 62.63 | 3451 | 3335 | 2947 | 2868 | 81 | 932 | 888 | 1129 | 2949 | 0 | -79 | 83.11% | 100% | 25.763 | 997.479 | 25698.026 | 8960.2601 | 17 | 29443
2020-07-27 | 96.9 | 61.7 | 3431 | 3259 | 3225 | 3072 | 89 | 925 | 887 | 1349 | 3161 | 0 | -153 | 89.54% | 100% | 28.1001 | 997.0102 | 28016.045 | 9119.8063 | 115 | 29558
2020-07-28 | 96.29 | 62.05 | 3439 | 3213 | 3365 | 3146 | 93 | 924 | 885 | 1430 | 3239 | 0 | -219 | 91.48% | 100% | 29.161 | 994.4597 | 28999.484 | 9217.8907 | 171 | 29729
2020-07-29 | 96.92 | 63.16 | 3428 | 3239 | 3276 | 3070 | 90 | 917 | 881 | 1362 | 3160 | 0 | -206 | 89.56% | 100% | 28.1323 | 993.1724 | 27940.242 | 9101.056 | 182 | 29911
2020-07-30 | 94.33 | 65.46 | 3455 | 3270 | 3191 | 3024 | 89 | 922 | 890 | 1301 | 3113 | 0 | -167 | 87.53% | 100% | 27.5593 | 993.1723 | 27371.121 | 9051.2966 | 137 | 30048
2020-07-31 | 94.21 | 62.75 | 3452 | 3327 | 3005 | 2986 | 86 | 930 | 900 | 1242 | 3072 | 0 | -19 | 86.5% | 100% | 26.9433 | 996.3242 | 26844.292 | 8990.0509 | 93 | 30141
Total/ Average | 94.7042 | 60.8661 | 106948 | 95527 | 93573 | 83219.05 | 2683 | 28248 | 22952 | 34793 | 85993 | 1 | -10243 | 77.81% | 96.12% | 755.6834 | 1001.5304 | 756875.9068 | 9094.9837 | 9943 | 30141
Date | Daily Important Events (0000 hrs to 2400 hrs)
2020-07-01 | Plant load remained at 117 MW as per NPCC demand.
2020-07-02 | Max. load demand received at 0747 from NPCC and 117 MW load demand received at 2221 hrs from NPCC. Max. load demand received at 2355 from NPCC .
2020-07-03 | Plant load remained 128~131 MW from 0000 ~ 2400 hrs as per NPCC max load demand.
2020-07-04 | Plant load reduced to 117 MW at 1807 hrs as per NPCC demand. CT-1 desynchronized at 1914 hrs as per NPCC demand of 58 MW.
2020-07-05 | CT-1 Synch @ 1215 hrs as per NPCC Max. load demand. Plant load reduced to 117 MW @ 1807 hrs as per NPCC demand.
2020-07-06 | Plant load increased to 134 MW at 1222 hrs and load reduced to 117 MW at 1714 hrs as per NPCC demand.
2020-07-07 | Plant load increased to 134 MW at 0711 hrs, load reduced to 117 MW at 1823 hrs and load increased to 134 MW at 2004 hrs as per NPCC demand.
2020-07-08 | Plant load reduced to 117 MW at 0310 hrs, load increased to 134 MW at 0934 hrs, load reduced to 117 MW at 1802 hrs and load increased to 134 MW at 2250 hrs as per NPCC demand.
2020-07-09 | Plant load remained 128 ~ 132 MW from 0000 ~ 2400 hrs as per NPCC max. load demand.
2020-07-10 | Plant load reduced to 116 MW at 1755 hrs as per NPCC demand.
2020-07-11 | Plant load increased to 134 MW at 0812 hrs as per NPCC maximum load demand. Plant load reduced to 113 MW at 1715 hrs and CT-2 desynchronized at 2220 hrs as per NPCC 61 MW load demand.
2020-07-12 | Plant load remained 61 MW from 0000~0903hrs as per NPCC demand. Maximum load demand received from NPCC at 0903hrs but plant load remained 61~63MW due to shutdown of CT-2 to rectify high blade path spread issue.
2020-07-13 | Plant load remained 67 MW due to shutdown of CT-2 to rectify high blade path spread issue.
2020-07-14 | Plant load remained 67 MW due to shutdown of CT-2 to rectify high blade path spread issue.
2020-07-15 | Plant load remained 64~67 MW due to shutdown of CT-2 to rectify high blade path spread issue.
2020-07-16 | CT-2 Synch @ 0156 hrs after rectification of hight blade path spread issue. Plant load reduced to 117 MW @ 0335 hrs as per NPCC demand.Complex tripped at 2059 hrs due to Wapda supply failure. CT-1 synch @ 2210 hrs, STG synch @ 2239 hrs & CT-2 synch @ 2325 hrs.
2020-07-17 | Plant load reduced to 117 MW at 0046 hrs, and again load increased to 133 MW at 0948 hrs as per NPCC demand.
2020-07-18 | Plant load remained 129 ~ 132 MW from 0000 ~ 2400 hrs as per NPCC max. load demand.
2020-07-19 | Plant load reduced to 113 MW at 1616 hrs as per NPCC demand.
2020-07-20 | Plant load increased to 133 MW at 0804 hrs and load reduced to 115 MW at 1913 hrs as per NPCC demand.
2020-07-21 | Plant load remained at 115 MW from 0000 ~ 1850 hrs and CT-2 desynchronized at 1906 hrs as per NPCC 60 MW load demand.
2020-07-22 | CT-2 Synch at 0917 hrs as per NPCC max. load demand. Plant load reduced to 117 MW at 1551 hrs and CT-2 Desynch at 2031 hrs as per NPCC 60 MW load demand.
2020-07-23 | CT-2 synchronized at 0837 hrs as per NPCC max. load demand. Plant load remained 117 MW from 1800~2340 hrs as per NPCC demand.
2020-07-24 | Plant load increased to 133MW at 1414 hrs as per NPCC max load demand and Plant load reduced to 117MW at 1553 hrs as per NPCC demand.
2020-07-25 | Plant load increased to 133 MW at 0018 hrs as per NPCC max load demand and Plant load reduced to 116 MW at 0310 hrs as per NPCC demand. Plant load increased to 134 MW at 1217 hrs as per NPCC max load demand and Plant load reduced to 117 MW at 1637 hrs as per NPCC demand. Plant load increased to 134 MW at 1955 hrs as per NPCC max load demand
2020-07-26 | Plant load reduced to 117 MW at 0145 hrs as per NPCC demand. Plant load increased to 132 MW at 1519 hrs as per NPCC max load demand and Plant load reduced to 117 MW at 1755 hrs as per NPCC demand. Plant load increased to 133 MW at 2219 hrs as per NPCC max load demand
2020-07-27 | Plant Load reduced to 116 MW at 0429 hrs as per NPCC demand.Plant load increased to 133 MW at 0920 hrs as per NPCC max load demand.
2020-07-28 | Plant load remained 129 ~133 MW from 0000 ~ 2400 hrs as per NPCC max. load demand.
2020-07-29 | Plant Load reduced to 116 MW at 0431 hrs as per NPCC demand.Plant load increased to 133 MW at 0808 hrs as per NPCC max load demand.
2020-07-30 | Plant load reduced to 116 MW at 1658 hrs as per NPCC demand.
2020-07-31 | Plant load increased to 133 MW at 0449 hrs and load reduced to 116 MW at 1758 hrs as per NPCC demand.
2

## Sheet1
9608
9116.3698
10648.8289 |  | 2794
9153.3301 |  | 1447
9096.5803
9062.4917
10302.7757
9257.381 | 8732.6848
9856.6942 | 8645.2564
9566.9391 | 8983.8938
8777.6943
8783.3893
8835.765
8705.9982
8780.6688